## Sheet1
Original Text | Translated Text | Previous Context
Aardingsconcepten en veiligheid | Grounding Concepts and Safety
Hoofdstuk 5 beschrijft de aardingsconcepten en de veiligheid in de distributienetten. Op deze netten worden de installaties van de klanten aangesloten, waardoor het aspect van de veiligheid bijzondere aandacht verdient. Naast de beveiligingsconcepten wordt aandacht besteed aan de aanrakingsveiligheid tijdens kortsluitingen in het laag- of middenspanningsnet. | Chapter 5 describes the grounding concepts and safety in distribution networks. Customer installations are connected to these networks, which makes the aspect of safety particularly important. In addition to security concepts, attention is given to touch safety during short circuits in low or medium voltage networks. | Grounding Concepts and Safety
5 Aardingsconcepten en veiligheid | 5 Grounding Concepts and Safety | these networks, which makes the aspect of safety particularly important. In addition to security concepts, attention is given to touch safety during short circuits in low or medium voltage networks.
5.1 Aardingsconcepten | 5.1 Grounding Concepts | aspect of safety particularly important. In addition to security concepts, attention is given to touch safety during short circuits in low or medium voltage networks. 5 Grounding Concepts and Safety
5.2 Toepassingen | 5.2 Applications | particularly important. In addition to security concepts, attention is given to touch safety during short circuits in low or medium voltage networks. 5 Grounding Concepts and Safety 5.1 Grounding Concepts
5.3 Het aansluiten van een klant op een laagspanningsnet | 5.3 Connecting a customer to a low voltage network | In addition to security concepts, attention is given to touch safety during short circuits in low or medium voltage networks. 5 Grounding Concepts and Safety 5.1 Grounding Concepts 5.2 Applications
5.4 Aardelektrode | 5.4 Grounding Electrode | touch safety during short circuits in low or medium voltage networks. 5 Grounding Concepts and Safety 5.1 Grounding Concepts 5.2 Applications 5.3 Connecting a customer to a low voltage network
5.5 Potentiaalvereffening | 5.5 Potential Equalization | short circuits in low or medium voltage networks. 5 Grounding Concepts and Safety 5.1 Grounding Concepts 5.2 Applications 5.3 Connecting a customer to a low voltage network 5.4 Grounding Electrode
5.6 Gevaarlijke situaties | 5.6 Dangerous Situations | low or medium voltage networks. 5 Grounding Concepts and Safety 5.1 Grounding Concepts 5.2 Applications 5.3 Connecting a customer to a low voltage network 5.4 Grounding Electrode 5.5 Potential Equalization
5.7 Aanrakingsveiligheid | 5.7 Touch Safety | voltage networks. 5 Grounding Concepts and Safety 5.1 Grounding Concepts 5.2 Applications 5.3 Connecting a customer to a low voltage network 5.4 Grounding Electrode 5.5 Potential Equalization 5.6 Dangerous Situations
5.7.1 Kortsluiting in een TT-stelsel | 5.7.1 Short Circuit in a TT System | Grounding Concepts and Safety 5.1 Grounding Concepts 5.2 Applications 5.3 Connecting a customer to a low voltage network 5.4 Grounding Electrode 5.5 Potential Equalization 5.6 Dangerous Situations 5.7 Touch Safety
5.7.2 Kortsluiting in een TN-stelsel | 5.7.2 Short Circuit in a TN System | 5.2 Applications 5.3 Connecting a customer to a low voltage network 5.4 Grounding Electrode 5.5 Potential Equalization 5.6 Dangerous Situations 5.7 Touch Safety 5.7.1 Short Circuit in a TT System
5.7.3 Kortsluitingen in het MS-net | 5.7.3 Short Circuits in the MV Network | a low voltage network 5.4 Grounding Electrode 5.5 Potential Equalization 5.6 Dangerous Situations 5.7 Touch Safety 5.7.1 Short Circuit in a TT System 5.7.2 Short Circuit in a TN System
5 Aardingsconcepten en veiligheid | 5 Grounding Concepts and Safety | 5.5 Potential Equalization 5.6 Dangerous Situations 5.7 Touch Safety 5.7.1 Short Circuit in a TT System 5.7.2 Short Circuit in a TN System 5.7.3 Short Circuits in the MV Network
Netbeheerders transporteren en distribueren elektriciteit op diverse spanningsniveaus. Elk spanningsniveau kent zijn eigen aardingsmethode om de betrouwbaarheid, de beveiliging en de bescherming van mensen en apparatuur te kunnen garanderen. In het verleden zijn de aardingen van de hoog-, midden- en laagspanningsnetten veelal onafhankelijk van elkaar ontworpen en uitgevoerd. | Grid operators transport and distribute electricity at various voltage levels. Each voltage level has its own grounding method to ensure reliability, security, and the protection of people and equipment. In the past, the grounding of high, medium, and low voltage networks was often designed and implemented independently of each other. | Situations 5.7 Touch Safety 5.7.1 Short Circuit in a TT System 5.7.2 Short Circuit in a TN System 5.7.3 Short Circuits in the MV Network 5 Grounding Concepts and Safety
Door het gebruik van storingsgevoelige elektronica moeten de aardingssystemen beter op elkaar afgestemd worden en moeten netbeheerders dit integraal aanpakken. Een aspect van de integrale aanpak is dat de aardingssystemen van netten van verschillende spanningsniveaus aan elkaar worden gekoppeld. De keerzijde hiervan is dat door integratie van aardingssystemen fouten die zich voortdoen in netten met een hogere spanning ook elders in het elektriciteitsnet merkbaar zijn. Ontwerpers moeten zich hiervan terdege bewust zijn. Een extra complicerende factor is dat in het verleden de metalen waterleidingen en elektriciteitskabels met loodmantels aanzienlijk bijdroegen aan de elektrische veiligheid in het laagspanningsnet, omdat ze over een grote lengte contact hadden met de aarde en daardoor hoge spanningsverschillen beperkten. Kunststof vervangt meer en meer de metalen waterleiding. Bij nieuwbouw en vervanging worden veelal kabels met kunststoffen buitenmantel toegepast. Omdat op deze manier het contact met de aarde afneemt, moeten aanvullende maatregelen genomen worden om de veiligheid van de laagspanningsaangeslotenen en -apparatuur te garanderen. Dit gebeurt door het integreren van de aardingssystemen van netten op alle spanningsniveaus en van de overige telecom- en kabeltelevisienetten (Waes, 2003-2). | Due to the use of interference-sensitive electronics, grounding systems need to be better coordinated, and network operators must address this integrally. One aspect of the integral approach is that the grounding systems of networks with different voltage levels are interconnected. The downside of this is that by integrating grounding systems, faults occurring in higher voltage networks can also be noticeable elsewhere in the electrical grid. Designers must be fully aware of this. An additional complicating factor is that in the past, metal water pipes and lead-sheathed electrical cables significantly contributed to electrical safety in the low voltage network because they had extensive contact with the ground, thereby limiting high voltage differences. Plastic is increasingly replacing metal water pipes. In new constructions and replacements, cables with plastic outer sheaths are often used. Since this reduces contact with the ground, additional measures must be taken to ensure the safety of low voltage connections and equipment. This is achieved by integrating the grounding systems of networks at all voltage levels and the other telecom and cable television networks (Waes, 2003-2). | reliability, security, and the protection of people and equipment. In the past, the grounding of high, medium, and low voltage networks was often designed and implemented independently of each other.
Iets wat men zich vaak niet realiseert is dat de stroom, die bij de energiebron naar de aangeslotenen vertrekt, via een retourpad ook weer terug moet keren om een fysisch evenwicht te realiseren. Een belangrijke route hierbij is die van de aarde. Door aardingssystemen bewust in het ontwerp mee te nemen, ontstaat er een betere controle over de routes die de stromen zullen volgen om aan de natuurkundige wetten te kunnen gehoorzamen. | Something that people often do not realize is that the current, which departs from the energy source to the connected devices, must also return via a return path to achieve a physical balance. An important route for this is through the ground. By consciously incorporating grounding systems into the design, better control is achieved over the routes the currents will follow to comply with the laws of physics. | of low voltage connections and equipment. This is achieved by integrating the grounding systems of networks at all voltage levels and the other telecom and cable television networks (Waes, 2003-2).
Een van de meest voorkomende storingen in het net is dat een kabel beschadigd wordt door graafwerkzaamheden. Hierbij kan een sluiting ontstaan tussen een fase en de beschermende omhulling van de kabel. Het zijn meestal deze sluitingen die tot verhoging van de aanrakingspanning leiden. Om deze reden focust de studie van de veiligheid zich op de toegepaste aardingsconcepten en de gevolgen van fase-aardsluitingen. Dit hoofdstuk gaat in op de aspecten rondom de aarding en de veiligheid. De berekening van de grootte van de kortsluitstromen wordt behandeld in hoofdstuk 10. | One of the most common failures in the network is that a cable gets damaged by excavation work. This can cause a short circuit between a phase and the protective sheath of the cable. It is usually these short circuits that lead to an increase in touch voltage. For this reason, the study of safety focuses on the applied grounding concepts and the consequences of phase-to-ground faults. This chapter addresses the aspects surrounding grounding and safety. The calculation of the magnitude of short-circuit currents is covered in chapter 10. | is through the ground. By consciously incorporating grounding systems into the design, better control is achieved over the routes the currents will follow to comply with the laws of physics.
5.1 Aardingsconcepten | 5.1 Grounding Concepts | grounding concepts and the consequences of phase-to-ground faults. This chapter addresses the aspects surrounding grounding and safety. The calculation of the magnitude of short-circuit currents is covered in chapter 10.
De veiligheid van de netten wordt geborgd door het nemen van de juiste veiligheidsmaatregelen tijdens ontwerp, aanleg, bedrijfsvoering, inspectie en onderhoud. Een belangrijk onderdeel van de veiligheid is de veiligheidsaarding. | The safety of the networks is ensured by taking the appropriate safety measures during design, installation, operation, inspection, and maintenance. An important aspect of safety is protective grounding. | the consequences of phase-to-ground faults. This chapter addresses the aspects surrounding grounding and safety. The calculation of the magnitude of short-circuit currents is covered in chapter 10. 5.1 Grounding Concepts
Het aarden van een elektriciteitsnet begint bij het voedingspunt. Dit is meestal de secundaire wikkeling van een transformator. Indien de secundaire wikkeling een naar buiten uitgevoerd sterpunt heeft, kan het sterpunt geaard worden: direct (star) of via een aardingsimpedantie. Indien het voedingspunt geen naar buiten uitgevoerd sterpunt heeft, kan met behulp van een aardingstransformator een kunstmatig sterpunt gecreëerd worden, dat via een impedantie geaard is. Ook bestaat de mogelijkheid om een net niet te aarden. | Grounding an electrical network begins at the power supply point. This is usually the secondary winding of a transformer. If the secondary winding has an externally accessible neutral point, the neutral point can be grounded: directly (solid) or through a grounding impedance. If the power supply point does not have an externally accessible neutral point, an artificial neutral point can be created using a grounding transformer, which is grounded through an impedance. It is also possible to leave a network ungrounded. | Grounding Concepts The safety of the networks is ensured by taking the appropriate safety measures during design, installation, operation, inspection, and maintenance. An important aspect of safety is protective grounding.
Zwevend net | Floating network | externally accessible neutral point, an artificial neutral point can be created using a grounding transformer, which is grounded through an impedance. It is also possible to leave a network ungrounded.
In netwerken met een zwevend sterpunt, zoals afgebeeld in figuur 5.1, bestaat geen specifiek retourpad voor de stromen in de mantels van de kabels, die vloeien tijdens het contact van een fase met de aarde. De retourstromen kunnen nu alleen vloeien door de in het netwerk verspreid aanwezige capaciteiten tussen de fasegeleiders en de mantels van de kabels. Deze stromen zijn capacitief en de grootte is afhankelijk van de totale lengte van het zwevende net achter de voedingstransformator. Zwevende netten worden met name in de MS-distributienetten toegepast. | In networks with a floating neutral point, as depicted in figure 5.1, there is no specific return path for the currents in the cable sheaths that flow during the contact of a phase with the ground. The return currents can now only flow through the capacitances present in the network between the phase conductors and the cable sheaths. These currents are capacitive, and their magnitude depends on the total length of the floating network behind the supply transformer. Floating networks are particularly used in medium voltage (MV) distribution networks. | neutral point, an artificial neutral point can be created using a grounding transformer, which is grounded through an impedance. It is also possible to leave a network ungrounded. Floating network
Figuur 5.1 Netwerk met zwevend sterpunt | Figure 5.1 Network with Floating Neutral Point | currents are capacitive, and their magnitude depends on the total length of the floating network behind the supply transformer. Floating networks are particularly used in medium voltage (MV) distribution networks.
De gekoppelde spanningen tussen de fasen onderling worden in geval van een fase-aardsluiting nauwelijks beïnvloed, zodat de belastingen achter een Dy-transformator er niets van merken. Maar de waarden van de spanningen van de niet gestoorde fasen ten opzichte van aarde zullen toenemen met een factor √3. Dit is afgebeeld met de spanningsvectoren in figuur 5.2. De linkergrafiek toont de spanningsvectoren ten opzichte van de aardpotentiaal. In de normale bedrijfstoestand is de spanning van het niet geaarde sterpunt gelijk aan de aardpotentiaal en valt het beginpunt van de vectoren samen met de oorsprong van de grafiek. In geval van een fase-aardsluiting in fase | The coupled voltages between the phases themselves are hardly affected in the event of a phase-to-ground fault, so the loads behind a Dy-transformer do not notice it. However, the values of the voltages of the unaffected phases relative to ground will increase by a factor of √3. This is illustrated with the voltage vectors in Figure 5.2. The left graph shows the voltage vectors relative to the ground potential. In normal operating conditions, the voltage of the ungrounded neutral point is equal to the ground potential, and the starting point of the vectors coincides with the origin of the graph. In the event of a phase-to-ground fault in phase | on the total length of the floating network behind the supply transformer. Floating networks are particularly used in medium voltage (MV) distribution networks. Figure 5.1 Network with Floating Neutral Point
a | a | point is equal to the ground potential, and the starting point of the vectors coincides with the origin of the graph. In the event of a phase-to-ground fault in phase
is de spanning van die fase ten opzichte van de aarde nul. Als gevolg verschuift het niet geaarde sterpunt van het net in de negatieve richting van de oorspronkelijke spanningsvector van fase | the voltage of that phase with respect to the ground is zero. As a result, the ungrounded neutral point of the network shifts in the negative direction of the original voltage vector of phase | is equal to the ground potential, and the starting point of the vectors coincides with the origin of the graph. In the event of a phase-to-ground fault in phase a
a | a | phase with respect to the ground is zero. As a result, the ungrounded neutral point of the network shifts in the negative direction of the original voltage vector of phase
. Daarmee verschuiven de vectoren van de fasen | . As a result, the vectors of the phases shift | with respect to the ground is zero. As a result, the ungrounded neutral point of the network shifts in the negative direction of the original voltage vector of phase a
b | b | the ungrounded neutral point of the network shifts in the negative direction of the original voltage vector of phase a . As a result, the vectors of the phases shift
en | en | ungrounded neutral point of the network shifts in the negative direction of the original voltage vector of phase a . As a result, the vectors of the phases shift b
c | c | neutral point of the network shifts in the negative direction of the original voltage vector of phase a . As a result, the vectors of the phases shift b en
ook in diezelfde richting. Het gehele stelsel is nu verschoven en dit is zichtbaar gemaakt met de gestreepte vectoren. Als gevolg geven de rode vectoren de spanning aan van de fasen | also in the same direction. The entire system has now shifted, and this is made visible with the striped vectors. As a result, the red vectors indicate the voltage of the phases | point of the network shifts in the negative direction of the original voltage vector of phase a . As a result, the vectors of the phases shift b en c
b | b | the same direction. The entire system has now shifted, and this is made visible with the striped vectors. As a result, the red vectors indicate the voltage of the phases
en | en | same direction. The entire system has now shifted, and this is made visible with the striped vectors. As a result, the red vectors indicate the voltage of the phases b
c | c | direction. The entire system has now shifted, and this is made visible with the striped vectors. As a result, the red vectors indicate the voltage of the phases b en
ten opzichte van de aarde. De gekoppelde spanningen tussen de fasen onderling blijven ongewijzigd, maar de fasespanningen ten opzichte van de aarde wijzigen ingrijpend. | relative to the ground. The coupled voltages between the phases themselves remain unchanged, but the phase voltages relative to the ground change significantly. | The entire system has now shifted, and this is made visible with the striped vectors. As a result, the red vectors indicate the voltage of the phases b en c
De kortsluitstroom in de kortgesloten fase kan enkele honderden Ampère bedragen maar hoeft in beginsel, vanwege de relatief lage kortsluitstroom, niet veel schade aan te richten. Indien het net uitgebreid wordt, moet rekening gehouden worden dat de kortsluitstroom niet te groot wordt. Maatregelen kunnen zijn het zwevende net te splitsen of het aardingsprincipe van het net te wijzigen door het net met een aardingstransformator te aarden. | The short-circuit current in the shorted phase can amount to several hundred Amperes but does not necessarily cause much damage due to the relatively low short-circuit current. If the network is expanded, it must be ensured that the short-circuit current does not become too large. Measures can include splitting the floating network or changing the grounding principle of the network by grounding it with a grounding transformer. | voltage of the phases b en c relative to the ground. The coupled voltages between the phases themselves remain unchanged, but the phase voltages relative to the ground change significantly.
Figuur 5.2 Spanningsvectoren in een net met zwevend sterpunt: zonder (links) en met (rechts) fase-aardsluiting | Figure 5.2 Voltage vectors in a network with a floating neutral point: without (left) and with (right) phase-to-ground connection | the short-circuit current does not become too large. Measures can include splitting the floating network or changing the grounding principle of the network by grounding it with a grounding transformer.
Een fase-aardsluiting in een zwevend net kan in praktijk tot enkele uren blijven bestaan. Dit wordt beschouwd als een belangrijk voordeel omdat het net tijdens de storing in bedrijf kan blijven. Het lokaliseren van de kortsluiting is echter lastig. De foutlocatie is pas bekend als de streng, waarin de fout zich bevindt, wordt afgeschakeld. De fasespanningen nemen na het afschakelen weer de juiste waarden aan. De noodzaak tot het op deze manier zoeken van de fout wordt als een belangrijk nadeel beschouwd. Een ander nadeel is dat het voor komt dat in netwerken met weinig kabellengte de kortsluitstroom bij een fase-aardsluiting zo klein is dat de fout herhaaldelijk verdwijnt en vervolgens herontsteekt, waardoor hoge spanningspieken ontstaan. Dit verschijnsel wordt veroorzaakt doordat door het capacitieve karakter van de foutstroom de kortsluiting dooft op het moment van de maximale waarde van de spanning. Herhaaldelijk ontsteken kan leiden tot overspanningen die 3,5 maal zo groot zijn als de fasespanning (EnergieNed, 1996). Een derde nadeel is dat door de verhoogde spanning tijdens de fase-aardsluiting een tweede kortsluiting ontstaat in een van de gezonde fasen, leidend tot een grote kortsluitstroom waarna het net wordt afgeschakeld. | A phase-to-ground fault in a floating network can persist for several hours in practice. This is considered a significant advantage because the network can remain operational during the fault. However, locating the short circuit is challenging. The fault location is only known when the section containing the fault is disconnected. After disconnection, the phase voltages return to their correct values. The necessity of locating the fault in this manner is considered a major disadvantage. Another disadvantage is that in networks with short cable lengths, the short-circuit current during a phase-to-ground fault can be so small that the fault repeatedly disappears and then reignites, causing high voltage spikes. This phenomenon is caused by the capacitive nature of the fault current, which extinguishes the short circuit at the moment of the maximum voltage value. Repeated reignition can lead to overvoltages that are 3.5 times the phase voltage (EnergieNed, 1996). A third disadvantage is that the increased voltage during the phase-to-ground fault can cause a second short circuit in one of the healthy phases, leading to a large short-circuit current after which the network is disconnected. | principle of the network by grounding it with a grounding transformer. Figure 5.2 Voltage vectors in a network with a floating neutral point: without (left) and with (right) phase-to-ground connection
Figuur 5.3 Star geaard netwerk | Figure 5.3 Star-grounded network | increased voltage during the phase-to-ground fault can cause a second short circuit in one of the healthy phases, leading to a large short-circuit current after which the network is disconnected.
Star geaard net | Star-grounded network | phase-to-ground fault can cause a second short circuit in one of the healthy phases, leading to a large short-circuit current after which the network is disconnected. Figure 5.3 Star-grounded network
In star geaarde netten is het sterpunt van de secundaire wikkeling van de voedingstransformator direct verbonden met de aarde, zoals afgebeeld in figuur 5.3. Met name LS-netten worden star geaard. In werkelijkheid is de aardingsimpedantie geen nul Ohm, maar wordt deze bepaald door de aardverspreidingsweerstand. Dit retourpad voor de aardstromen heeft een lage impedantie. Fase-aardsluitingen leiden daarom tot grote kortsluitstromen en veroorzaken hierdoor spanningsdips in het net. In tegenstelling tot een fout in een zwevend net zal een eenmaal ontstane fout in een star geaard net meestal niet spontaan doven. In een geaard net treden relatief grote foutstromen op. Dit wordt beschouwd als een voordeel omdat de fout met behulp van de beveiliging goed is te detecteren en daarmee selectief kan worden afgeschakeld. Bij het ontwerp van een net moet rekening gehouden worden met de situatie dat de retourgeleiders en kabelmantels in staat zijn deze kortsluitstromen te voeren. | In star-grounded networks, the neutral point of the secondary winding of the power transformer is directly connected to the ground, as shown in figure 5.3. Specifically, low-voltage networks are star-grounded. In reality, the grounding impedance is not zero Ohms but is determined by the ground resistance. This return path for the ground currents has a low impedance. Therefore, phase-to-ground faults lead to large short-circuit currents and cause voltage dips in the network. Unlike a fault in an ungrounded network, a fault in a star-grounded network usually does not extinguish spontaneously. In a grounded network, relatively large fault currents occur. This is considered an advantage because the fault can be easily detected with protection devices and can be selectively disconnected. When designing a network, it must be taken into account that the return conductors and cable sheaths are capable of carrying these short-circuit currents. | can cause a second short circuit in one of the healthy phases, leading to a large short-circuit current after which the network is disconnected. Figure 5.3 Star-grounded network Star-grounded network
Tijdens een fase-aardsluiting zullen de niet gestoorde fasen nauwelijks beïnvloed worden. Rekening moet worden gehouden met de mogelijkheid dat de aardpotentiaal op de foutlocatie sterk verhoogd wordt. | During a phase-to-ground fault, the unaffected phases will be barely influenced. Consideration must be given to the possibility that the ground potential at the fault location may be significantly increased. | devices and can be selectively disconnected. When designing a network, it must be taken into account that the return conductors and cable sheaths are capable of carrying these short-circuit currents.
Figuur 5.4 Impedantie geaard netwerk | Figure 5.4 Impedance Grounded Network | During a phase-to-ground fault, the unaffected phases will be barely influenced. Consideration must be given to the possibility that the ground potential at the fault location may be significantly increased.
Impedantie geaard net | Impedance grounded network | unaffected phases will be barely influenced. Consideration must be given to the possibility that the ground potential at the fault location may be significantly increased. Figure 5.4 Impedance Grounded Network
Aarding van het sterpunt via een impedantie wordt in MS-netten toegepast en gebeurt meestal met een spoel of met een aardingstransformator, zoals afgebeeld in figuur 5.4. De impedantie van een spoel en een aardingstransformator bestaat voornamelijk uit reactantie. De weerstand is zeer klein, zodat de verliezen bij asymmetrie, wanneer er een stroom via het sterpunt kan lopen, klein zijn. Sterpuntsaarding via een impedantie wordt toegepast om de hoge foutstromen te beperken. De foutstroom en de retourstroom zijn nog steeds hoog genoeg om door de beveiliging te worden gedetecteerd en om selectief te worden afgeschakeld. Dit is noodzakelijk wanneer kabels worden toegepast met een beperkte doorsnede van het aardscherm, zoals kunststofkabels. | Grounding the neutral point via an impedance is applied in medium voltage networks and is usually done with a coil or a grounding transformer, as shown in Figure 5.4. The impedance of a coil and a grounding transformer consists mainly of reactance. The resistance is very small, so the losses during asymmetry, when a current can flow through the neutral point, are minimal. Neutral point grounding via an impedance is used to limit the high fault currents. The fault current and the return current are still high enough to be detected by the protection system and to be selectively disconnected. This is necessary when cables with a limited cross-section of the earth shield, such as plastic cables, are used. | be barely influenced. Consideration must be given to the possibility that the ground potential at the fault location may be significantly increased. Figure 5.4 Impedance Grounded Network Impedance grounded network
Netwerken kunnen worden geaard met een hoge of een lage impedantie. In netwerken die met een hoge impedantie geaard zijn, zullen de fase-aardsluitstromen klein zijn en zullen de niet gestoorde fasen een spanning ten opzichte van de aarde aannemen die hoger is dan in de ongestoorde situatie. In netwerken die met een lage impedantie geaard zijn, is de fase-aardsluitstroom groot, maar wordt deze beperkt door de impedantie, bijvoorbeeld een spoel. Hierdoor is de kortsluitstroom gecontroleerd kleiner dan in een star geaarde netsituatie en zijn spanningsdips en verhoging van de aardpotentiaal op de storingslocatie beperkt. | Networks can be grounded with either high or low impedance. In networks that are grounded with high impedance, the phase-to-ground fault currents will be small, and the undisturbed phases will assume a voltage relative to the ground that is higher than in the undisturbed situation. In networks that are grounded with low impedance, the phase-to-ground fault current is large, but it is limited by the impedance, for example, a coil. As a result, the short-circuit current is controlled to be smaller than in a solidly grounded network situation, and voltage dips and the increase of ground potential at the fault location are limited. | be detected by the protection system and to be selectively disconnected. This is necessary when cables with a limited cross-section of the earth shield, such as plastic cables, are used.
Sterpuntsaarding met een lage impedantie werd in het verleden alleen toegepast bij kabels met kleine doorsnede van het aardscherm. Tegenwoordig wordt deze vorm van sterpuntsaarding steeds vaker toegepast omdat dit een goed compromis is tussen star geaarde netten en netten die met een hoge impedantie geaard zijn. In middenspanningsnetten die geaard zijn met een lage impedantie, moet bij lange strengen worden berekend of een fase-aardfout aan het einde van de streng niet leidt tot een foutstroom die te klein is om door de fasebeveiliging gedetecteerd te worden. Dit aspect dient bij ieder netontwerp te worden gecontroleerd. Indien meerdere strengen in serie worden bedreven, dient de beveiliging van de voorliggende streng te functioneren als back-up beveiliging van de onderliggende streng. De back-up beveiliging moet in staat zijn om een aardfout aan het einde van de achterliggende streng te detecteren. Ook dit hoort bij ieder ontwerp gecontroleerd te worden. | Low-impedance grounding was previously only applied to cables with a small cross-section of the earth shield. Nowadays, this form of grounding is increasingly used because it offers a good compromise between solidly grounded networks and networks grounded with high impedance. In medium voltage networks that are grounded with low impedance, it must be calculated for long feeders whether a phase-to-ground fault at the end of the feeder does not result in a fault current that is too small to be detected by the phase protection. This aspect must be checked in every network design. If multiple feeders are operated in series, the protection of the preceding feeder must function as backup protection for the underlying feeder. The backup protection must be able to detect a ground fault at the end of the subsequent feeder. This too must be checked in every design. | the short-circuit current is controlled to be smaller than in a solidly grounded network situation, and voltage dips and the increase of ground potential at the fault location are limited.
Een bijzondere vorm van impedantie-aarding is de toepassing van een blusspoel, ook wel Petersen spoel genoemd. De waarde van de spoel wordt zodanig berekend dat de capacitieve stroom bij een fase-aardfout door de inductieve stroomcomponent van de spoel gecompenseerd wordt. Een nadeel dat bij deze oplossing kan optreden is dat de fase-aardsluitstroom bij toepassing van een blusspoel zeer klein wordt. Hierdoor kan een fout doven en eventueel weer herontsteken. Deze manier van aarden wordt met name bij bovengrondse netten toegepast. De oplossing werkt in de praktijk niet goed indien zich veel kabels in het net bevinden. | A special form of impedance grounding is the use of an arc suppression coil, also known as a Petersen coil. The value of the coil is calculated in such a way that the capacitive current during a phase-to-ground fault is compensated by the inductive current component of the coil. A disadvantage that can occur with this solution is that the phase-to-ground fault current becomes very small when using an arc suppression coil. As a result, a fault can extinguish and potentially reignite. This method of grounding is primarily used in overhead networks. The solution does not work well in practice if there are many cables in the network. | for the underlying feeder. The backup protection must be able to detect a ground fault at the end of the subsequent feeder. This too must be checked in every design.
Met aardingstransformator geaard netwerk | Network grounded with grounding transformer | extinguish and potentially reignite. This method of grounding is primarily used in overhead networks. The solution does not work well in practice if there are many cables in the network.
In het geval dat geen sterpunt beschikbaar is, kan het netwerk geaard worden met behulp van een aardingstransformator, ook wel sterpuntstransformator of nulpunttransformator genoemd. De impedantie van een aardingstransformator bestaat voornamelijk uit reactantie, zodat de verliezen beperkt zijn. Afhankelijk van de grootte van de impedantie van de aardingstransformator kan deze manier van aarden worden behandeld als aarding met hoge of met lage impedantie. De opbouw en de werking van de aardingstransformator wordt beschreven in paragraaf 8.4. | In the event that no neutral point is available, the network can be grounded using a grounding transformer, also known as a neutral grounding transformer or zero-sequence transformer. The impedance of a grounding transformer consists mainly of reactance, so the losses are limited. Depending on the size of the impedance of the grounding transformer, this method of grounding can be treated as high-impedance or low-impedance grounding. The construction and operation of the grounding transformer are described in section 8.4. | method of grounding is primarily used in overhead networks. The solution does not work well in practice if there are many cables in the network. Network grounded with grounding transformer
Figuur 5.5 Met nulpunttransformator geaard netwerk | Figure 5.5 Network grounded with a grounding transformer | impedance of the grounding transformer, this method of grounding can be treated as high-impedance or low-impedance grounding. The construction and operation of the grounding transformer are described in section 8.4.
5.2 Toepassingen | 5.2 Applications | grounding can be treated as high-impedance or low-impedance grounding. The construction and operation of the grounding transformer are described in section 8.4. Figure 5.5 Network grounded with a grounding transformer
Hoogspanningsnetten | Hoogspanningsnetten | be treated as high-impedance or low-impedance grounding. The construction and operation of the grounding transformer are described in section 8.4. Figure 5.5 Network grounded with a grounding transformer 5.2 Applications
Bij een spanningsniveau vanaf 50 kV wordt het sterpunt direct of via een blusspoel geaard. Als er in een direct geaard net een éénfase-aardsluiting optreedt, dan is de aardsluitstroom van dezelfde orde grootte als de kortsluitstroom bij een driefasenkortsluiting en de beveiligingsinrichting zal het gestoorde circuit afschakelen. Een aantal bovengrondse netten is via een blusspoel, een zogenaamde Petersen-spoel, geaard. In een blusspoel geaard net is de waarde van de aardsluitstroom klein, zodat de beveiligingsinrichting van de gestoorde fase niet afschakelt maar slechts een richtingsindicatie geeft. Veel fase-aardfouten in bovengrondse netten worden namelijk veroorzaakt door takken of andere objecten of door blikseminslag. Deze fouten zijn zelfherstellend en leiden niet tot een onderbreking. | At a voltage level of 50 kV or higher, the neutral point is grounded directly or via an arc suppression coil. If a single-phase ground fault occurs in a directly grounded network, the ground fault current is of the same magnitude as the short-circuit current in a three-phase short circuit, and the protection device will disconnect the faulty circuit. Several overhead networks are grounded via an arc suppression coil, also known as a Petersen coil. In a network grounded with an arc suppression coil, the value of the ground fault current is small, so the protection device of the faulty phase does not disconnect but only provides a directional indication. Many phase-to-ground faults in overhead networks are caused by branches or other objects or by lightning strikes. These faults are self-healing and do not lead to an interruption. | treated as high-impedance or low-impedance grounding. The construction and operation of the grounding transformer are described in section 8.4. Figure 5.5 Network grounded with a grounding transformer 5.2 Applications Hoogspanningsnetten
Middenspanningsnetten | Middenspanningsnetten | directional indication. Many phase-to-ground faults in overhead networks are caused by branches or other objects or by lightning strikes. These faults are self-healing and do not lead to an interruption.
De meeste middenspanningsnetten worden gevoed via HS/MS-transformatoren, waarvan de secundaire wikkelingen in driehoekschakeling geconfigureerd zijn. Ook de primaire wikkelingen van de aangesloten MS/LS-distributietransformatoren zijn in driehoekschakeling geconfigureerd. De middenspanningsnetten hoeven in principe niet geaard te zijn, maar veel van deze middenspanningsnetten zijn impedantie geaard. Figuur 5.6 toont de aardingssituatie in het distributienet en de schakelingen van de HS/MS-transformator en de MS/LS-transformator. Het HS-net is impedantie geaard (vaak Petersen aarding). Het MS-net is zwevend en het LS-net is impedantie geaard. Soms worden MS-netten met een aardingstransformator geaard. | Most medium voltage networks are fed via HV/MV transformers, whose secondary windings are configured in a delta connection. The primary windings of the connected MV/LV distribution transformers are also configured in a delta connection. Medium voltage networks do not necessarily need to be grounded, but many of these medium voltage networks are impedance grounded. Figure 5.6 shows the grounding situation in the distribution network and the configurations of the HV/MV transformer and the MV/LV transformer. The HV network is impedance grounded (often Petersen grounding). The MV network is floating, and the LV network is impedance grounded. Sometimes MV networks are grounded with a grounding transformer. | indication. Many phase-to-ground faults in overhead networks are caused by branches or other objects or by lightning strikes. These faults are self-healing and do not lead to an interruption. Middenspanningsnetten
Figuur 5.6 Transformatorschakelingen van HS naar LS | Figure 5.6 Transformer connections from HV to LV | The HV network is impedance grounded (often Petersen grounding). The MV network is floating, and the LV network is impedance grounded. Sometimes MV networks are grounded with a grounding transformer.
In een klein net zal een fase-aardsluiting in een kabel niet direct leiden tot een afschakeling. Zolang de kortsluitstroom niet schadelijk is voor de kabelschermen, kan de fout blijven staan. De fout kan worden opgespoord en kan worden geïsoleerd zonder dat de energielevering onderbroken wordt. Doordat bij een fase-aardfout in een zwevend net de spanning tussen fase en aarde van de niet gestoorde fasen even groot wordt als de gekoppelde spanning, kan dit leiden tot een tweede fase-aardsluiting, die samen met de eerste sluiting wel leidt tot een grote kortsluitstroom en dus tot een afschakeling. | In a small network, a phase-to-ground fault in a cable will not immediately lead to a disconnection. As long as the short-circuit current is not harmful to the cable shields, the fault can remain. The fault can be detected and isolated without interrupting the power supply. Because in a floating network, a phase-to-ground fault causes the voltage between phase and ground of the unaffected phases to become as high as the line voltage, this can lead to a second phase-to-ground fault. Together with the first fault, this will result in a large short-circuit current and thus a disconnection. | grounding). The MV network is floating, and the LV network is impedance grounded. Sometimes MV networks are grounded with a grounding transformer. Figure 5.6 Transformer connections from HV to LV
In grote middenspanningsnetten kan bij een fase-aardfout de capacitieve kortsluitstroom zo groot worden dat deze wel schade aan de kabels kan aanrichten. In dat geval is het wel gewenst dat een fase-aardsluiting wordt afgeschakeld. Het middenspanningsnet wordt dan impedantie geaard. Dit gebeurt hetzij met een spoel op het sterpunt, hetzij met behulp van een aardingstransformator indien er geen sterpunt aanwezig is. Elke fase-aardsluiting zal in dat geval leiden tot aanspreken van de beveiliging. | In large medium-voltage networks, a phase-to-ground fault can cause the capacitive short-circuit current to become so large that it can damage the cables. In that case, it is desirable for a phase-to-ground fault to be disconnected. The medium-voltage network is then impedance grounded. This is done either with a coil at the neutral point or with the help of a grounding transformer if no neutral point is present. In that case, any phase-to-ground fault will trigger the protection system. | high as the line voltage, this can lead to a second phase-to-ground fault. Together with the first fault, this will result in a large short-circuit current and thus a disconnection.
Bij het ontwerpen van een middenspanningsnet moet rekening gehouden worden met onderstaande zaken: | When designing a medium voltage network, the following considerations must be taken into account: | coil at the neutral point or with the help of a grounding transformer if no neutral point is present. In that case, any phase-to-ground fault will trigger the protection system.
de grootte van de fase-aarde kortsluitstroom neemt af bij toenemende afstand van de kortsluitplaats tot de beveiliging | the magnitude of the phase-to-ground short-circuit current decreases with increasing distance from the short-circuit location to the protection system | no neutral point is present. In that case, any phase-to-ground fault will trigger the protection system. When designing a medium voltage network, the following considerations must be taken into account:
de kortsluitstroom moet groot genoeg zijn om door de beveiliging te kunnen worden gedetecteerd | the short-circuit current must be large enough to be detected by the protection system | medium voltage network, the following considerations must be taken into account: the magnitude of the phase-to-ground short-circuit current decreases with increasing distance from the short-circuit location to the protection system
bij meerdere strengen in serie moet de back-up beveiliging in de voorliggende streng in staat zijn om een aardfout aan het einde van de achterliggende streng te detecteren | with multiple strings in series, the backup protection in the preceding string must be able to detect a ground fault at the end of the subsequent string | the phase-to-ground short-circuit current decreases with increasing distance from the short-circuit location to the protection system the short-circuit current must be large enough to be detected by the protection system
de schade aan de kabel op de foutplaats moet groot genoeg zijn om door de reparatieploeg ontdekt te kunnen worden | the damage to the cable at the fault location must be significant enough to be detected by the repair crew | the protection system with multiple strings in series, the backup protection in the preceding string must be able to detect a ground fault at the end of the subsequent string
de kortsluitstroom moet klein genoeg zijn om de diepte van de spanningsdips te beperken, om geen veiligheidsproblemen te veroorzaken en om te voorkomen dat de mantelstroom in de kabel te groot wordt. | The short-circuit current must be small enough to limit the depth of the voltage dips, to avoid safety issues, and to prevent the sheath current in the cable from becoming too large. | a ground fault at the end of the subsequent string the damage to the cable at the fault location must be significant enough to be detected by the repair crew
Het is duidelijk dat niet altijd aan alle eisen maximaal kan worden voldaan. Het ontwerpen van een middenspanningsnet is dan ook altijd een proces waarbij op tegenstrijdige eisen geoptimaliseerd moet worden. Onder alle omstandigheden moet echter de aanrakingsveiligheid gewaarborgd zijn. | It is clear that not all requirements can always be fully met. Designing a medium voltage network is therefore always a process of optimizing conflicting requirements. However, under all circumstances, touch safety must be guaranteed. | current must be small enough to limit the depth of the voltage dips, to avoid safety issues, and to prevent the sheath current in the cable from becoming too large.
Impedantie geaarde middenspanningsnetten worden ontworpen op een fase-aardsluitstroom van 2000 A bij het onderstation. Deze waarde mag niet leiden tot onacceptabele spanningsstijging van de lokale aarde en ook niet tot te grote stromen door de kabelmantels. | Impedance-grounded medium voltage networks are designed for a phase-to-ground fault current of 2000 A at the substation. This value must not lead to an unacceptable voltage rise of the local ground and also must not result in excessively high currents through the cable sheaths. | all requirements can always be fully met. Designing a medium voltage network is therefore always a process of optimizing conflicting requirements. However, under all circumstances, touch safety must be guaranteed.
Laagspanningsnetten | Laagspanningsnetten | at the substation. This value must not lead to an unacceptable voltage rise of the local ground and also must not result in excessively high currents through the cable sheaths.
Laagspanningsnetten worden gevoed met MS/LS-distributietransformatoren, waarvan de secundaire wikkelingen in sterschakeling geconfigureerd zijn. In principe zijn deze netten star geaard. De aardingsimpedantie wordt bepaald door het aantal aardelektroden en de aardverspreidingsweerstand van de aardelektroden. De kortsluitstroom bij een fase-aardsluiting in het LS-net is groot en zal door de beveiliging in het netstation afgeschakeld worden. | Low-voltage networks are powered by MV/LV distribution transformers, whose secondary windings are configured in a star connection. In principle, these networks are solidly grounded. The grounding impedance is determined by the number of ground electrodes and the ground spread resistance of the ground electrodes. The short-circuit current in the event of a phase-to-ground fault in the LV network is high and will be interrupted by the protection system in the substation. | the substation. This value must not lead to an unacceptable voltage rise of the local ground and also must not result in excessively high currents through the cable sheaths. Laagspanningsnetten
5.3 Het aansluiten van een klant op een laagspanningsnet | 5.3 Connecting a customer to a low-voltage network | the ground electrodes. The short-circuit current in the event of a phase-to-ground fault in the LV network is high and will be interrupted by the protection system in the substation.
De aardingssystemen in laagspanningsnetten achter de distributietransformator kunnen op diverse wijzen worden uitgevoerd, waarbij ten aanzien van de veiligheid naar keuze veel of weinig verantwoording bij de aangeslotene wordt gelegd. De varianten zijn beschreven in de internationale norm IEC 60364. In de benaming van de aardingssystemen wordt een lettercodering gebruikt, waarvan de meest gebruikte zijn aangeduid met TT en TN. De eerste letter heeft betrekking op de aarding van de voedingsbron, dus in de meeste gevallen van de distributietransformator. Deze heeft bij de standaard 400V-laagspanningsnetten de aanduiding T, die staat voor ‘Terre’, hetgeen betekent dat het sterpunt van de secundaire wikkeling van de distributietransformator star geaard is. De norm voorziet ook in een geïsoleerd of met hoge impedantie geaard sterpunt, aangeduid met de letter I. Voor de tweede en volgende letters geldt: | The grounding systems in low-voltage networks behind the distribution transformer can be implemented in various ways, with the responsibility for safety being placed more or less on the connected party. The variants are described in the international standard IEC 60364. In the naming of the grounding systems, a letter coding is used, with the most commonly used being designated as TT and TN. The first letter pertains to the grounding of the power source, which in most cases is the distribution transformer. In standard 400V low-voltage networks, this is designated by the letter T, which stands for 'Terre', meaning that the neutral point of the secondary winding of the distribution transformer is solidly grounded. The standard also provides for an isolated or high-impedance grounded neutral point, indicated by the letter I. For the second and subsequent letters: | event of a phase-to-ground fault in the LV network is high and will be interrupted by the protection system in the substation. 5.3 Connecting a customer to a low-voltage network
T: installatie van de aangeslotene is direct geaard | T: installation of the connected party is directly grounded | of the distribution transformer is solidly grounded. The standard also provides for an isolated or high-impedance grounded neutral point, indicated by the letter I. For the second and subsequent letters:
N: installatie van de aangeslotene is met de bedrijfsaarde verbonden | N: installation of the connected party is connected to the system ground | also provides for an isolated or high-impedance grounded neutral point, indicated by the letter I. For the second and subsequent letters: T: installation of the connected party is directly grounded
C: nulgeleider en beschermingsleiding zijn in een gemeenschappelijke geleider (PEN) uitgevoerd | C: neutral conductor and protective conductor are combined in a common conductor (PEN) | the letter I. For the second and subsequent letters: T: installation of the connected party is directly grounded N: installation of the connected party is connected to the system ground
S: nulgeleider en beschermingsleiding zijn met twee separate geleiders uitgevoerd | S: neutral conductor and protective conductor are implemented with two separate conductors | connected party is directly grounded N: installation of the connected party is connected to the system ground C: neutral conductor and protective conductor are combined in a common conductor (PEN)
De beschermingsleiding wordt aangeduid met de term PE, dat staat voor ‘Protective Earth’. Meestal wordt de afscherming van een kabel gebruikt als PE-geleider. | The protective conductor is referred to by the term PE, which stands for 'Protective Earth.' Usually, the shielding of a cable is used as the PE conductor. | connected to the system ground C: neutral conductor and protective conductor are combined in a common conductor (PEN) S: neutral conductor and protective conductor are implemented with two separate conductors
Figuur 5.7 TT-stelsel | Figure 5.7 TT system | two separate conductors The protective conductor is referred to by the term PE, which stands for 'Protective Earth.' Usually, the shielding of a cable is used as the PE conductor.
TT aardingssysteem | TT grounding system | protective conductor is referred to by the term PE, which stands for 'Protective Earth.' Usually, the shielding of a cable is used as the PE conductor. Figure 5.7 TT system
In een TT-stelsel is één punt van de voedingsbron rechtstreeks met aarde verbonden en zijn de metalen gestellen in de installatie verbonden met aardelektroden die elektrisch onafhankelijk zijn van de aardelektroden van de voedingsbron. In het TT-stelsel zijn de aardingssystemen van de aangeslotene en het distributienet dus gescheiden, zie figuur 5.7. In dit stelsel is de klant zelf verantwoordelijk voor het onderhoud en het goed functioneren van zijn eigen aarding. Het retourpad voor fase-aardsluitingen bestaat uit de aardelektrode bij de aangeslotene, de aardelektroden in het netstation en de weerstand van de grond tussen de aangeslotene en het netstation. De weerstand van het retourpad moet zo klein zijn dat de beveiliging een fase-aardfout kan afschakelen. Een vuistregel voor de weerstand R | In a TT system, one point of the power source is directly connected to the earth, and the metal frames in the installation are connected to grounding electrodes that are electrically independent of the grounding electrodes of the power source. In the TT system, the grounding systems of the consumer and the distribution network are thus separated, see figure 5.7. In this system, the customer is responsible for the maintenance and proper functioning of their own grounding. The return path for phase-to-earth faults consists of the grounding electrode at the consumer, the grounding electrodes at the substation, and the resistance of the ground between the consumer and the substation. The resistance of the return path must be low enough for the protection to disconnect a phase-to-earth fault. A rule of thumb for the resistance R | referred to by the term PE, which stands for 'Protective Earth.' Usually, the shielding of a cable is used as the PE conductor. Figure 5.7 TT system TT grounding system
c | c | consumer and the substation. The resistance of the return path must be low enough for the protection to disconnect a phase-to-earth fault. A rule of thumb for the resistance R
van het retourpad in het geval dat smeltveiligheden zijn toegepast is: | of the return path in the event that fuses are used is: | and the substation. The resistance of the return path must be low enough for the protection to disconnect a phase-to-earth fault. A rule of thumb for the resistance R c
[ | [ | enough for the protection to disconnect a phase-to-earth fault. A rule of thumb for the resistance R c of the return path in the event that fuses are used is:
5.1 | 5.1 | for the protection to disconnect a phase-to-earth fault. A rule of thumb for the resistance R c of the return path in the event that fuses are used is: [
] | ] | the protection to disconnect a phase-to-earth fault. A rule of thumb for the resistance R c of the return path in the event that fuses are used is: [ 5.1
waarin | waarin | protection to disconnect a phase-to-earth fault. A rule of thumb for the resistance R c of the return path in the event that fuses are used is: [ 5.1 ]
I | I | to disconnect a phase-to-earth fault. A rule of thumb for the resistance R c of the return path in the event that fuses are used is: [ 5.1 ] waarin
n | n | disconnect a phase-to-earth fault. A rule of thumb for the resistance R c of the return path in the event that fuses are used is: [ 5.1 ] waarin I
de nominale stroom van de smeltveiligheid is (Provoost, 2004). De impedantie van het totale circuit moet laag genoeg zijn om de spanningsverhoging te beperken en een snelle afschakeling te verzekeren. Deze methode is alleen haalbaar bij grond met een lage specifieke weerstand. Een smeltpatroon van 16 A heeft op grond van vergelijking 5.1 een impedantie van 2 Ω nodig voor het retourpad. Op zandgrond is een smeltpatroon van 16 A niet haalbaar in dit aardingssysteem. | the nominal current of the fuse is (Provoost, 2004). The impedance of the entire circuit must be low enough to limit the voltage rise and ensure a quick disconnection. This method is only feasible in soil with low specific resistance. A fuse of 16 A requires an impedance of 2 Ω for the return path based on equation 5.1. In sandy soil, a fuse of 16 A is not feasible in this grounding system. | a phase-to-earth fault. A rule of thumb for the resistance R c of the return path in the event that fuses are used is: [ 5.1 ] waarin I n
In het verleden was er bij de juiste grondsoort nooit een probleem met de grootte van de weerstand van het retourpad, mede door het op veel plaatsen aanwezig zijnde contact met aarde. Echter, door het vervangen van metalen leidingen door kunststof leidingen en door het toepassen van kunststof in kabelmantels, wordt in het TT-stelsel de weerstand van het aardingscircuit ten opzichte van de oude situatie vergroot. In de gevallen dat de retourweerstand niet klein genoeg is, worden als alternatief (door de aangeslotene) aardlekschakelaars ingezet. Een voordeel van de aardlekschakelaar is dat deze al bij een kleine fase-aardfoutstroom uitschakelt waardoor de kans op elektrocutie, beschadiging of brand klein is. Een nadeel is dat aardlekschakelaars kunnen weigeren, waardoor de fout blijft staan. Dit maakt het nodig dat aardlekschakelaars regelmatig door de aangeslotenen moeten worden getest. | In the past, with the right type of soil, there was never an issue with the size of the resistance of the return path, partly due to the widespread contact with the earth. However, by replacing metal pipes with plastic pipes and using plastic in cable sheaths, the resistance of the grounding circuit in the TT system has increased compared to the old situation. In cases where the return resistance is not low enough, residual current devices (RCDs) are used as an alternative by the connected party. An advantage of the RCD is that it trips at a small phase-to-earth fault current, reducing the risk of electrocution, damage, or fire. A disadvantage is that RCDs can fail, leaving the fault in place. This necessitates regular testing of RCDs by the connected parties. | A requires an impedance of 2 Ω for the return path based on equation 5.1. In sandy soil, a fuse of 16 A is not feasible in this grounding system.
TN aardingssysteem | TN grounding system | reducing the risk of electrocution, damage, or fire. A disadvantage is that RCDs can fail, leaving the fault in place. This necessitates regular testing of RCDs by the connected parties.
In het TN-stelsel wordt de veilige aarding door de netbeheerder geleverd. In principe is één punt van de voedingsbron rechtstreeks met aarde verbonden en zijn de metalen gestellen in de installaties door beschermingsleidingen met dat punt verbonden. Dit wordt gerealiseerd met een laagohmige verbinding tussen de veiligheidsaarde van de aangeslotene en de bedrijfsaarde van het netstation. Een TN-stelsel levert altijd een voldoende lage impedantie voor het retourpad, met een orde grootte van 0,3 Ω. Met de vuistregel (vergelijking 5.1) kan worden berekend dat bij deze impedantie van het retourpad alle gangbare smeltpatronen afschakelen bij een fase-aardfout in de installatie van de aangeslotene. | In the TN system, safe grounding is provided by the network operator. In principle, one point of the power source is directly connected to the ground, and the metal frames in the installations are connected to that point via protective conductors. This is achieved with a low-ohm connection between the protective earth of the connected party and the operational earth of the substation. A TN system always provides a sufficiently low impedance for the return path, with an order of magnitude of 0.3 Ω. Using the rule of thumb (equation 5.1), it can be calculated that with this impedance of the return path, all common fuses will disconnect in the event of a phase-to-earth fault in the installation of the connected party. | of electrocution, damage, or fire. A disadvantage is that RCDs can fail, leaving the fault in place. This necessitates regular testing of RCDs by the connected parties. TN grounding system
Figuur 5.8 TN-S-stelsel | Figure 5.8 TN-S system | can be calculated that with this impedance of the return path, all common fuses will disconnect in the event of a phase-to-earth fault in the installation of the connected party.
In het TN-stelsel zijn diverse uitvoeringsvormen mogelijk. In een TN-S-stelsel zijn de nul- en PE-geleider gescheiden uitgevoerd, zie figuur 5.8. Het elektriciteitsvoorzieningscircuit en het aardingscircuit zijn gescheiden en de stroomverdeling is goed gedefinieerd. Dit stelsel gebruikt vijf geleiders, die in de meeste laagspanningskabels voorkomen: drie fasen, nul en afscherming als PE-geleider. Een onderbreking in de PE-geleider leidt in dit systeem tot een veiligheidsrisico. | In the TN system, various configurations are possible. In a TN-S system, the neutral and PE conductor are separated, see figure 5.8. The power supply circuit and the grounding circuit are separated, and the current distribution is well-defined. This system uses five conductors, which are found in most low-voltage cables: three phases, neutral, and shielding as the PE conductor. An interruption in the PE conductor in this system leads to a safety risk. | with this impedance of the return path, all common fuses will disconnect in the event of a phase-to-earth fault in the installation of the connected party. Figure 5.8 TN-S system
Figuur 5.9 TN-C-stelsel | Figure 5.9 TN-C system | which are found in most low-voltage cables: three phases, neutral, and shielding as the PE conductor. An interruption in the PE conductor in this system leads to a safety risk.
In een TN-C-stelsel zijn de nulgeleider en de PE-geleider gecombineerd in een enkele PEN-geleider, zie figuur 5.9. Deze systemen gebruiken maar 4 geleiders en worden vaak toegepast in industriële netten. Een onderbreking in de PEN-geleider leidt tot spanningsproblemen en tot een veiligheidsrisico. | In a TN-C system, the neutral conductor and the PE conductor are combined into a single PEN conductor, see figure 5.9. These systems use only 4 conductors and are often applied in industrial networks. An interruption in the PEN conductor leads to voltage problems and a safety risk. | most low-voltage cables: three phases, neutral, and shielding as the PE conductor. An interruption in the PE conductor in this system leads to a safety risk. Figure 5.9 TN-C system
Figuur 5.10 TN-C-S-stelsel | Figure 5.10 TN-C-S system | see figure 5.9. These systems use only 4 conductors and are often applied in industrial networks. An interruption in the PEN conductor leads to voltage problems and a safety risk.
Het TN-C-S-stelsel is een combinatie van een TN-C- en een TN-S-stelsel, zie figuur 5.10. Het transportgedeelte vanaf de distributietransformator heeft het TN-C-stelsel en het distributiegedeelte bij de aangeslotenen heeft het TN-S-stelsel. | The TN-C-S system is a combination of a TN-C and a TN-S system, see figure 5.10. The transport section from the distribution transformer uses the TN-C system, and the distribution section at the consumers uses the TN-S system. | systems use only 4 conductors and are often applied in industrial networks. An interruption in the PEN conductor leads to voltage problems and a safety risk. Figure 5.10 TN-C-S system
Tegenwoordig zijn de meeste laagspanningsnetten gebaseerd op het TN-C-S-stelsel. Om de veiligheid te garanderen zijn in het TN-C gedeelte de vieraderige kabels voorzien van een koperen afscherming van voldoende geleiderdoorsnede. In alle moffen worden de nul en de afscherming met elkaar verbonden. Ook in de installatie van de aangeslotene zijn nul en PE met elkaar verbonden. Hierdoor ontstaat een veilig retourpad, zelfs indien de nulgeleider is onderbroken. Het risico dat zowel de nulgeleider als de afscherming zijn onderbroken wordt verwaarloosd (Provoost, 2004). Deze manier van aarden combineert de voordelen van de TN-S- en TN-C-stelsels. De parallelschakeling van de nulgeleider en de afscherming reduceert bovendien de retourimpedantie voor asymmetrische stromen en reduceert spanningsdips als gevolg van het starten van zware enkelfasige belastingen. Figuur 5.11 geeft schematisch de toepassing van het TN-C-S-stelsel weer voor een streng van het laagspanningsnet. | Nowadays, most low-voltage networks are based on the TN-C-S system. To ensure safety, the four-core cables in the TN-C section are equipped with a copper shield of sufficient conductor cross-section. In all joints, the neutral and the shield are connected. In the installation of the consumer, the neutral and PE are also connected. This creates a safe return path, even if the neutral conductor is interrupted. The risk of both the neutral conductor and the shield being interrupted is negligible (Provoost, 2004). This method of grounding combines the advantages of the TN-S and TN-C systems. The parallel connection of the neutral conductor and the shield also reduces the return impedance for asymmetric currents and reduces voltage dips caused by the starting of heavy single-phase loads. Figure 5.11 schematically shows the application of the TN-C-S system for a section of the low-voltage network. | TN-C and a TN-S system, see figure 5.10. The transport section from the distribution transformer uses the TN-C system, and the distribution section at the consumers uses the TN-S system.
Figuur 5.11 Laagspanningsstreng met TN-C-S-stelsel | Figure 5.11 Low-voltage line with TN-C-S system | currents and reduces voltage dips caused by the starting of heavy single-phase loads. Figure 5.11 schematically shows the application of the TN-C-S system for a section of the low-voltage network.
Samenvattend houdt aarding via het TN-stelsel voor een LS-net onder meer het volgende in: | In summary, grounding via the TN system for a low-voltage network includes, among other things, the following: | the starting of heavy single-phase loads. Figure 5.11 schematically shows the application of the TN-C-S system for a section of the low-voltage network. Figure 5.11 Low-voltage line with TN-C-S system
de aarding wordt doorgezet in de moffen | the grounding is continued in the joints | a section of the low-voltage network. Figure 5.11 Low-voltage line with TN-C-S system In summary, grounding via the TN system for a low-voltage network includes, among other things, the following:
de aarding wordt afgemonteerd op het voedende netstation | the grounding is terminated at the supplying substation | 5.11 Low-voltage line with TN-C-S system In summary, grounding via the TN system for a low-voltage network includes, among other things, the following: the grounding is continued in the joints
netstations zijn geaard | substations are grounded | grounding via the TN system for a low-voltage network includes, among other things, the following: the grounding is continued in the joints the grounding is terminated at the supplying substation
de PE(N)-leiding kan op meerdere punten met aarde zijn verbonden | the PE(N) conductor can be connected to the ground at multiple points | TN system for a low-voltage network includes, among other things, the following: the grounding is continued in the joints the grounding is terminated at the supplying substation substations are grounded
de PE(N)-leiding is zo geïnstalleerd dat het risico van een breuk zo klein mogelijk is. | The PE(N) conductor is installed in such a way that the risk of a break is minimized as much as possible. | the grounding is continued in the joints the grounding is terminated at the supplying substation substations are grounded the PE(N) conductor can be connected to the ground at multiple points
Door de verbinding van de veiligheidsaarde van de aangeslotene met de bedrijfsaarde, ontstaat het risico van een verhoogde aanrakingsspanning bij kortsluitingen in het LS-distributienet. Meer hierover in paragraaf 5.7.2. Indien de aardingssystemen ook met die van hogere spanningsniveaus zijn gekoppeld, hebben ook kortsluitingen in die netten invloed op de veiligheid van de aangeslotene in het laagspanningsnet. Hiermee moet terdege rekening gehouden worden bij het ontwerpen van het net. Meer hierover in paragraaf 5.7.3. | Due to the connection of the protective earth of the connected party with the operational earth, there is a risk of increased touch voltage during short circuits in the low-voltage distribution network. More on this in section 5.7.2. If the grounding systems are also connected to those of higher voltage levels, short circuits in those networks also affect the safety of the connected party in the low-voltage network. This must be thoroughly considered when designing the network. More on this in section 5.7.3. | can be connected to the ground at multiple points The PE(N) conductor is installed in such a way that the risk of a break is minimized as much as possible.
Van een op het TN-stelsel gebaseerd laagspanningsnet wordt de veiligheid geëvalueerd voor de situaties van fase-aardsluitingen met de beschermingsleiding. Maar ook de situatie dat een fase-aardsluiting optreedt met een geleidend voorwerp, dat via een impedantie met de beschermingsleiding is verbonden, kan leiden tot potentiaalverhoging van de beschermingsleiding en moet worden geëvalueerd. De spanning op de beschermingsleiding mag ook in die gevallen niet te hoog worden. Onderstaande vuistregel geldt voor de situatie van een fase-aardfout op een geleidend object dat niet rechtstreeks met de beschermingsleiding is verbonden: | For a low-voltage network based on the TN system, safety is evaluated for situations involving phase-to-earth faults with the protective conductor. However, the situation where a phase-to-earth fault occurs with a conductive object that is connected to the protective conductor via an impedance can also lead to an increase in potential of the protective conductor and must be evaluated. The voltage on the protective conductor must not become too high in those cases either. The following rule of thumb applies to the situation of a phase-to-earth fault on a conductive object that is not directly connected to the protective conductor: | in those networks also affect the safety of the connected party in the low-voltage network. This must be thoroughly considered when designing the network. More on this in section 5.7.3.
[ | [ | in those cases either. The following rule of thumb applies to the situation of a phase-to-earth fault on a conductive object that is not directly connected to the protective conductor:
5.2 | 5.2 | those cases either. The following rule of thumb applies to the situation of a phase-to-earth fault on a conductive object that is not directly connected to the protective conductor: [
] | ] | cases either. The following rule of thumb applies to the situation of a phase-to-earth fault on a conductive object that is not directly connected to the protective conductor: [ 5.2
waarin: | in which: | either. The following rule of thumb applies to the situation of a phase-to-earth fault on a conductive object that is not directly connected to the protective conductor: [ 5.2 ]
R | R | following rule of thumb applies to the situation of a phase-to-earth fault on a conductive object that is not directly connected to the protective conductor: [ 5.2 ] in which:
B | B | rule of thumb applies to the situation of a phase-to-earth fault on a conductive object that is not directly connected to the protective conductor: [ 5.2 ] in which: R
totale aardverspreidingsweerstand van alle parallelgeschakelde aardelektroden plus beschermingsleiding (Ω) | total earth resistance of all parallel-connected earth electrodes plus protective conductor (Ω) | of thumb applies to the situation of a phase-to-earth fault on a conductive object that is not directly connected to the protective conductor: [ 5.2 ] in which: R B
R | R | conductive object that is not directly connected to the protective conductor: [ 5.2 ] in which: R B total earth resistance of all parallel-connected earth electrodes plus protective conductor (Ω)
E | E | object that is not directly connected to the protective conductor: [ 5.2 ] in which: R B total earth resistance of all parallel-connected earth electrodes plus protective conductor (Ω) R
minimum contactweerstand met aarde van vreemde geleidende delen die niet met een beschermingsleiding zijn verbonden, maar via welke een fase-aardfout zou kunnen optreden (Ω) | minimum contact resistance with earth of foreign conductive parts that are not connected to a protective conductor, but through which a phase-to-earth fault could occur (Ω) | that is not directly connected to the protective conductor: [ 5.2 ] in which: R B total earth resistance of all parallel-connected earth electrodes plus protective conductor (Ω) R E
U | U | conductor (Ω) R E minimum contact resistance with earth of foreign conductive parts that are not connected to a protective conductor, but through which a phase-to-earth fault could occur (Ω)
0 | 0 | (Ω) R E minimum contact resistance with earth of foreign conductive parts that are not connected to a protective conductor, but through which a phase-to-earth fault could occur (Ω) U
nominale fasespanning (V) | nominal phase voltage (V) | R E minimum contact resistance with earth of foreign conductive parts that are not connected to a protective conductor, but through which a phase-to-earth fault could occur (Ω) U 0
Dit betekent dat in een LS-net met een nominale spanning van 230 V de verhouding van | This means that in an LV network with a nominal voltage of 230 V, the ratio of | resistance with earth of foreign conductive parts that are not connected to a protective conductor, but through which a phase-to-earth fault could occur (Ω) U 0 nominal phase voltage (V)
R | R | which a phase-to-earth fault could occur (Ω) U 0 nominal phase voltage (V) This means that in an LV network with a nominal voltage of 230 V, the ratio of
B | B | a phase-to-earth fault could occur (Ω) U 0 nominal phase voltage (V) This means that in an LV network with a nominal voltage of 230 V, the ratio of R
tot | tot | phase-to-earth fault could occur (Ω) U 0 nominal phase voltage (V) This means that in an LV network with a nominal voltage of 230 V, the ratio of R B
R | R | fault could occur (Ω) U 0 nominal phase voltage (V) This means that in an LV network with a nominal voltage of 230 V, the ratio of R B tot
E | E | could occur (Ω) U 0 nominal phase voltage (V) This means that in an LV network with a nominal voltage of 230 V, the ratio of R B tot R
kleiner moet zijn dan 0,278. Indien wordt aangenomen dat de contactweerstand op de plek van de fase-aardsluiting R | must be less than 0.278. Assuming that the contact resistance at the point of the phase-to-earth connection R | occur (Ω) U 0 nominal phase voltage (V) This means that in an LV network with a nominal voltage of 230 V, the ratio of R B tot R E
E | E | voltage of 230 V, the ratio of R B tot R E must be less than 0.278. Assuming that the contact resistance at the point of the phase-to-earth connection R
minimaal 10 Ω is, zal de waarde van de foutspanning op de beschermingsleiding ten opzichte van aarde de 50 V niet overschrijden indien de totale aardverspreidingsweerstand van alle parallelgeschakelde aardelektroden plus beschermingsleiding | is at least 10 Ω, the fault voltage on the protective conductor relative to earth will not exceed 50 V if the total earth spreading resistance of all parallel-connected earth electrodes plus the protective conductor | of 230 V, the ratio of R B tot R E must be less than 0.278. Assuming that the contact resistance at the point of the phase-to-earth connection R E
R | R | the fault voltage on the protective conductor relative to earth will not exceed 50 V if the total earth spreading resistance of all parallel-connected earth electrodes plus the protective conductor
B | B | fault voltage on the protective conductor relative to earth will not exceed 50 V if the total earth spreading resistance of all parallel-connected earth electrodes plus the protective conductor R
kleiner dan of gelijk aan 2,7 Ω is. | is less than or equal to 2.7 Ω. | voltage on the protective conductor relative to earth will not exceed 50 V if the total earth spreading resistance of all parallel-connected earth electrodes plus the protective conductor R B
Figuur 5.12 Fase-aardfout met een niet met de beschermingsleiding verbonden object | Figure 5.12 Phase-to-earth fault with an object not connected to the protective conductor | will not exceed 50 V if the total earth spreading resistance of all parallel-connected earth electrodes plus the protective conductor R B is less than or equal to 2.7 Ω.
5.4 Aardelektrode | 5.4 Earth Electrode | parallel-connected earth electrodes plus the protective conductor R B is less than or equal to 2.7 Ω. Figure 5.12 Phase-to-earth fault with an object not connected to the protective conductor
Bij een fase-aardsluiting loopt de retourstroom via diverse locaties met aardcontact. Een belangrijke aardcontact, dat overigens langzamerhand verdwijnt, is het contact van de metalen mantels van GPLK-kabels. Verder zijn er talloze lokale aardcontacten in het midden- en laagspanningsnet. In een laagspanningsdistributienet is veel ‘verborgen aarde’ aanwezig. Het kan zijn dat op elke huisaansluiting of OV-aansluiting de PE-leiding een zeker contact met aarde maakt, hetzij direct via een geslagen aardelektrode, hetzij indirect via aansluiting op een geleidend buizenstelsel of via contact met overige in de grond bevestigde metalen delen. Een aardcontact met redelijk gedefinieerde weerstandswaarde wordt met een aardelektrode bereikt. | In the event of a phase-to-earth fault, the return current flows through various locations with earth contact. An important earth contact, which is gradually disappearing, is the contact of the metal sheaths of GPLK cables. Additionally, there are numerous local earth contacts in the medium and low voltage network. In a low voltage distribution network, there is a lot of 'hidden earth.' It may be that at every house connection or public lighting connection, the PE conductor makes some contact with the earth, either directly through a driven earth electrode or indirectly through connection to a conductive piping system or through contact with other metal parts embedded in the ground. An earth contact with a reasonably defined resistance value is achieved with an earth electrode. | plus the protective conductor R B is less than or equal to 2.7 Ω. Figure 5.12 Phase-to-earth fault with an object not connected to the protective conductor 5.4 Earth Electrode
De aardelektrode wordt gemodelleerd met een weerstand naar de ‘verre aarde’. De weerstand van de aardelektrode is afhankelijk van de specifieke bodemweerstand | The earth electrode is modeled with a resistance to the 'remote earth'. The resistance of the earth electrode depends on the specific soil resistivity. | a conductive piping system or through contact with other metal parts embedded in the ground. An earth contact with a reasonably defined resistance value is achieved with an earth electrode.
ρ | ρ | is achieved with an earth electrode. The earth electrode is modeled with a resistance to the 'remote earth'. The resistance of the earth electrode depends on the specific soil resistivity.
en de fysieke afmetingen van de aardelektrode. Voor een enkele ronde penvormige aardelektrode geldt formule 5.3 voor berekening van de aardverspreidingsweerstand (Happoldt, 1978): | and the physical dimensions of the earth electrode. For a single round rod-shaped earth electrode, formula 5.3 applies for calculating the earth resistance (Happoldt, 1978): | achieved with an earth electrode. The earth electrode is modeled with a resistance to the 'remote earth'. The resistance of the earth electrode depends on the specific soil resistivity. ρ
(Ω) | (Ohms) | the specific soil resistivity. ρ and the physical dimensions of the earth electrode. For a single round rod-shaped earth electrode, formula 5.3 applies for calculating the earth resistance (Happoldt, 1978):
[ | [ | specific soil resistivity. ρ and the physical dimensions of the earth electrode. For a single round rod-shaped earth electrode, formula 5.3 applies for calculating the earth resistance (Happoldt, 1978): (Ohms)
5.3 | 5.3 | soil resistivity. ρ and the physical dimensions of the earth electrode. For a single round rod-shaped earth electrode, formula 5.3 applies for calculating the earth resistance (Happoldt, 1978): (Ohms) [
] | ] | resistivity. ρ and the physical dimensions of the earth electrode. For a single round rod-shaped earth electrode, formula 5.3 applies for calculating the earth resistance (Happoldt, 1978): (Ohms) [ 5.3
met: | with: | ρ and the physical dimensions of the earth electrode. For a single round rod-shaped earth electrode, formula 5.3 applies for calculating the earth resistance (Happoldt, 1978): (Ohms) [ 5.3 ]
ρ | ρ | and the physical dimensions of the earth electrode. For a single round rod-shaped earth electrode, formula 5.3 applies for calculating the earth resistance (Happoldt, 1978): (Ohms) [ 5.3 ] with:
specifieke weerstand van de bodem (Ωm) | specific resistance of the soil (Ωm) | the physical dimensions of the earth electrode. For a single round rod-shaped earth electrode, formula 5.3 applies for calculating the earth resistance (Happoldt, 1978): (Ohms) [ 5.3 ] with: ρ
L | L | electrode. For a single round rod-shaped earth electrode, formula 5.3 applies for calculating the earth resistance (Happoldt, 1978): (Ohms) [ 5.3 ] with: ρ specific resistance of the soil (Ωm)
lengte van de verticale aardelektrode in de grond (m) | length of the vertical earth electrode in the ground (m) | For a single round rod-shaped earth electrode, formula 5.3 applies for calculating the earth resistance (Happoldt, 1978): (Ohms) [ 5.3 ] with: ρ specific resistance of the soil (Ωm) L
d | d | for calculating the earth resistance (Happoldt, 1978): (Ohms) [ 5.3 ] with: ρ specific resistance of the soil (Ωm) L length of the vertical earth electrode in the ground (m)
diameter van de aardelektrode (m) | diameter of the earth electrode (m) | calculating the earth resistance (Happoldt, 1978): (Ohms) [ 5.3 ] with: ρ specific resistance of the soil (Ωm) L length of the vertical earth electrode in the ground (m) d
De specifieke weerstand is afhankelijk van het bodemmateriaal en de hoeveelheid vocht in en de temperatuur van de bodem. Tabel 5.1 geeft een overzicht voor diverse bodemsoorten. | The specific resistance depends on the soil material, the amount of moisture in the soil, and the soil temperature. Table 5.1 provides an overview for various soil types. | (Ohms) [ 5.3 ] with: ρ specific resistance of the soil (Ωm) L length of the vertical earth electrode in the ground (m) d diameter of the earth electrode (m)
Tabel 5.1 Specifieke weerstand van bodemsoorten | Table 5.1 Specific Resistance of Soil Types | electrode (m) The specific resistance depends on the soil material, the amount of moisture in the soil, and the soil temperature. Table 5.1 provides an overview for various soil types.
Bodemsoort | Bodemsoort | the soil material, the amount of moisture in the soil, and the soil temperature. Table 5.1 provides an overview for various soil types. Table 5.1 Specific Resistance of Soil Types
ρ minimaal [Ωm] | ρ minimum [Ωm] | soil material, the amount of moisture in the soil, and the soil temperature. Table 5.1 provides an overview for various soil types. Table 5.1 Specific Resistance of Soil Types Bodemsoort
ρ maximaal [Ωm] | ρ maximum [Ωm] | amount of moisture in the soil, and the soil temperature. Table 5.1 provides an overview for various soil types. Table 5.1 Specific Resistance of Soil Types Bodemsoort ρ minimum [Ωm]
Veen | Veen | in the soil, and the soil temperature. Table 5.1 provides an overview for various soil types. Table 5.1 Specific Resistance of Soil Types Bodemsoort ρ minimum [Ωm] ρ maximum [Ωm]
5 | 5 | the soil, and the soil temperature. Table 5.1 provides an overview for various soil types. Table 5.1 Specific Resistance of Soil Types Bodemsoort ρ minimum [Ωm] ρ maximum [Ωm] Veen
40 | 40 | soil, and the soil temperature. Table 5.1 provides an overview for various soil types. Table 5.1 Specific Resistance of Soil Types Bodemsoort ρ minimum [Ωm] ρ maximum [Ωm] Veen 5
Klei | Klei | and the soil temperature. Table 5.1 provides an overview for various soil types. Table 5.1 Specific Resistance of Soil Types Bodemsoort ρ minimum [Ωm] ρ maximum [Ωm] Veen 5 40
20 | 20 | the soil temperature. Table 5.1 provides an overview for various soil types. Table 5.1 Specific Resistance of Soil Types Bodemsoort ρ minimum [Ωm] ρ maximum [Ωm] Veen 5 40 Klei
200 | 200 | soil temperature. Table 5.1 provides an overview for various soil types. Table 5.1 Specific Resistance of Soil Types Bodemsoort ρ minimum [Ωm] ρ maximum [Ωm] Veen 5 40 Klei 20
Zand | Zand | temperature. Table 5.1 provides an overview for various soil types. Table 5.1 Specific Resistance of Soil Types Bodemsoort ρ minimum [Ωm] ρ maximum [Ωm] Veen 5 40 Klei 20 200
200 | 200 | Table 5.1 provides an overview for various soil types. Table 5.1 Specific Resistance of Soil Types Bodemsoort ρ minimum [Ωm] ρ maximum [Ωm] Veen 5 40 Klei 20 200 Zand
2500 | 2500 | 5.1 provides an overview for various soil types. Table 5.1 Specific Resistance of Soil Types Bodemsoort ρ minimum [Ωm] ρ maximum [Ωm] Veen 5 40 Klei 20 200 Zand 200
Kiezel | Kiezel | provides an overview for various soil types. Table 5.1 Specific Resistance of Soil Types Bodemsoort ρ minimum [Ωm] ρ maximum [Ωm] Veen 5 40 Klei 20 200 Zand 200 2500
2000 | 2000 | an overview for various soil types. Table 5.1 Specific Resistance of Soil Types Bodemsoort ρ minimum [Ωm] ρ maximum [Ωm] Veen 5 40 Klei 20 200 Zand 200 2500 Kiezel
3000 | 3000 | overview for various soil types. Table 5.1 Specific Resistance of Soil Types Bodemsoort ρ minimum [Ωm] ρ maximum [Ωm] Veen 5 40 Klei 20 200 Zand 200 2500 Kiezel 2000
Het verschil tussen de minimale en maximale waarden van de specifieke bodemweerstand wordt bepaald door het gewichtspercentage van het in het materiaal aanwezige vocht. Dit kan gemeten worden tijdens het slaan van de aardelektrode, ervan uitgaande dat de meting representatief is voor de laagste vochtigheid van de bodem. | The difference between the minimum and maximum values of the specific soil resistance is determined by the weight percentage of the moisture present in the material. This can be measured during the driving of the ground electrode, assuming that the measurement is representative of the lowest moisture content of the soil. | for various soil types. Table 5.1 Specific Resistance of Soil Types Bodemsoort ρ minimum [Ωm] ρ maximum [Ωm] Veen 5 40 Klei 20 200 Zand 200 2500 Kiezel 2000 3000
In Nederland is de aardelektrode vaak een geslagen aardelektrode van rond koperdraad met een doorsnede van 50 mm | In the Netherlands, the ground electrode is often a driven ground electrode made of round copper wire with a diameter of 50 mm. | moisture present in the material. This can be measured during the driving of the ground electrode, assuming that the measurement is representative of the lowest moisture content of the soil.
2 | 2 | the lowest moisture content of the soil. In the Netherlands, the ground electrode is often a driven ground electrode made of round copper wire with a diameter of 50 mm.
(d = 0,0075 m) | (d = 0.0075 m) | lowest moisture content of the soil. In the Netherlands, the ground electrode is often a driven ground electrode made of round copper wire with a diameter of 50 mm. 2
. Er worden ook andere soorten aardelektrodes toegepast, zoals massief staal (rond, ster- of kruisvormig) voorzien van een goedhechtende koperlaag aan de oppervlakte of een verzinkte rond stalen variant. Voor het maken van een aardelektrode met een aardverspreidingsweerstand kleiner dan 1 Ω moeten vaak meerdere parallelle aardelektroden geslagen worden, op ruime afstand van elkaar. Volgens formule 5.3 is de aardverspreidingsweerstand voor een aardelektrode van 10 m met een diameter van 7,5 mm in bodem en met een specifieke weerstand van 100 Ωm gelijk aan 13,7 Ω. De literatuur (Happoldt, 1978) (Tleis, 2008) geeft formules voor het berekenen van parallelle of andere vormen van aardelektroden. | Other types of ground electrodes are also used, such as solid steel (round, star-shaped, or cross-shaped) with a well-adhering copper layer on the surface or a galvanized round steel variant. To create a ground electrode with a ground spreading resistance of less than 1 Ω, multiple parallel ground electrodes often need to be driven into the ground, spaced widely apart. According to formula 5.3, the ground spreading resistance for a 10 m ground electrode with a diameter of 7.5 mm in soil with a specific resistance of 100 Ωm is equal to 13.7 Ω. The literature (Happoldt, 1978) (Tleis, 2008) provides formulas for calculating parallel or other forms of ground electrodes. | the soil. In the Netherlands, the ground electrode is often a driven ground electrode made of round copper wire with a diameter of 50 mm. 2 (d = 0.0075 m)
In een distributienet worden voor alle spanningniveaus specifieke waarden voor de aardverspreidingsweerstanden toegepast. Onderstaande waarden kunnen voorkomen. | In a distribution network, specific values for ground resistance are applied for all voltage levels. The following values may occur. | soil with a specific resistance of 100 Ωm is equal to 13.7 Ω. The literature (Happoldt, 1978) (Tleis, 2008) provides formulas for calculating parallel or other forms of ground electrodes.
Een HS/MS-onderstation heeft een aardingsimpedantie van 0,2 Ω. | A high-voltage/medium-voltage substation has a grounding impedance of 0.2 Ω. | formulas for calculating parallel or other forms of ground electrodes. In a distribution network, specific values for ground resistance are applied for all voltage levels. The following values may occur.
Een MS/LS-netstation heeft een aardingsimpedantie van 2 Ω. | A medium-voltage/low-voltage substation has a grounding impedance of 2 Ω. | In a distribution network, specific values for ground resistance are applied for all voltage levels. The following values may occur. A high-voltage/medium-voltage substation has a grounding impedance of 0.2 Ω.
Een LS-aansluiting kan een aardelektrode hebben met een impedantie van 5 Ω of groter. | An LV connection can have a grounding electrode with an impedance of 5 Ω or greater. | applied for all voltage levels. The following values may occur. A high-voltage/medium-voltage substation has a grounding impedance of 0.2 Ω. A medium-voltage/low-voltage substation has a grounding impedance of 2 Ω.
5.5 Potentiaalvereffening | 5.5 Potential Equalization | impedance of 0.2 Ω. A medium-voltage/low-voltage substation has a grounding impedance of 2 Ω. An LV connection can have a grounding electrode with an impedance of 5 Ω or greater.
De aarding moet altijd zodanig aangelegd zijn, dat dit niet leidt tot spanningsverhogingen met bijbehorende verhoogde risico’s voor mens en apparatuur. De aanrakingsspanning wordt niet alleen bepaald door de spanning van de PE-leiding en de lokale aarde, maar vooral door de spanningsverschillen tussen alle metalen voorwerpen die gelijktijdig aangeraakt kunnen worden. Om die reden worden zo veel mogelijk alle niet tot de elektrische installatie behorende geleidende delen op een centrale plaats (de hoofdaardrail) met de PE-leiding van de elektrische installatie verbonden, zodat alle gelijktijdig aanraakbare metalen gestellen dezelfde potentiaal voeren. De norm NEN 1010 beschrijft dat voor een goede potentiaalvereffening in elk gebouw alle geleidende delen van watervoorziening, gasvoorziening, verwarmingsystemen, luchtbehandelingsystemen, staalconstructie en betonbewapening moeten zijn verbonden met de hoofdaardrail. De potentiaalvereffening moet zo dicht mogelijk bij de plaats van binnenkomst in het gebouw plaatsvinden. Bovendien wordt aanbevolen om de beschermingsleiding op zoveel mogelijk plaatsen met beschikbare goed geaarde delen te verbinden. Bij een TT-stelsel moet ook de lokale aardelektrode op de hoofdaardrail worden aangesloten. Tevens moeten de beschermende leidingen van telecom- en kabeltelevisienetten op de centrale plaats geaard worden. Dit is minder van belang voor de aanrakingsveiligheid, maar wel voor de bescherming van elektronische apparatuur, | The grounding must always be installed in such a way that it does not lead to voltage increases with associated increased risks for people and equipment. The touch voltage is not only determined by the voltage of the PE conductor and the local ground, but especially by the voltage differences between all metal objects that can be touched simultaneously. For this reason, as many conductive parts not belonging to the electrical installation as possible are connected at a central location (the main grounding bar) with the PE conductor of the electrical installation, so that all simultaneously touchable metal frames carry the same potential. The NEN 1010 standard describes that for good potential equalization in every building, all conductive parts of the water supply, gas supply, heating systems, air handling systems, steel structures, and concrete reinforcement must be connected to the main grounding bar. The potential equalization should take place as close as possible to the point of entry into the building. Additionally, it is recommended to connect the protective conductor to as many available well-grounded parts as possible. In a TT system, the local grounding electrode must also be connected to the main grounding bar. Furthermore, the protective conductors of telecom and cable television networks must be grounded at the central location. This is less important for touch safety but crucial for the protection of electronic equipment. | Ω. A medium-voltage/low-voltage substation has a grounding impedance of 2 Ω. An LV connection can have a grounding electrode with an impedance of 5 Ω or greater. 5.5 Potential Equalization
De aarding in het distributienet is verspreid over alle netstations en alle aansluitingen. Elk netstation heeft een eigen aarding en ook LS-aansluitingen kunnen een aarding hebben. In een LS-net waar het TN-stelsel is toegepast, hoeft een aangeslotene theoretisch geen eigen lokale aardelektrode te hebben. Het enige aardpunt bevindt zich dan bij de MS/LS-distributietransformator. In praktijk echter, is er altijd wel ergens een verbinding met aarde aanwezig, hetzij via aardelektrodes of kabelmantels, hetzij indirect via contact met in de grond gelegde geleidende buizen. | The grounding in the distribution network is spread across all substations and all connections. Each substation has its own grounding, and LS connections can also have grounding. In an LS network where the TN system is applied, a connected user theoretically does not need their own local ground electrode. The only grounding point is then located at the MS/LS distribution transformer. In practice, however, there is always some connection to the ground present, either through ground electrodes or cable sheaths, or indirectly through contact with conductive pipes laid in the ground. | protective conductors of telecom and cable television networks must be grounded at the central location. This is less important for touch safety but crucial for the protection of electronic equipment.
In een distributienet zijn alle aardcontacten met elkaar verbonden. De invloed van verspreide aardcontacten kan vertaald worden in een equivalente aardimpedantie Z | In a distribution network, all ground contacts are interconnected. The influence of dispersed ground contacts can be translated into an equivalent ground impedance Z. | In practice, however, there is always some connection to the ground present, either through ground electrodes or cable sheaths, or indirectly through contact with conductive pipes laid in the ground.
eq | eq | conductive pipes laid in the ground. In a distribution network, all ground contacts are interconnected. The influence of dispersed ground contacts can be translated into an equivalent ground impedance Z.
. Deze kan worden berekend vanuit een laddernetwerk. De berekening volgt uit ontwikkeling van de reeks voor n segmenten van een laddernetwerk: | This can be calculated from a ladder network. The calculation follows from the development of the series for n segments of a ladder network: | pipes laid in the ground. In a distribution network, all ground contacts are interconnected. The influence of dispersed ground contacts can be translated into an equivalent ground impedance Z. eq
Figuur 5.13 Laddernetwerk voor verspreide aardcontacten | Figure 5.13 Ladder network for distributed ground contacts | an equivalent ground impedance Z. eq This can be calculated from a ladder network. The calculation follows from the development of the series for n segments of a ladder network:
In formulevorm geldt voor n secties: | In formula form, it holds for n sections: | be calculated from a ladder network. The calculation follows from the development of the series for n segments of a ladder network: Figure 5.13 Ladder network for distributed ground contacts
[ | [ | follows from the development of the series for n segments of a ladder network: Figure 5.13 Ladder network for distributed ground contacts In formula form, it holds for n sections:
5.4 | 5.4 | from the development of the series for n segments of a ladder network: Figure 5.13 Ladder network for distributed ground contacts In formula form, it holds for n sections: [
] | ] | the development of the series for n segments of a ladder network: Figure 5.13 Ladder network for distributed ground contacts In formula form, it holds for n sections: [ 5.4
waarin: | in which: | development of the series for n segments of a ladder network: Figure 5.13 Ladder network for distributed ground contacts In formula form, it holds for n sections: [ 5.4 ]
Z | Z | the series for n segments of a ladder network: Figure 5.13 Ladder network for distributed ground contacts In formula form, it holds for n sections: [ 5.4 ] in which:
s | s | series for n segments of a ladder network: Figure 5.13 Ladder network for distributed ground contacts In formula form, it holds for n sections: [ 5.4 ] in which: Z
impedantie van de PE-leiding tussen twee secties, eventueel parallel aan de nulgeleider | impedance of the PE conductor between two sections, possibly in parallel with the neutral conductor | for n segments of a ladder network: Figure 5.13 Ladder network for distributed ground contacts In formula form, it holds for n sections: [ 5.4 ] in which: Z s
Z | Z | In formula form, it holds for n sections: [ 5.4 ] in which: Z s impedance of the PE conductor between two sections, possibly in parallel with the neutral conductor
p | p | formula form, it holds for n sections: [ 5.4 ] in which: Z s impedance of the PE conductor between two sections, possibly in parallel with the neutral conductor Z
impedantie van het aardcontact | impedance of the ground contact | form, it holds for n sections: [ 5.4 ] in which: Z s impedance of the PE conductor between two sections, possibly in parallel with the neutral conductor Z p
Z | Z | sections: [ 5.4 ] in which: Z s impedance of the PE conductor between two sections, possibly in parallel with the neutral conductor Z p impedance of the ground contact
eq,n-1 | eq,n-1 | [ 5.4 ] in which: Z s impedance of the PE conductor between two sections, possibly in parallel with the neutral conductor Z p impedance of the ground contact Z
equivalente impedantie van de voorgaande sectie | equivalent impedance of the previous section | 5.4 ] in which: Z s impedance of the PE conductor between two sections, possibly in parallel with the neutral conductor Z p impedance of the ground contact Z eq,n-1
Voor de meeste toepassingen kan de invloed van de kabelimpedantie verwaarloosd worden en wordt de equivalente aardingsimpedantie van | For most applications, the influence of the cable impedance can be neglected, and the equivalent grounding impedance of | impedance of the PE conductor between two sections, possibly in parallel with the neutral conductor Z p impedance of the ground contact Z eq,n-1 equivalent impedance of the previous section
n | n | of the ground contact Z eq,n-1 equivalent impedance of the previous section For most applications, the influence of the cable impedance can be neglected, and the equivalent grounding impedance of
aardcontacten benaderd volgens: | ground contacts approximated according to: | the ground contact Z eq,n-1 equivalent impedance of the previous section For most applications, the influence of the cable impedance can be neglected, and the equivalent grounding impedance of n
[ | [ | equivalent impedance of the previous section For most applications, the influence of the cable impedance can be neglected, and the equivalent grounding impedance of n ground contacts approximated according to:
5.5 | 5.5 | impedance of the previous section For most applications, the influence of the cable impedance can be neglected, and the equivalent grounding impedance of n ground contacts approximated according to: [
] | ] | of the previous section For most applications, the influence of the cable impedance can be neglected, and the equivalent grounding impedance of n ground contacts approximated according to: [ 5.5
5.6 Gevaarlijke situaties | 5.6 Hazardous situations | the previous section For most applications, the influence of the cable impedance can be neglected, and the equivalent grounding impedance of n ground contacts approximated according to: [ 5.5 ]
Kortsluitingen waarbij contact gemaakt wordt met aarde leiden tot een spanningsverhoging op het aardsysteem of de lokale aarde. Als alle aardingssystemen met elkaar zijn verbonden, kan op alle niveaus een kortsluiting leiden tot een gevaarlijke situatie bij een aangeslotene. | Short circuits that make contact with the ground lead to an increase in voltage on the grounding system or the local ground. If all grounding systems are interconnected, a short circuit at any level can result in a hazardous situation for a connected individual. | For most applications, the influence of the cable impedance can be neglected, and the equivalent grounding impedance of n ground contacts approximated according to: [ 5.5 ] 5.6 Hazardous situations
Kortsluiting in een hoogspanningsnetwerk | Short circuit in a high-voltage network | on the grounding system or the local ground. If all grounding systems are interconnected, a short circuit at any level can result in a hazardous situation for a connected individual.
In een onderstation zijn de aardingssystemen van de hoogspannings- en middenspanningsnetwerken met elkaar verbonden. De retourstroom van een fase-aardsluiting in het hoogspanningsnetwerk zal niet alleen door het retourpad van het hoogspanningsnetwerk vloeien, maar ook door de aarding van het onderstation en de mantels van de middenspanningskabels. Met name kabels die parallel lopen aan de hoogspanningslijn, kunnen een grote retourstroom voeren. Deze stromen leiden tot potentiaalverhoging van de retourleidingen in het middenspanningsnetwerk. | In a substation, the grounding systems of the high-voltage and medium-voltage networks are interconnected. The return current from a phase-to-ground fault in the high-voltage network will not only flow through the return path of the high-voltage network but also through the grounding of the substation and the sheaths of the medium-voltage cables. Particularly, cables that run parallel to the high-voltage line can carry a significant return current. These currents lead to a potential rise in the return conductors of the medium-voltage network. | local ground. If all grounding systems are interconnected, a short circuit at any level can result in a hazardous situation for a connected individual. Short circuit in a high-voltage network
Kortsluitingen in een middenspanningsnetwerk | Short circuits in a medium-voltage network | Particularly, cables that run parallel to the high-voltage line can carry a significant return current. These currents lead to a potential rise in the return conductors of the medium-voltage network.
Tijdens een fase-aardsluiting in het middenspanningsnetwerk vloeit de retourstroom gedeeltelijk door de mantels van de middenspanningskabels en gedeeltelijk via de aardelektrodes door de aarde. In de netstations zijn de aardingssystemen van het middenspannings- en laagspanningsnetten met elkaar verbonden. De stromen door de aardelektrodes in de distributieruimten leiden tot potentiaalverhoging van de aarde in de netstations, waardoor ook de spanning op het aardingssysteem van de MS/LS-distributietransformatoren verhoogd worden. Als de aardingssystemen in het laagspanningsnet verbonden zijn met het aardingssysteem van de distributietransformator, kunnen deze potentiaalverhogingen merkbaar zijn in de installaties van de aangeslotenen. De duur van deze spanningsverhogingen wordt bepaald door de duur van de kortsluitstroom en is daarmee afhankelijk van de hoogte van de kortsluitstroom en de werking van de beveiliging. De hoogte van deze spanningsverhogingen wordt bepaald door grootte van de retourstroom en de impedanties van de aardelektrodes en afscherming van de kabel. | During a phase-to-earth fault in the medium-voltage network, the return current flows partially through the sheaths of the medium-voltage cables and partially through the grounding electrodes into the earth. In the substations, the grounding systems of the medium-voltage and low-voltage networks are interconnected. The currents through the grounding electrodes in the distribution areas lead to a potential rise in the earth in the substations, which also increases the voltage on the grounding system of the MV/LV distribution transformers. If the grounding systems in the low-voltage network are connected to the grounding system of the distribution transformer, these potential rises can be noticeable in the installations of the connected users. The duration of these voltage rises is determined by the duration of the short-circuit current and is thus dependent on the magnitude of the short-circuit current and the operation of the protection system. The magnitude of these voltage rises is determined by the size of the return current and the impedances of the grounding electrodes and the cable shielding. | the high-voltage line can carry a significant return current. These currents lead to a potential rise in the return conductors of the medium-voltage network. Short circuits in a medium-voltage network
De grootste retourstroom ontstaat bij een kortsluiting tussen een fase en aarde. In zwevende middenspanningsnetten is de retourstroom ongeveer 1,5 A per km kabel, hetgeen voor netten met typische gesommeerde lengten van 130 tot 400 km een stroom oplevert tussen 200 en 600 A. Indien deze stromen groter zijn dan 300 A kunnen zij door beveiligingen worden gedetecteerd en afgeschakeld. Indien deze stromen kleiner zijn dan 300 A liggen zij in de ordegrootte van normale bedrijfsstromen en zullen zij door eenvoudige maximum stroom-tijdbeveiligingen niet worden afgeschakeld. Een oplossing hiervoor is om deze netten met een impedantie te aarden, bijvoorbeeld met een aardingstransformator. In geaarde middenspanningsnetten is de retourstroom veel groter. Deze ligt in de ordegrootte van 700 tot 2000 A (Provoost, 2004). Vanwege de hoogte van de kortsluitstroom kan de beveiliging selectief ingrijpen en wordt de duur van de kortsluiting bepaald door deze beveiliging. | The largest return current occurs during a short circuit between a phase and ground. In floating medium voltage networks, the return current is approximately 1.5 A per km of cable, which for networks with typical summed lengths of 130 to 400 km results in a current between 200 and 600 A. If these currents are greater than 300 A, they can be detected and disconnected by protection systems. If these currents are less than 300 A, they are in the order of magnitude of normal operating currents and will not be disconnected by simple maximum current-time protections. A solution for this is to ground these networks with an impedance, for example, with a grounding transformer. In grounded medium voltage networks, the return current is much larger. It is in the order of magnitude of 700 to 2000 A (Provoost, 2004). Due to the high short-circuit current, the protection can intervene selectively, and the duration of the short circuit is determined by this protection. | of the protection system. The magnitude of these voltage rises is determined by the size of the return current and the impedances of the grounding electrodes and the cable shielding.
Kortsluitingen in een laagspanningsnetwerk | Short circuits in a low-voltage network | of 700 to 2000 A (Provoost, 2004). Due to the high short-circuit current, the protection can intervene selectively, and the duration of the short circuit is determined by this protection.
Laagspanningsnetten zijn in principe star geaard. De aardingsimpedantie wordt bepaald door de aardverspreidingsweerstand van de aardelektrode. Een kortsluiting tussen fasegeleider en nulgeleider of aarde resulteert in een potentiaalverhoging van de nulgeleider, afscherming van de kabel of de aarde. Met name bij de toepassing van een TN-stelsel moet terdege rekening worden gehouden met het feit dat kortsluitingen in het distributienet leiden tot verhoogde aanrakingsspanningen in het aardingssysteem van de aangeslotenen. Deze spanningen en de duur daarvan moeten begrensd blijven tot veilige waarden. De netontwerper moet de hoogte van de aanrakingsspanningen en de tijdsduur controleren. Dit kan bijvoorbeeld met behulp van een computerprogramma voor LS-netontwerp (Phase, 2009). | Low-voltage networks are essentially solidly grounded. The grounding impedance is determined by the earth resistance of the grounding electrode. A short circuit between the phase conductor and the neutral conductor or ground results in a potential increase of the neutral conductor, cable shielding, or ground. Particularly in the application of a TN system, it must be thoroughly considered that short circuits in the distribution network lead to increased touch voltages in the grounding system of the connected users. These voltages and their duration must be limited to safe values. The network designer must check the level of touch voltages and the duration. This can be done, for example, using a computer program for LV network design (Phase, 2009). | 2004). Due to the high short-circuit current, the protection can intervene selectively, and the duration of the short circuit is determined by this protection. Short circuits in a low-voltage network
Teneinde de impedantie van het retourpad zo klein mogelijk te houden, hebben de laagspanningskabels een nulgeleider en een koperen afscherming. Bovendien worden vaak om reden van veiligheid in alle moffen de nulgeleider en het kabelscherm met elkaar verbonden, zoals aangegeven in figuur 5.11. | In order to keep the impedance of the return path as low as possible, the low-voltage cables have a neutral conductor and a copper shield. Additionally, for safety reasons, the neutral conductor and the cable shield are often connected to each other in all joints, as shown in figure 5.11. | values. The network designer must check the level of touch voltages and the duration. This can be done, for example, using a computer program for LV network design (Phase, 2009).
5.7 Aanrakingsveiligheid | 5.7 Touch Safety | conductor and a copper shield. Additionally, for safety reasons, the neutral conductor and the cable shield are often connected to each other in all joints, as shown in figure 5.11.
Storingen zoals fase-aardsluitingen zijn een veel voorkomend verschijnsel. Het is belangrijk dat die storingen niet mogen leiden tot gevaarlijke situaties. Een spanningsverhoging op de aardingsvoorzieningen kan beperkt worden door ervoor te zorgen dat het retourpad een voldoende lage impedantie heeft. De eisen waaraan netten en installaties moeten voldoen zijn vastgelegd in de nationale norm NEN 1010. In die norm ligt de nadruk op het tijdig afschakelen bij een spanningsverhoging op de aardingsvoorziening. Door ongevallen in het verleden zijn de netbeheerders verantwoordelijk gesteld voor situaties waarin een aardingsvoorziening niet meer voldoet. Mede hierom leveren de netbeheerders een deugdelijke aarde aan de aangeslotene en stellen zij zich zelf verantwoordelijk voor de kwaliteit van de aardverbinding. | Faults such as phase-to-ground faults are a common occurrence. It is important that these faults do not lead to dangerous situations. A voltage increase on the grounding provisions can be limited by ensuring that the return path has a sufficiently low impedance. The requirements that networks and installations must meet are laid down in the national standard NEN 1010. This standard emphasizes timely disconnection in the event of a voltage increase on the grounding provision. Due to accidents in the past, network operators have been held responsible for situations where a grounding provision no longer meets the standards. For this reason, network operators provide a reliable ground to the connected party and take responsibility for the quality of the ground connection. | copper shield. Additionally, for safety reasons, the neutral conductor and the cable shield are often connected to each other in all joints, as shown in figure 5.11. 5.7 Touch Safety
In hoog- en middenspanningsnetten leidt het aanraken van spanningsvoerende delen meestal tot ernstig letsel of overlijden. Het aanraken van laagspanning kan ook tot letsel leiden. De omvang van de schade hangt af van de stroomsterkte en de duur van de door het lichaam gaande stroom. Een blijvende stroom van enkele tientallen milliampères is al dodelijk. In de internationale norm IEC 60479 is met behulp van stroom-tijd gevarencurves aangegeven welke stroomsterkte gedurende welke tijd een bepaald gevaar oplevert. | In high and medium voltage networks, touching live parts usually leads to serious injury or death. Touching low voltage can also cause injury. The extent of the damage depends on the current strength and the duration of the current passing through the body. A continuous current of several tens of milliamperes is already fatal. In the international standard IEC 60479, hazard curves based on current-time are used to indicate which current strength poses a certain danger over a specific period. | grounding provision no longer meets the standards. For this reason, network operators provide a reliable ground to the connected party and take responsibility for the quality of the ground connection.
Figuur 5.14 Stroom-tijd gevarencurven volgens IEC 60479 | Figure 5.14 Current-time hazard curves according to IEC 60479 | milliamperes is already fatal. In the international standard IEC 60479, hazard curves based on current-time are used to indicate which current strength poses a certain danger over a specific period.
In de grafiek is met behulp van vier zones aangegeven in welke mate een menselijk lichaam de stroom ervaart: | The graph uses four zones to indicate the extent to which a human body experiences the current: | 60479, hazard curves based on current-time are used to indicate which current strength poses a certain danger over a specific period. Figure 5.14 Current-time hazard curves according to IEC 60479
AC-1: het gebied tot lijn A (0,5 mA); in dit gebied is het mogelijk dat een stroom wordt waargenomen, maar dit leidt niet tot een schrikreactie | AC-1: the area up to line A (0.5 mA); in this area, it is possible that a current is perceived, but it does not lead to a startle reaction. | over a specific period. Figure 5.14 Current-time hazard curves according to IEC 60479 The graph uses four zones to indicate the extent to which a human body experiences the current:
AC-2: het gebied tussen lijnen A en B; in dit gebied voelt men de stroom, maar dit heeft gewoonlijk geen schadelijke fysiologische effecten; bij ongeveer 10 mA ligt de zogenaamde loslaat-drempel | AC-2: the area between lines A and B; in this area, the current is felt, but it usually has no harmful physiological effects; at approximately 10 mA lies the so-called let-go threshold. | current: AC-1: the area up to line A (0.5 mA); in this area, it is possible that a current is perceived, but it does not lead to a startle reaction.
AC-3: het gebied rechts van de lijn B; in dit gebied treden sterke spiercontracties op, ademhalingsmoeilijkheden, niet-blijvende verstoring van de hartfunctie; immobilisatie is mogelijk; doorgaans treedt geen schade aan organen op | AC-3: the area to the right of line B; in this area, strong muscle contractions occur, breathing difficulties, temporary disruption of heart function; immobilization is possible; generally, no organ damage occurs. | area between lines A and B; in this area, the current is felt, but it usually has no harmful physiological effects; at approximately 10 mA lies the so-called let-go threshold.
AC-4: het gebied rechts van lijn C1: in dit gebied treden sterke fysiologische effecten op, zoals hartstilstand, stilstand van de ademhaling, schade aan organen en brandwonden | AC-4: the area to the right of line C1: in this area, strong physiological effects occur, such as cardiac arrest, respiratory arrest, organ damage, and burns. | the area to the right of line B; in this area, strong muscle contractions occur, breathing difficulties, temporary disruption of heart function; immobilization is possible; generally, no organ damage occurs.
AC-4,1: tussen C1 en C2: tot 5% kans op hartfibrillatie | AC-4.1: between C1 and C2: up to 5% chance of heart fibrillation | no organ damage occurs. AC-4: the area to the right of line C1: in this area, strong physiological effects occur, such as cardiac arrest, respiratory arrest, organ damage, and burns.
AC-4,2: tussen C3 en C3: tot 50% kans op hartfibrillatie | AC-4.2: between C3 and C3: up to 50% chance of heart fibrillation | C1: in this area, strong physiological effects occur, such as cardiac arrest, respiratory arrest, organ damage, and burns. AC-4.1: between C1 and C2: up to 5% chance of heart fibrillation
AC-4,3: rechts van C3: meer dan 50% kans op hartfibrillatie. | AC-4.3: to the right of C3: more than 50% chance of heart fibrillation. | respiratory arrest, organ damage, and burns. AC-4.1: between C1 and C2: up to 5% chance of heart fibrillation AC-4.2: between C3 and C3: up to 50% chance of heart fibrillation
Figuur 5.15 Lichaamsweerstand van de mens als functie van de aanrakingsspanning (één hand – één hand) | Figure 5.15 Human body resistance as a function of contact voltage (one hand - one hand) | 5% chance of heart fibrillation AC-4.2: between C3 and C3: up to 50% chance of heart fibrillation AC-4.3: to the right of C3: more than 50% chance of heart fibrillation.
Naast deze curven wordt ook wel de Lc-curve toegepast, die zich bevindt in het AC-3 gebied, tussen de curven B en C1. Deze curve is ooit geïntroduceerd door de NEN 1010-commissie en biedt extra zekerheid. De curve ligt op een zodanige afstand van de curve C1, dat verondersteld wordt dat eventuele afwijkingen van de gemiddelde situatie er niet toe leiden dat de curve C1 wordt overschreden. | In addition to these curves, the Lc-curve is also applied, which is located in the AC-3 area, between curves B and C1. This curve was introduced by the NEN 1010 committee and provides extra assurance. The curve is positioned at such a distance from curve C1 that it is assumed any deviations from the average situation will not result in exceeding curve C1. | fibrillation AC-4.3: to the right of C3: more than 50% chance of heart fibrillation. Figure 5.15 Human body resistance as a function of contact voltage (one hand - one hand)
De stroomsterkte door het lichaam is afhankelijk van de aanrakingsspanning en de weerstand van het lichaam. Deze laatste is niet constant, maar hangt af van: | The current through the body depends on the touch voltage and the body's resistance. The latter is not constant but depends on: | extra assurance. The curve is positioned at such a distance from curve C1 that it is assumed any deviations from the average situation will not result in exceeding curve C1.
de aanrakingsspanning | the touch voltage | situation will not result in exceeding curve C1. The current through the body depends on the touch voltage and the body's resistance. The latter is not constant but depends on:
U | U | result in exceeding curve C1. The current through the body depends on the touch voltage and the body's resistance. The latter is not constant but depends on: the touch voltage
a | a | in exceeding curve C1. The current through the body depends on the touch voltage and the body's resistance. The latter is not constant but depends on: the touch voltage U
, | , | exceeding curve C1. The current through the body depends on the touch voltage and the body's resistance. The latter is not constant but depends on: the touch voltage U a
de manier van aanraken (een hand en een voet of twee handen en twee voeten), | the manner of contact (one hand and one foot or two hands and two feet), | curve C1. The current through the body depends on the touch voltage and the body's resistance. The latter is not constant but depends on: the touch voltage U a ,
de schoeiselweerstand. | the footwear resistance. | resistance. The latter is not constant but depends on: the touch voltage U a , the manner of contact (one hand and one foot or two hands and two feet),
De lichaamsweerstand is vastgelegd in de internationale norm IEC 60479. De lichaamsweerstand verschilt natuurlijk van persoon tot persoon. Daarom geeft de norm de weerstanden voor statistische bevolkingsgroepen (‘Best knowledge on the Total body impedances for living adults’). Figuur 5.15 geeft de curven met weerstandswaarden waar volgens de statistiek, 5, 50 en 95% van de bevolking onder blijft. De 5%-lijn is de veiligste en die wordt dan ook meestal gebruikt. | The body resistance is established in the international standard IEC 60479. Naturally, body resistance varies from person to person. Therefore, the standard provides the resistances for statistical population groups ("Best knowledge on the Total body impedances for living adults"). Figure 5.15 shows the curves with resistance values where, according to statistics, 5%, 50%, and 95% of the population fall below. The 5% line is the safest and is therefore most commonly used. | is not constant but depends on: the touch voltage U a , the manner of contact (one hand and one foot or two hands and two feet), the footwear resistance.
De lichaamsweerstand is gespecificeerd voor het geval dat de stroom het traject van een hand naar de andere hand aflegt of van een hand naar een voet. Meestal wordt de lichaamsweerstand berekend voor het aanraken met twee handen en met beide voeten op de grond, zodat de waarde uit de curven volgens IEC 60479 door 2 gedeeld moet worden. De aanrakingsspanning is meestal slechts een deel van de foutspanning, omdat het menselijk lichaam in serie staat met de weerstand van de vloer en van het schoeisel. De schoeiselweerstand | The body resistance is specified for the case where the current travels from one hand to the other hand or from one hand to a foot. Usually, the body resistance is calculated for touching with both hands and with both feet on the ground, so the value from the curves according to IEC 60479 must be divided by 2. The touch voltage is usually only a part of the fault voltage because the human body is in series with the resistance of the floor and the footwear. The footwear resistance | the curves with resistance values where, according to statistics, 5%, 50%, and 95% of the population fall below. The 5% line is the safest and is therefore most commonly used.
R | R | touch voltage is usually only a part of the fault voltage because the human body is in series with the resistance of the floor and the footwear. The footwear resistance
sch | sch | voltage is usually only a part of the fault voltage because the human body is in series with the resistance of the floor and the footwear. The footwear resistance R
is van veel factoren afhankelijk, maar een gebruikelijke waarde is 1000 Ω. Het uitrekenen van de maximale tijd waarbinnen een foutspanning moet worden afgeschakeld is een iteratief proces, omdat de aanrakingsspanning wordt bepaald door de spanningsdeling over de weerstanden | depends on many factors, but a common value is 1000 Ω. Calculating the maximum time within which a fault voltage must be disconnected is an iterative process, because the touch voltage is determined by the voltage division over the resistances. | is usually only a part of the fault voltage because the human body is in series with the resistance of the floor and the footwear. The footwear resistance R sch
R | R | Ω. Calculating the maximum time within which a fault voltage must be disconnected is an iterative process, because the touch voltage is determined by the voltage division over the resistances.
m | m | Calculating the maximum time within which a fault voltage must be disconnected is an iterative process, because the touch voltage is determined by the voltage division over the resistances. R
en R | and R | the maximum time within which a fault voltage must be disconnected is an iterative process, because the touch voltage is determined by the voltage division over the resistances. R m
sch | sch | time within which a fault voltage must be disconnected is an iterative process, because the touch voltage is determined by the voltage division over the resistances. R m and R
over de foutspanning | over the fault voltage | within which a fault voltage must be disconnected is an iterative process, because the touch voltage is determined by the voltage division over the resistances. R m and R sch
U | U | voltage must be disconnected is an iterative process, because the touch voltage is determined by the voltage division over the resistances. R m and R sch over the fault voltage
f | f | must be disconnected is an iterative process, because the touch voltage is determined by the voltage division over the resistances. R m and R sch over the fault voltage U
en de weerstand van de mens | and the resistance of the human | be disconnected is an iterative process, because the touch voltage is determined by the voltage division over the resistances. R m and R sch over the fault voltage U f
R | R | because the touch voltage is determined by the voltage division over the resistances. R m and R sch over the fault voltage U f and the resistance of the human
m | m | the touch voltage is determined by the voltage division over the resistances. R m and R sch over the fault voltage U f and the resistance of the human R
afhangt van de aanrakingsspanning | depends on the touch voltage | touch voltage is determined by the voltage division over the resistances. R m and R sch over the fault voltage U f and the resistance of the human R m
U | U | the voltage division over the resistances. R m and R sch over the fault voltage U f and the resistance of the human R m depends on the touch voltage
a | a | voltage division over the resistances. R m and R sch over the fault voltage U f and the resistance of the human R m depends on the touch voltage U
. | . | division over the resistances. R m and R sch over the fault voltage U f and the resistance of the human R m depends on the touch voltage U a
Figuur 5.16 Spanningsdeling voor het berekenen van de aanrakingsspanning | Figure 5.16 Voltage division for calculating the touch voltage | over the resistances. R m and R sch over the fault voltage U f and the resistance of the human R m depends on the touch voltage U a .
Ondanks het feit dat de gevaarlijke invloedsfactor de stroomsterkte is en niet de spanning, zijn de beschermingsmaatregelen vaak geformuleerd als een spanningsbeperking. Hierbij is gebruik gemaakt van het verband tussen de stroomsterkte en de aanrakingsspanning. Dit wordt gedaan omdat een spanning gemakkelijk meetbaar is. In dit boek wordt echter steeds uitgegaan van de stroom door het menselijk lichaam. | Despite the fact that the dangerous influencing factor is the current and not the voltage, the protective measures are often formulated as a voltage limitation. This is based on the relationship between the current and the touch voltage. This is done because voltage is easily measurable. However, in this book, the focus is consistently on the current through the human body. | the fault voltage U f and the resistance of the human R m depends on the touch voltage U a . Figure 5.16 Voltage division for calculating the touch voltage
5.7.1 Kortsluiting in een TT-stelsel | 5.7.1 Short Circuit in a TT System | between the current and the touch voltage. This is done because voltage is easily measurable. However, in this book, the focus is consistently on the current through the human body.
Bij toepassing van het TT-stelsel kan een fase-aardsluiting in de installatie van de aangeslotene leiden tot een verhoogde spanning van de lokale aarde. Figuur 5.17 illustreert dit voor een kortsluiting tussen fase L1 en de PE van de installatie van de aangeslotene. Dit kan overigens ook een kortsluiting in een apparaat zijn. Hierdoor wordt de spanning op het lokale aardingssysteem van de aangeslotene verhoogd. | When applying the TT system, a phase-to-earth fault in the consumer's installation can lead to an increased voltage of the local earth. Figure 5.17 illustrates this for a short circuit between phase L1 and the PE of the consumer's installation. This can also be a short circuit in a device. As a result, the voltage on the consumer's local grounding system is increased. | This is done because voltage is easily measurable. However, in this book, the focus is consistently on the current through the human body. 5.7.1 Short Circuit in a TT System
Figuur 5.17 Kortsluiting in een TT-stelsel | Figure 5.17 Short circuit in a TT system | and the PE of the consumer's installation. This can also be a short circuit in a device. As a result, the voltage on the consumer's local grounding system is increased.
De foutspanning voor een fase-aardfout in een installatie met TT-stelsel kan bij benadering worden berekend aan de hand van een eenvoudig vervangingsschema. In dit vervangingsschema zijn de impedanties weergegeven van de transformator ( | The fault voltage for a phase-to-earth fault in an installation with a TT system can be approximately calculated using a simple equivalent circuit. In this equivalent circuit, the impedances of the transformer are represented. | can also be a short circuit in a device. As a result, the voltage on the consumer's local grounding system is increased. Figure 5.17 Short circuit in a TT system
Z | Z | a phase-to-earth fault in an installation with a TT system can be approximately calculated using a simple equivalent circuit. In this equivalent circuit, the impedances of the transformer are represented.
T | T | phase-to-earth fault in an installation with a TT system can be approximately calculated using a simple equivalent circuit. In this equivalent circuit, the impedances of the transformer are represented. Z
), de fasegeleider ( | ), the phase conductor ( | fault in an installation with a TT system can be approximately calculated using a simple equivalent circuit. In this equivalent circuit, the impedances of the transformer are represented. Z T
Z | Z | a TT system can be approximately calculated using a simple equivalent circuit. In this equivalent circuit, the impedances of the transformer are represented. Z T ), the phase conductor (
L | L | TT system can be approximately calculated using a simple equivalent circuit. In this equivalent circuit, the impedances of the transformer are represented. Z T ), the phase conductor ( Z
), de nulgeleider ( | ), the neutral conductor ( | system can be approximately calculated using a simple equivalent circuit. In this equivalent circuit, the impedances of the transformer are represented. Z T ), the phase conductor ( Z L
Z | Z | using a simple equivalent circuit. In this equivalent circuit, the impedances of the transformer are represented. Z T ), the phase conductor ( Z L ), the neutral conductor (
N | N | a simple equivalent circuit. In this equivalent circuit, the impedances of the transformer are represented. Z T ), the phase conductor ( Z L ), the neutral conductor ( Z
) en de aardelektrode bij de nettransformator ( | ) and the grounding electrode at the network transformer ( | simple equivalent circuit. In this equivalent circuit, the impedances of the transformer are represented. Z T ), the phase conductor ( Z L ), the neutral conductor ( Z N
Z | Z | the transformer are represented. Z T ), the phase conductor ( Z L ), the neutral conductor ( Z N ) and the grounding electrode at the network transformer (
E1 | E1 | transformer are represented. Z T ), the phase conductor ( Z L ), the neutral conductor ( Z N ) and the grounding electrode at the network transformer ( Z
) en bij de installatie van de aangeslotene ( | ) and at the installation of the connected party | are represented. Z T ), the phase conductor ( Z L ), the neutral conductor ( Z N ) and the grounding electrode at the network transformer ( Z E1
Z | Z | Z L ), the neutral conductor ( Z N ) and the grounding electrode at the network transformer ( Z E1 ) and at the installation of the connected party
E2 | E2 | L ), the neutral conductor ( Z N ) and the grounding electrode at the network transformer ( Z E1 ) and at the installation of the connected party Z
). De fout is een fase-aardsluiting in de installatie van de aangeslotene. De foutspanning op de beschermingsleiding van de aangeslotene is | ). The fault is a phase-to-earth connection in the installation of the connected party. The fault voltage on the protective conductor of the connected party is | ), the neutral conductor ( Z N ) and the grounding electrode at the network transformer ( Z E1 ) and at the installation of the connected party Z E2
U | U | connected party Z E2 ). The fault is a phase-to-earth connection in the installation of the connected party. The fault voltage on the protective conductor of the connected party is
f | f | party Z E2 ). The fault is a phase-to-earth connection in the installation of the connected party. The fault voltage on the protective conductor of the connected party is U
. Eveneens zijn aangegeven: de weerstand van het menselijk lichaam ( | . Also indicated: the resistance of the human body ( | Z E2 ). The fault is a phase-to-earth connection in the installation of the connected party. The fault voltage on the protective conductor of the connected party is U f
R | R | the installation of the connected party. The fault voltage on the protective conductor of the connected party is U f . Also indicated: the resistance of the human body (
m | m | installation of the connected party. The fault voltage on the protective conductor of the connected party is U f . Also indicated: the resistance of the human body ( R
), de schoeiselweerstand naar aarde ( | ), the footwear resistance to earth ( | of the connected party. The fault voltage on the protective conductor of the connected party is U f . Also indicated: the resistance of the human body ( R m
R | R | on the protective conductor of the connected party is U f . Also indicated: the resistance of the human body ( R m ), the footwear resistance to earth (
sch | sch | the protective conductor of the connected party is U f . Also indicated: the resistance of the human body ( R m ), the footwear resistance to earth ( R
) en de aanrakingsspanning ( | ) and the touch voltage ( | protective conductor of the connected party is U f . Also indicated: the resistance of the human body ( R m ), the footwear resistance to earth ( R sch
U | U | is U f . Also indicated: the resistance of the human body ( R m ), the footwear resistance to earth ( R sch ) and the touch voltage (
a | a | U f . Also indicated: the resistance of the human body ( R m ), the footwear resistance to earth ( R sch ) and the touch voltage ( U
). | ). | f . Also indicated: the resistance of the human body ( R m ), the footwear resistance to earth ( R sch ) and the touch voltage ( U a
Figuur 5.18 Kortsluiting in een installatie met TT-stelsel | Figure 5.18 Short circuit in an installation with TT system | . Also indicated: the resistance of the human body ( R m ), the footwear resistance to earth ( R sch ) and the touch voltage ( U a ).
In het schema is zichtbaar dat het retourpad bestaat uit de serieschakeling van de aardelektrodes bij de distributietransformator en bij de installatie van de aangeslotene. De impedantie | In the diagram, it is visible that the return path consists of the series connection of the grounding electrodes at the distribution transformer and at the installation of the connected party. The impedance | R m ), the footwear resistance to earth ( R sch ) and the touch voltage ( U a ). Figure 5.18 Short circuit in an installation with TT system
Z | Z | it is visible that the return path consists of the series connection of the grounding electrodes at the distribution transformer and at the installation of the connected party. The impedance
f | f | is visible that the return path consists of the series connection of the grounding electrodes at the distribution transformer and at the installation of the connected party. The impedance Z
van het totale circuit voor de kortsluitstroom bestaat dan uit de serieschakeling van de transformatorimpedantie, de fase-impedantie en de retourimpedantie: | of the total circuit for the short-circuit current then consists of the series connection of the transformer impedance, the phase impedance, and the return impedance: | visible that the return path consists of the series connection of the grounding electrodes at the distribution transformer and at the installation of the connected party. The impedance Z f
[ | [ | party. The impedance Z f of the total circuit for the short-circuit current then consists of the series connection of the transformer impedance, the phase impedance, and the return impedance:
5.6 | 5.6 | The impedance Z f of the total circuit for the short-circuit current then consists of the series connection of the transformer impedance, the phase impedance, and the return impedance: [
] | ] | impedance Z f of the total circuit for the short-circuit current then consists of the series connection of the transformer impedance, the phase impedance, and the return impedance: [ 5.6
De kortsluitstroom wordt berekend uit de nominale transformatorfasespanning ( | The short-circuit current is calculated from the nominal transformer phase voltage | Z f of the total circuit for the short-circuit current then consists of the series connection of the transformer impedance, the phase impedance, and the return impedance: [ 5.6 ]
U | U | consists of the series connection of the transformer impedance, the phase impedance, and the return impedance: [ 5.6 ] The short-circuit current is calculated from the nominal transformer phase voltage
nom | nom | of the series connection of the transformer impedance, the phase impedance, and the return impedance: [ 5.6 ] The short-circuit current is calculated from the nominal transformer phase voltage U
) en de circuit-impedantie. Hierbij wordt uitgegaan dat de bron aan middenspanningszijde van de transformator oneindig sterk is. | ) and the circuit impedance. It is assumed that the source on the medium voltage side of the transformer is infinitely strong. | the series connection of the transformer impedance, the phase impedance, and the return impedance: [ 5.6 ] The short-circuit current is calculated from the nominal transformer phase voltage U nom
[ | [ | from the nominal transformer phase voltage U nom ) and the circuit impedance. It is assumed that the source on the medium voltage side of the transformer is infinitely strong.
5.7 | 5.7 | the nominal transformer phase voltage U nom ) and the circuit impedance. It is assumed that the source on the medium voltage side of the transformer is infinitely strong. [
] | ] | nominal transformer phase voltage U nom ) and the circuit impedance. It is assumed that the source on the medium voltage side of the transformer is infinitely strong. [ 5.7
De foutspanning op de PE van de aangeslotene wordt berekend uit de foutstroom en de impedantie van de aardelektrode van zijn installatie. Dit is gelijk aan de spanningsdeling van deze impedantie op de totale circuitimpedantie. | The fault voltage on the PE of the connected party is calculated from the fault current and the impedance of the grounding electrode of their installation. This is equal to the voltage division of this impedance over the total circuit impedance. | transformer phase voltage U nom ) and the circuit impedance. It is assumed that the source on the medium voltage side of the transformer is infinitely strong. [ 5.7 ]
[ | [ | calculated from the fault current and the impedance of the grounding electrode of their installation. This is equal to the voltage division of this impedance over the total circuit impedance.
5.8 | 5.8 | from the fault current and the impedance of the grounding electrode of their installation. This is equal to the voltage division of this impedance over the total circuit impedance. [
] | ] | the fault current and the impedance of the grounding electrode of their installation. This is equal to the voltage division of this impedance over the total circuit impedance. [ 5.8
Aan de hand van de aldus berekende foutspanning kan de stroom door het menselijk lichaam en daarmee de maximale tijdsduur worden bepaald. De aanrakingsspanning wordt als volgt berekend: | Based on the calculated fault voltage, the current through the human body and thus the maximum duration can be determined. The touch voltage is calculated as follows: | fault current and the impedance of the grounding electrode of their installation. This is equal to the voltage division of this impedance over the total circuit impedance. [ 5.8 ]
[ | [ | [ 5.8 ] Based on the calculated fault voltage, the current through the human body and thus the maximum duration can be determined. The touch voltage is calculated as follows:
5.9 | 5.9 | 5.8 ] Based on the calculated fault voltage, the current through the human body and thus the maximum duration can be determined. The touch voltage is calculated as follows: [
] | ] | ] Based on the calculated fault voltage, the current through the human body and thus the maximum duration can be determined. The touch voltage is calculated as follows: [ 5.9
Vervolgens kan de stroom door het menselijk lichaam worden berekend: | Subsequently, the current through the human body can be calculated: | Based on the calculated fault voltage, the current through the human body and thus the maximum duration can be determined. The touch voltage is calculated as follows: [ 5.9 ]
[ | [ | human body and thus the maximum duration can be determined. The touch voltage is calculated as follows: [ 5.9 ] Subsequently, the current through the human body can be calculated:
5.10 | 5.10 | body and thus the maximum duration can be determined. The touch voltage is calculated as follows: [ 5.9 ] Subsequently, the current through the human body can be calculated: [
] | ] | and thus the maximum duration can be determined. The touch voltage is calculated as follows: [ 5.9 ] Subsequently, the current through the human body can be calculated: [ 5.10
Aangezien de lichaamsweerstand | Since the body resistance | thus the maximum duration can be determined. The touch voltage is calculated as follows: [ 5.9 ] Subsequently, the current through the human body can be calculated: [ 5.10 ]
R | R | can be determined. The touch voltage is calculated as follows: [ 5.9 ] Subsequently, the current through the human body can be calculated: [ 5.10 ] Since the body resistance
m | m | be determined. The touch voltage is calculated as follows: [ 5.9 ] Subsequently, the current through the human body can be calculated: [ 5.10 ] Since the body resistance R
afhankelijk is van de spanning, moet deze berekening iteratief worden uitgevoerd. | depends on the voltage, this calculation must be performed iteratively. | determined. The touch voltage is calculated as follows: [ 5.9 ] Subsequently, the current through the human body can be calculated: [ 5.10 ] Since the body resistance R m
Rekenvoorbeeld TT-stelsel | Example calculation TT system | ] Subsequently, the current through the human body can be calculated: [ 5.10 ] Since the body resistance R m depends on the voltage, this calculation must be performed iteratively.
Een laagspanningsnet wordt gevoed via een 10250/400 V transformator van 250 kVA (u | A low-voltage network is powered by a 10250/400 V transformer of 250 kVA (u | through the human body can be calculated: [ 5.10 ] Since the body resistance R m depends on the voltage, this calculation must be performed iteratively. Example calculation TT system
k | k | R m depends on the voltage, this calculation must be performed iteratively. Example calculation TT system A low-voltage network is powered by a 10250/400 V transformer of 250 kVA (u
m depends on the voltage, this calculation must be performed iteratively. Example calculation TT system A low-voltage network is powered by a 10250/400 V transformer of 250 kVA (u k
k | k | the voltage, this calculation must be performed iteratively. Example calculation TT system A low-voltage network is powered by a 10250/400 V transformer of 250 kVA (u k =4% and P
voltage, this calculation must be performed iteratively. Example calculation TT system A low-voltage network is powered by a 10250/400 V transformer of 250 kVA (u k =4% and P k
Z | Z | calculation TT system A low-voltage network is powered by a 10250/400 V transformer of 250 kVA (u k =4% and P k =2.8 kW). The impedance of this transformer is:
T | T | TT system A low-voltage network is powered by a 10250/400 V transformer of 250 kVA (u k =4% and P k =2.8 kW). The impedance of this transformer is: Z
system A low-voltage network is powered by a 10250/400 V transformer of 250 kVA (u k =4% and P k =2.8 kW). The impedance of this transformer is: Z T
De laagspanningsstreng is 300 m lang. Het kabeltype is 4x95 VVMvKsas/Alk. | The low-voltage line is 300 meters long. The cable type is 4x95 VVMvKsas/Alk. | powered by a 10250/400 V transformer of 250 kVA (u k =4% and P k =2.8 kW). The impedance of this transformer is: Z T = 0.0072 + j0.0246 Ω.
Figuur 5.19 Rekenvoorbeeld TT-stelsel | Figure 5.19 Calculation Example TT System | P k =2.8 kW). The impedance of this transformer is: Z T = 0.0072 + j0.0246 Ω. The low-voltage line is 300 meters long. The cable type is 4x95 VVMvKsas/Alk.
De impedantie van de fasegeleider over 300 m is: | The impedance of the phase conductor over 300 meters is: | of this transformer is: Z T = 0.0072 + j0.0246 Ω. The low-voltage line is 300 meters long. The cable type is 4x95 VVMvKsas/Alk. Figure 5.19 Calculation Example TT System
Z | Z | Ω. The low-voltage line is 300 meters long. The cable type is 4x95 VVMvKsas/Alk. Figure 5.19 Calculation Example TT System The impedance of the phase conductor over 300 meters is:
L | L | The low-voltage line is 300 meters long. The cable type is 4x95 VVMvKsas/Alk. Figure 5.19 Calculation Example TT System The impedance of the phase conductor over 300 meters is: Z
low-voltage line is 300 meters long. The cable type is 4x95 VVMvKsas/Alk. Figure 5.19 Calculation Example TT System The impedance of the phase conductor over 300 meters is: Z L
. | . | long. The cable type is 4x95 VVMvKsas/Alk. Figure 5.19 Calculation Example TT System The impedance of the phase conductor over 300 meters is: Z L = 0.0960 + j0.0246 Ω
De impedantie van de aardelektrode bij de distributietransformator is: | The impedance of the grounding electrode at the distribution transformer is: | The cable type is 4x95 VVMvKsas/Alk. Figure 5.19 Calculation Example TT System The impedance of the phase conductor over 300 meters is: Z L = 0.0960 + j0.0246 Ω .
Z | Z | System The impedance of the phase conductor over 300 meters is: Z L = 0.0960 + j0.0246 Ω . The impedance of the grounding electrode at the distribution transformer is:
E1 | E1 | The impedance of the phase conductor over 300 meters is: Z L = 0.0960 + j0.0246 Ω . The impedance of the grounding electrode at the distribution transformer is: Z
impedance of the phase conductor over 300 meters is: Z L = 0.0960 + j0.0246 Ω . The impedance of the grounding electrode at the distribution transformer is: Z E1
. | . | phase conductor over 300 meters is: Z L = 0.0960 + j0.0246 Ω . The impedance of the grounding electrode at the distribution transformer is: Z E1 = 1 Ω
De impedantie van de aardelektrode bij de installatie van de aangeslotene is: | The impedance of the grounding electrode at the installation of the connected party is: | conductor over 300 meters is: Z L = 0.0960 + j0.0246 Ω . The impedance of the grounding electrode at the distribution transformer is: Z E1 = 1 Ω .
Z | Z | impedance of the grounding electrode at the distribution transformer is: Z E1 = 1 Ω . The impedance of the grounding electrode at the installation of the connected party is:
E2 | E2 | of the grounding electrode at the distribution transformer is: Z E1 = 1 Ω . The impedance of the grounding electrode at the installation of the connected party is: Z
the grounding electrode at the distribution transformer is: Z E1 = 1 Ω . The impedance of the grounding electrode at the installation of the connected party is: Z E2
Hieruit volgt: | From this follows: | at the distribution transformer is: Z E1 = 1 Ω . The impedance of the grounding electrode at the installation of the connected party is: Z E2 = 2 Ω.
[ | [ | transformer is: Z E1 = 1 Ω . The impedance of the grounding electrode at the installation of the connected party is: Z E2 = 2 Ω. From this follows:
5.11 | 5.11 | is: Z E1 = 1 Ω . The impedance of the grounding electrode at the installation of the connected party is: Z E2 = 2 Ω. From this follows: [
] | ] | Z E1 = 1 Ω . The impedance of the grounding electrode at the installation of the connected party is: Z E2 = 2 Ω. From this follows: [ 5.11
Volgens de vuistregel van formule 5.1 moet voor de smeltveiligheid gelden: | According to the rule of thumb from formula 5.1, the following must apply for fuse safety: | E1 = 1 Ω . The impedance of the grounding electrode at the installation of the connected party is: Z E2 = 2 Ω. From this follows: [ 5.11 ]
I | I | connected party is: Z E2 = 2 Ω. From this follows: [ 5.11 ] According to the rule of thumb from formula 5.1, the following must apply for fuse safety:
n | n | party is: Z E2 = 2 Ω. From this follows: [ 5.11 ] According to the rule of thumb from formula 5.1, the following must apply for fuse safety: I
< 30 / Z | < 30 / Z | is: Z E2 = 2 Ω. From this follows: [ 5.11 ] According to the rule of thumb from formula 5.1, the following must apply for fuse safety: I n
retour | retour | 2 Ω. From this follows: [ 5.11 ] According to the rule of thumb from formula 5.1, the following must apply for fuse safety: I n < 30 / Z
Ω. From this follows: [ 5.11 ] According to the rule of thumb from formula 5.1, the following must apply for fuse safety: I n < 30 / Z retour
Door een fase-aardsluiting ontstaat bij de aangeslotene een foutspanning | A phase-to-earth fault at the connected party results in a fault voltage. | According to the rule of thumb from formula 5.1, the following must apply for fuse safety: I n < 30 / Z retour = 30 / 3 = 10 A
U | U | apply for fuse safety: I n < 30 / Z retour = 30 / 3 = 10 A A phase-to-earth fault at the connected party results in a fault voltage.
f | f | for fuse safety: I n < 30 / Z retour = 30 / 3 = 10 A A phase-to-earth fault at the connected party results in a fault voltage. U
met een absolute waarde van 148 V. | with an absolute value of 148 V. | fuse safety: I n < 30 / Z retour = 30 / 3 = 10 A A phase-to-earth fault at the connected party results in a fault voltage. U f
De schoeiselweerstand | The footwear resistance | Z retour = 30 / 3 = 10 A A phase-to-earth fault at the connected party results in a fault voltage. U f with an absolute value of 148 V.
R | R | 30 / 3 = 10 A A phase-to-earth fault at the connected party results in a fault voltage. U f with an absolute value of 148 V. The footwear resistance
sch | sch | / 3 = 10 A A phase-to-earth fault at the connected party results in a fault voltage. U f with an absolute value of 148 V. The footwear resistance R
is 1000 Ω. | is 1000 Ω. | 3 = 10 A A phase-to-earth fault at the connected party results in a fault voltage. U f with an absolute value of 148 V. The footwear resistance R sch
De toegepaste curve voor de lichaamsweerstand is de 5%-curve. | The applied curve for body resistance is the 5% curve. | A A phase-to-earth fault at the connected party results in a fault voltage. U f with an absolute value of 148 V. The footwear resistance R sch is 1000 Ω.
De aanrakingswijze is met twee handen en twee voeten. Hierdoor wordt de lichaamsweerstand door 2 gedeeld: | The method of contact is with two hands and two feet. As a result, the body resistance is divided by 2: | a fault voltage. U f with an absolute value of 148 V. The footwear resistance R sch is 1000 Ω. The applied curve for body resistance is the 5% curve.
R | R | applied curve for body resistance is the 5% curve. The method of contact is with two hands and two feet. As a result, the body resistance is divided by 2:
m | m | curve for body resistance is the 5% curve. The method of contact is with two hands and two feet. As a result, the body resistance is divided by 2: R
’ = R | ' = R | for body resistance is the 5% curve. The method of contact is with two hands and two feet. As a result, the body resistance is divided by 2: R m
m | m | is the 5% curve. The method of contact is with two hands and two feet. As a result, the body resistance is divided by 2: R m ' = R
/ 2. | / 2. | the 5% curve. The method of contact is with two hands and two feet. As a result, the body resistance is divided by 2: R m ' = R m
De lichaamsweerstand van de mens hangt af van de te berekenen aanrakingsspanning | The body's resistance of a human depends on the contact voltage to be calculated. | curve. The method of contact is with two hands and two feet. As a result, the body resistance is divided by 2: R m ' = R m / 2.
U | U | result, the body resistance is divided by 2: R m ' = R m / 2. The body's resistance of a human depends on the contact voltage to be calculated.
a | a | the body resistance is divided by 2: R m ' = R m / 2. The body's resistance of a human depends on the contact voltage to be calculated. U
en moet eerst geschat worden. Neem bijvoorbeeld aan dat de weerstand | and must first be estimated. For example, assume that the resistance | body resistance is divided by 2: R m ' = R m / 2. The body's resistance of a human depends on the contact voltage to be calculated. U a
R | R | m / 2. The body's resistance of a human depends on the contact voltage to be calculated. U a and must first be estimated. For example, assume that the resistance
m | m | / 2. The body's resistance of a human depends on the contact voltage to be calculated. U a and must first be estimated. For example, assume that the resistance R
gelijk is aan de schoeiselweerstand | is equal to the footwear resistance | 2. The body's resistance of a human depends on the contact voltage to be calculated. U a and must first be estimated. For example, assume that the resistance R m
R | R | human depends on the contact voltage to be calculated. U a and must first be estimated. For example, assume that the resistance R m is equal to the footwear resistance
sch | sch | depends on the contact voltage to be calculated. U a and must first be estimated. For example, assume that the resistance R m is equal to the footwear resistance R
, waardoor: | , resulting in: | on the contact voltage to be calculated. U a and must first be estimated. For example, assume that the resistance R m is equal to the footwear resistance R sch
U | U | voltage to be calculated. U a and must first be estimated. For example, assume that the resistance R m is equal to the footwear resistance R sch , resulting in:
a | a | to be calculated. U a and must first be estimated. For example, assume that the resistance R m is equal to the footwear resistance R sch , resulting in: U
be calculated. U a and must first be estimated. For example, assume that the resistance R m is equal to the footwear resistance R sch , resulting in: U a
f | f | U a and must first be estimated. For example, assume that the resistance R m is equal to the footwear resistance R sch , resulting in: U a = U
/ 2 = 74 V | / 2 = 74 V | a and must first be estimated. For example, assume that the resistance R m is equal to the footwear resistance R sch , resulting in: U a = U f
. | . | estimated. For example, assume that the resistance R m is equal to the footwear resistance R sch , resulting in: U a = U f / 2 = 74 V
Uit de 5%-curve volgt: | From the 5% curve follows: | For example, assume that the resistance R m is equal to the footwear resistance R sch , resulting in: U a = U f / 2 = 74 V .
R | R | resistance R m is equal to the footwear resistance R sch , resulting in: U a = U f / 2 = 74 V . From the 5% curve follows:
m | m | R m is equal to the footwear resistance R sch , resulting in: U a = U f / 2 = 74 V . From the 5% curve follows: R
(75) = 1125 Ω | (75) = 1125 Ω | m is equal to the footwear resistance R sch , resulting in: U a = U f / 2 = 74 V . From the 5% curve follows: R m
. | . | the footwear resistance R sch , resulting in: U a = U f / 2 = 74 V . From the 5% curve follows: R m (75) = 1125 Ω
Uit de gekozen aanrakingswijze volgt: | From the chosen method of contact follows: | footwear resistance R sch , resulting in: U a = U f / 2 = 74 V . From the 5% curve follows: R m (75) = 1125 Ω .
R | R | U a = U f / 2 = 74 V . From the 5% curve follows: R m (75) = 1125 Ω . From the chosen method of contact follows:
m | m | a = U f / 2 = 74 V . From the 5% curve follows: R m (75) = 1125 Ω . From the chosen method of contact follows: R
(75)’ = 1125 / 2 = 562,5 Ω | (75)’ = 1125 / 2 = 562.5 Ω
. | . | . From the 5% curve follows: R m (75) = 1125 Ω . From the chosen method of contact follows: R m (75)’ = 1125 / 2 = 562.5 Ω
Uit de spanningsdeling volgt voor de aanrakingsspanning: | From the voltage division follows for the touch voltage: | From the 5% curve follows: R m (75) = 1125 Ω . From the chosen method of contact follows: R m (75)’ = 1125 / 2 = 562.5 Ω .
U | U | 1125 Ω . From the chosen method of contact follows: R m (75)’ = 1125 / 2 = 562.5 Ω . From the voltage division follows for the touch voltage:
a | a | Ω . From the chosen method of contact follows: R m (75)’ = 1125 / 2 = 562.5 Ω . From the voltage division follows for the touch voltage: U
. From the chosen method of contact follows: R m (75)’ = 1125 / 2 = 562.5 Ω . From the voltage division follows for the touch voltage: U a
f | f | the chosen method of contact follows: R m (75)’ = 1125 / 2 = 562.5 Ω . From the voltage division follows for the touch voltage: U a = U
· R | · R | chosen method of contact follows: R m (75)’ = 1125 / 2 = 562.5 Ω . From the voltage division follows for the touch voltage: U a = U f
m | m | of contact follows: R m (75)’ = 1125 / 2 = 562.5 Ω . From the voltage division follows for the touch voltage: U a = U f · R
(75)’ / (R | (75)’ / (R | contact follows: R m (75)’ = 1125 / 2 = 562.5 Ω . From the voltage division follows for the touch voltage: U a = U f · R m
m | m | m (75)’ = 1125 / 2 = 562.5 Ω . From the voltage division follows for the touch voltage: U a = U f · R m (75)’ / (R
(75)’ + R | (75)’ + R | (75)’ = 1125 / 2 = 562.5 Ω . From the voltage division follows for the touch voltage: U a = U f · R m (75)’ / (R m
sch | sch | / 2 = 562.5 Ω . From the voltage division follows for the touch voltage: U a = U f · R m (75)’ / (R m (75)’ + R
) = 148 · 562,5 / (562,5+1000) = 53 V | ) = 148 · 562.5 / (562.5 + 1000) = 53 V | 2 = 562.5 Ω . From the voltage division follows for the touch voltage: U a = U f · R m (75)’ / (R m (75)’ + R sch
Dit is een eerste benadering van de waarde van de aanrakingsspanning. Met deze waarde kan de lichaamsweerstand van de mens worden gecorrigeerd. Volgens de 5%-curve uit figuur 5.15 is de lichaamsweerstand: | This is a first approximation of the value of the touch voltage. With this value, the human body's resistance can be corrected. According to the 5% curve from figure 5.15, the body resistance is: | touch voltage: U a = U f · R m (75)’ / (R m (75)’ + R sch ) = 148 · 562.5 / (562.5 + 1000) = 53 V
R | R | approximation of the value of the touch voltage. With this value, the human body's resistance can be corrected. According to the 5% curve from figure 5.15, the body resistance is:
m | m | of the value of the touch voltage. With this value, the human body's resistance can be corrected. According to the 5% curve from figure 5.15, the body resistance is: R
(53) = 1350 Ω | (53) = 1350 Ω | the value of the touch voltage. With this value, the human body's resistance can be corrected. According to the 5% curve from figure 5.15, the body resistance is: R m
. | . | touch voltage. With this value, the human body's resistance can be corrected. According to the 5% curve from figure 5.15, the body resistance is: R m (53) = 1350 Ω
Uit de gekozen aanrakingswijze volgt: | From the chosen method of contact follows: | voltage. With this value, the human body's resistance can be corrected. According to the 5% curve from figure 5.15, the body resistance is: R m (53) = 1350 Ω .
R | R | resistance can be corrected. According to the 5% curve from figure 5.15, the body resistance is: R m (53) = 1350 Ω . From the chosen method of contact follows:
m | m | can be corrected. According to the 5% curve from figure 5.15, the body resistance is: R m (53) = 1350 Ω . From the chosen method of contact follows: R
(53)’ = 1350 / 2 = 675 Ω. | (53)’ = 1350 / 2 = 675 Ω. | be corrected. According to the 5% curve from figure 5.15, the body resistance is: R m (53) = 1350 Ω . From the chosen method of contact follows: R m
Uit de spanningsdeling volgt voor de aanrakingsspanning: | From the voltage division, the touch voltage is: | figure 5.15, the body resistance is: R m (53) = 1350 Ω . From the chosen method of contact follows: R m (53)’ = 1350 / 2 = 675 Ω.
U | U | (53) = 1350 Ω . From the chosen method of contact follows: R m (53)’ = 1350 / 2 = 675 Ω. From the voltage division, the touch voltage is:
a | a
1350 Ω . From the chosen method of contact follows: R m (53)’ = 1350 / 2 = 675 Ω. From the voltage division, the touch voltage is: U a
f | f | . From the chosen method of contact follows: R m (53)’ = 1350 / 2 = 675 Ω. From the voltage division, the touch voltage is: U a = U
· R | · R | From the chosen method of contact follows: R m (53)’ = 1350 / 2 = 675 Ω. From the voltage division, the touch voltage is: U a = U f
m | m | chosen method of contact follows: R m (53)’ = 1350 / 2 = 675 Ω. From the voltage division, the touch voltage is: U a = U f · R
(53)’ / (R | (53)’ / (R | method of contact follows: R m (53)’ = 1350 / 2 = 675 Ω. From the voltage division, the touch voltage is: U a = U f · R m
m | m | follows: R m (53)’ = 1350 / 2 = 675 Ω. From the voltage division, the touch voltage is: U a = U f · R m (53)’ / (R
(53)’ + R | (53)’ + R | R m (53)’ = 1350 / 2 = 675 Ω. From the voltage division, the touch voltage is: U a = U f · R m (53)’ / (R m
sch | sch
) = 148 · 675 / (675+1000) = 60 V | ) = 148 · 675 / (675+1000) = 60 V | 1350 / 2 = 675 Ω. From the voltage division, the touch voltage is: U a = U f · R m (53)’ / (R m (53)’ + R sch
De berekening moet net zolang herhaald worden tot dat de aanrakingsspanning niet meer verandert. In bovenstaand rekenvoorbeeld wordt ervan uitgegaan dat de juiste aanrakingsspanning 60 V is. | The calculation must be repeated until the touch voltage no longer changes. In the above calculation example, it is assumed that the correct touch voltage is 60 V. | the touch voltage is: U a = U f · R m (53)’ / (R m (53)’ + R sch ) = 148 · 675 / (675+1000) = 60 V
De bijbehorende waarde voor | The corresponding value for | 60 V The calculation must be repeated until the touch voltage no longer changes. In the above calculation example, it is assumed that the correct touch voltage is 60 V.
R | R | must be repeated until the touch voltage no longer changes. In the above calculation example, it is assumed that the correct touch voltage is 60 V. The corresponding value for
m | m | be repeated until the touch voltage no longer changes. In the above calculation example, it is assumed that the correct touch voltage is 60 V. The corresponding value for R
(60)’ is 1300 / 2 = 650 Ω | (60)’ is 1300 / 2 = 650 Ω | repeated until the touch voltage no longer changes. In the above calculation example, it is assumed that the correct touch voltage is 60 V. The corresponding value for R m
. Nu kan de stroom door het lichaam van de mens berekend worden: | . Now the current through the human body can be calculated: | In the above calculation example, it is assumed that the correct touch voltage is 60 V. The corresponding value for R m (60)’ is 1300 / 2 = 650 Ω
[ | [ | touch voltage is 60 V. The corresponding value for R m (60)’ is 1300 / 2 = 650 Ω . Now the current through the human body can be calculated:
5.12 | 5.12 | voltage is 60 V. The corresponding value for R m (60)’ is 1300 / 2 = 650 Ω . Now the current through the human body can be calculated: [
] | ] | is 60 V. The corresponding value for R m (60)’ is 1300 / 2 = 650 Ω . Now the current through the human body can be calculated: [ 5.12
Deze stroomwaarde kan worden opgezocht in de stroom-tijd gevarencurves van figuur 5.14. Hieruit volgt bij toepassing van de C1-curve dat deze stroom ongeveer binnen 550 ms moet worden afgeschakeld. | This current value can be looked up in the current-time hazard curves of figure 5.14. From this, it follows that by applying the C1 curve, this current must be switched off within approximately 550 ms. | 60 V. The corresponding value for R m (60)’ is 1300 / 2 = 650 Ω . Now the current through the human body can be calculated: [ 5.12 ]
Hoe snel de kortsluiting daadwerkelijk wordt afgeschakeld, hangt voornamelijk af van de impedanties van de toegepaste aardelektrodes en de specificaties van de toegepaste beveiliging. | How quickly the short circuit is actually disconnected mainly depends on the impedances of the applied grounding electrodes and the specifications of the applied protection. | looked up in the current-time hazard curves of figure 5.14. From this, it follows that by applying the C1 curve, this current must be switched off within approximately 550 ms.
5.7.2 Kortsluiting in een TN-stelsel | 5.7.2 Short Circuit in a TN System | off within approximately 550 ms. How quickly the short circuit is actually disconnected mainly depends on the impedances of the applied grounding electrodes and the specifications of the applied protection.
Bij toepassing van een TN-stelsel moet rekening gehouden worden met het feit dat fase-aardsluitingen in het elektriciteitsnet leiden tot verhoogde aanrakingsspanningen op het aardingssysteem ten opzichte van de lokale aardpotentiaal bij de aangeslotenen. Figuur 5.20 illustreert dit voor een kortsluiting tussen fase L1 en de nulgeleider, waardoor de spanning op de nulgeleider verhoogd wordt. Doordat op zoveel mogelijk plaatsen de nul- en de PE-geleiders met elkaar verbonden zijn, wordt ook de spanning op het aardingssysteem verhoogd. Een mens, die in aanraking komt met een geaard apparaat, ervaart dan deze verhoogde spanning U | When applying a TN system, it must be taken into account that phase-to-earth faults in the electrical network lead to increased touch voltages on the grounding system relative to the local earth potential at the connected points. Figure 5.20 illustrates this for a short circuit between phase L1 and the neutral conductor, which causes the voltage on the neutral conductor to increase. Because the neutral and PE conductors are connected at as many points as possible, the voltage on the grounding system is also increased. A person who comes into contact with a grounded device will then experience this increased voltage U. | the short circuit is actually disconnected mainly depends on the impedances of the applied grounding electrodes and the specifications of the applied protection. 5.7.2 Short Circuit in a TN System
f | f | many points as possible, the voltage on the grounding system is also increased. A person who comes into contact with a grounded device will then experience this increased voltage U.
ten opzichte van de lokale aarde. | relative to the local ground. | points as possible, the voltage on the grounding system is also increased. A person who comes into contact with a grounded device will then experience this increased voltage U. f
Figuur 5.20 Kortsluiting in een TN-C-S-stelsel | Figure 5.20 Short circuit in a TN-C-S system | on the grounding system is also increased. A person who comes into contact with a grounded device will then experience this increased voltage U. f relative to the local ground.
De foutspanning voor een fase-aardfout in een laagspanningsstreng met TN-C-S-stelsel kan bij benadering worden berekend aan de hand van een eenvoudig vervangingsschema. In dit vervangingsschema zijn de impedanties weergegeven van de transformator ( | The fault voltage for a phase-to-earth fault in a low voltage line with a TN-C-S system can be approximately calculated using a simple equivalent circuit. In this equivalent circuit, the impedances of the transformer are represented. | person who comes into contact with a grounded device will then experience this increased voltage U. f relative to the local ground. Figure 5.20 Short circuit in a TN-C-S system
Z | Z | fault in a low voltage line with a TN-C-S system can be approximately calculated using a simple equivalent circuit. In this equivalent circuit, the impedances of the transformer are represented.
T | T | in a low voltage line with a TN-C-S system can be approximately calculated using a simple equivalent circuit. In this equivalent circuit, the impedances of the transformer are represented. Z
), de fasegeleider ( | ), the phase conductor | a low voltage line with a TN-C-S system can be approximately calculated using a simple equivalent circuit. In this equivalent circuit, the impedances of the transformer are represented. Z T
Z | Z | with a TN-C-S system can be approximately calculated using a simple equivalent circuit. In this equivalent circuit, the impedances of the transformer are represented. Z T ), the phase conductor
L | L | a TN-C-S system can be approximately calculated using a simple equivalent circuit. In this equivalent circuit, the impedances of the transformer are represented. Z T ), the phase conductor Z
), de nulgeleider ( | ), the neutral conductor ( | TN-C-S system can be approximately calculated using a simple equivalent circuit. In this equivalent circuit, the impedances of the transformer are represented. Z T ), the phase conductor Z L
Z | Z | calculated using a simple equivalent circuit. In this equivalent circuit, the impedances of the transformer are represented. Z T ), the phase conductor Z L ), the neutral conductor (
N | N | using a simple equivalent circuit. In this equivalent circuit, the impedances of the transformer are represented. Z T ), the phase conductor Z L ), the neutral conductor ( Z
), de PE-geleider ( | ), the PE conductor ( | a simple equivalent circuit. In this equivalent circuit, the impedances of the transformer are represented. Z T ), the phase conductor Z L ), the neutral conductor ( Z N
Z | Z | this equivalent circuit, the impedances of the transformer are represented. Z T ), the phase conductor Z L ), the neutral conductor ( Z N ), the PE conductor (
PE | PE | equivalent circuit, the impedances of the transformer are represented. Z T ), the phase conductor Z L ), the neutral conductor ( Z N ), the PE conductor ( Z
) en de aardelektrode bij de nettransformator ( | ) and the grounding electrode at the network transformer ( | circuit, the impedances of the transformer are represented. Z T ), the phase conductor Z L ), the neutral conductor ( Z N ), the PE conductor ( Z PE
Z | Z | ), the phase conductor Z L ), the neutral conductor ( Z N ), the PE conductor ( Z PE ) and the grounding electrode at the network transformer (
E1 | E1 | the phase conductor Z L ), the neutral conductor ( Z N ), the PE conductor ( Z PE ) and the grounding electrode at the network transformer ( Z
). De fout is een fase-aardsluiting aan het eind van de laagspanningsstreng. De foutspanning op de beschermingsleiding van de aangeslotene is | ). The fault is a phase-to-earth connection at the end of the low-voltage line. The fault voltage on the protective conductor of the connected equipment is | phase conductor Z L ), the neutral conductor ( Z N ), the PE conductor ( Z PE ) and the grounding electrode at the network transformer ( Z E1
U | U | transformer ( Z E1 ). The fault is a phase-to-earth connection at the end of the low-voltage line. The fault voltage on the protective conductor of the connected equipment is
f | f | ( Z E1 ). The fault is a phase-to-earth connection at the end of the low-voltage line. The fault voltage on the protective conductor of the connected equipment is U
. Eveneens zijn aangegeven: de weerstand van het menselijk lichaam ( | . Also indicated are: the resistance of the human body | Z E1 ). The fault is a phase-to-earth connection at the end of the low-voltage line. The fault voltage on the protective conductor of the connected equipment is U f
R | R | the end of the low-voltage line. The fault voltage on the protective conductor of the connected equipment is U f . Also indicated are: the resistance of the human body
m | m | end of the low-voltage line. The fault voltage on the protective conductor of the connected equipment is U f . Also indicated are: the resistance of the human body R
), de schoeiselweerstand naar aarde ( | ), the footwear resistance to earth ( | of the low-voltage line. The fault voltage on the protective conductor of the connected equipment is U f . Also indicated are: the resistance of the human body R m
R | R | on the protective conductor of the connected equipment is U f . Also indicated are: the resistance of the human body R m ), the footwear resistance to earth (
sch | sch | the protective conductor of the connected equipment is U f . Also indicated are: the resistance of the human body R m ), the footwear resistance to earth ( R
) en de aanrakingsspanning ( | ) and the touch voltage ( | protective conductor of the connected equipment is U f . Also indicated are: the resistance of the human body R m ), the footwear resistance to earth ( R sch
U | U | is U f . Also indicated are: the resistance of the human body R m ), the footwear resistance to earth ( R sch ) and the touch voltage (
a | a | U f . Also indicated are: the resistance of the human body R m ), the footwear resistance to earth ( R sch ) and the touch voltage ( U
). | ). | f . Also indicated are: the resistance of the human body R m ), the footwear resistance to earth ( R sch ) and the touch voltage ( U a
Figuur 5.21 Kortsluiting in een streng met TN-C-S-stelsel | Figure 5.21 Short circuit in a string with TN-C-S system | . Also indicated are: the resistance of the human body R m ), the footwear resistance to earth ( R sch ) and the touch voltage ( U a ).
In het schema is zichtbaar dat het retourpad bestaat uit de parallelschakeling van de nul- en de PE-geleider. De impedantie Z | In the diagram, it is visible that the return path consists of the parallel connection of the neutral and the PE conductor. The impedance Z | R m ), the footwear resistance to earth ( R sch ) and the touch voltage ( U a ). Figure 5.21 Short circuit in a string with TN-C-S system
f | f | a string with TN-C-S system In the diagram, it is visible that the return path consists of the parallel connection of the neutral and the PE conductor. The impedance Z
van het totale circuit voor de kortsluitstroom bestaat dan uit de serieschakeling van de transformatorimpedantie, de fase-impedantie en de retourimpedantie: | of the entire circuit for the short-circuit current then consists of the series connection of the transformer impedance, the phase impedance, and the return impedance: | string with TN-C-S system In the diagram, it is visible that the return path consists of the parallel connection of the neutral and the PE conductor. The impedance Z f
[ | [ | conductor. The impedance Z f of the entire circuit for the short-circuit current then consists of the series connection of the transformer impedance, the phase impedance, and the return impedance:
5.13 | 5.13 | The impedance Z f of the entire circuit for the short-circuit current then consists of the series connection of the transformer impedance, the phase impedance, and the return impedance: [
] | ] | impedance Z f of the entire circuit for the short-circuit current then consists of the series connection of the transformer impedance, the phase impedance, and the return impedance: [ 5.13
De kortsluitstroom wordt berekend uit de nominale transformatorspanning en de circuit-impedantie. Hierbij wordt uitgegaan dat de bron aan middenspanningszijde van de transformator oneindig sterk is. | The short-circuit current is calculated from the nominal transformer voltage and the circuit impedance. It is assumed that the source on the medium voltage side of the transformer is infinitely strong. | Z f of the entire circuit for the short-circuit current then consists of the series connection of the transformer impedance, the phase impedance, and the return impedance: [ 5.13 ]
[ | [ | short-circuit current is calculated from the nominal transformer voltage and the circuit impedance. It is assumed that the source on the medium voltage side of the transformer is infinitely strong.
5.14 | 5.14 | current is calculated from the nominal transformer voltage and the circuit impedance. It is assumed that the source on the medium voltage side of the transformer is infinitely strong. [
] | ] | is calculated from the nominal transformer voltage and the circuit impedance. It is assumed that the source on the medium voltage side of the transformer is infinitely strong. [ 5.14
De foutspanning op de PE wordt berekend uit de foutstroom en de retourimpedantie. Dit is gelijk aan de spanningsdeling van de retourimpedantie op de totale circuitimpedantie. | The fault voltage on the PE is calculated from the fault current and the return impedance. This is equal to the voltage division of the return impedance over the total circuit impedance. | calculated from the nominal transformer voltage and the circuit impedance. It is assumed that the source on the medium voltage side of the transformer is infinitely strong. [ 5.14 ]
[ | [ | voltage on the PE is calculated from the fault current and the return impedance. This is equal to the voltage division of the return impedance over the total circuit impedance.
5.15 | 5.15 | on the PE is calculated from the fault current and the return impedance. This is equal to the voltage division of the return impedance over the total circuit impedance. [
] | ] | the PE is calculated from the fault current and the return impedance. This is equal to the voltage division of the return impedance over the total circuit impedance. [ 5.15
De aanrakingsspanning, de stroom door het menselijk lichaam en de maximale tijdsduur worden op dezelfde manier berekenend als in vergelijkingen 5.9 en 5.10. De aanrakingsspanningen en de duur daarvan moeten begrensd blijven tot veilige waarden. Hierom wordt de impedantie van het retourpad zo klein mogelijk gehouden. Door de verhouding van impedanties van de distributietransformator en de fase- en retourgeleiders in de kabel, is de spanningsverhoging het grootst bij kortsluitingen aan het einde van een streng. Dit beperkt in een net met TN-stelsel de lengte van de kabel. Figuur 5.22 toont de spanningsverhoging op de PE-leiding als functie van de afstand van de foutplaats tot de distributietransformator voor een laagspanningsstreng van 300 m lange 4x95 VVMvKsas/Alk kabel, gevoed door een 10250/400 V transformator van 250 kVA. Hierbij is uitgegaan van fase-aardfouten in de netkabel. | The touch voltage, the current through the human body, and the maximum duration are calculated in the same way as in equations 5.9 and 5.10. The touch voltages and their duration must be limited to safe values. Therefore, the impedance of the return path is kept as low as possible. Due to the ratio of impedances of the distribution transformer and the phase and return conductors in the cable, the voltage increase is greatest during short circuits at the end of a section. This limits the length of the cable in a TN system network. Figure 5.22 shows the voltage increase on the PE conductor as a function of the distance from the fault location to the distribution transformer for a low-voltage section of a 300 m long 4x95 VVMvKsas/Alk cable, powered by a 10250/400 V transformer of 250 kVA. This assumes phase-to-earth faults in the network cable. | PE is calculated from the fault current and the return impedance. This is equal to the voltage division of the return impedance over the total circuit impedance. [ 5.15 ]
Figuur 5.22 Spanning op de PE als functie van de afstand van de kortsluitplaats tot het netstation | Figure 5.22 Voltage on the PE as a function of the distance from the short-circuit location to the substation | transformer for a low-voltage section of a 300 m long 4x95 VVMvKsas/Alk cable, powered by a 10250/400 V transformer of 250 kVA. This assumes phase-to-earth faults in the network cable.
Door de toenemende impedantie neemt de kortsluitstroom af naarmate de foutplaats zich verder naar het einde van de streng bevindt, waardoor een smeltveiligheid meer tijd nodig heeft om af te schakelen. Deze combinatie van hogere spanning op de PE en de langere duur van de kortsluiting maakt een kortsluiting op het einde van de streng gevaarlijker dan aan het begin van de streng. Met name dit fenomeen beperkt de lengte van de laagspanningskabel. Toepassing van snelle smeltveiligheden kan ruimte geven in de kabellengte. | Due to the increasing impedance, the short-circuit current decreases as the fault location moves further towards the end of the line, causing a fuse to take more time to disconnect. This combination of higher voltage on the PE and the longer duration of the short circuit makes a short circuit at the end of the line more dangerous than at the beginning of the line. This phenomenon, in particular, limits the length of the low-voltage cable. The application of fast-acting fuses can provide more flexibility in cable length. | of 250 kVA. This assumes phase-to-earth faults in the network cable. Figure 5.22 Voltage on the PE as a function of the distance from the short-circuit location to the substation
Samenvattend wordt de veiligheid bevorderd door een tijdige uitschakeling en door de beperking van de aanrakingsspanning. De tijdige uitschakeling wordt bepaald door de grootte van de kortsluitstroom en de gekozen beveiliging. De hoogte van de aanrakingsspanning wordt bepaald door de grootte van de impedantie van het pad naar de aarde. In het geval dat met traditionele middelen geen aanrakingsveilige situatie mogelijk is, worden snelle smeltveiligheden toegepast. | In summary, safety is enhanced by timely disconnection and by limiting the touch voltage. Timely disconnection is determined by the magnitude of the short-circuit current and the chosen protection. The level of touch voltage is determined by the impedance of the path to ground. In cases where a touch-safe situation cannot be achieved with traditional means, fast-acting fuses are applied. | than at the beginning of the line. This phenomenon, in particular, limits the length of the low-voltage cable. The application of fast-acting fuses can provide more flexibility in cable length.
Rekenvoorbeeld TN-stelsel | Calculation example TN system | level of touch voltage is determined by the impedance of the path to ground. In cases where a touch-safe situation cannot be achieved with traditional means, fast-acting fuses are applied.
Een laagspanningsnet wordt gevoed via een 10250/400 V transformator van 250 kVA (u | A low-voltage network is powered by a 10250/400 V transformer of 250 kVA. | is determined by the impedance of the path to ground. In cases where a touch-safe situation cannot be achieved with traditional means, fast-acting fuses are applied. Calculation example TN system
k | k | a touch-safe situation cannot be achieved with traditional means, fast-acting fuses are applied. Calculation example TN system A low-voltage network is powered by a 10250/400 V transformer of 250 kVA.
touch-safe situation cannot be achieved with traditional means, fast-acting fuses are applied. Calculation example TN system A low-voltage network is powered by a 10250/400 V transformer of 250 kVA. k
k | k | be achieved with traditional means, fast-acting fuses are applied. Calculation example TN system A low-voltage network is powered by a 10250/400 V transformer of 250 kVA. k =4% and P
achieved with traditional means, fast-acting fuses are applied. Calculation example TN system A low-voltage network is powered by a 10250/400 V transformer of 250 kVA. k =4% and P k
De impedantie van deze transformator is: | The impedance of this transformer is: | traditional means, fast-acting fuses are applied. Calculation example TN system A low-voltage network is powered by a 10250/400 V transformer of 250 kVA. k =4% and P k =2.8 kW).
Z | Z | Calculation example TN system A low-voltage network is powered by a 10250/400 V transformer of 250 kVA. k =4% and P k =2.8 kW). The impedance of this transformer is:
T | T | example TN system A low-voltage network is powered by a 10250/400 V transformer of 250 kVA. k =4% and P k =2.8 kW). The impedance of this transformer is: Z
TN system A low-voltage network is powered by a 10250/400 V transformer of 250 kVA. k =4% and P k =2.8 kW). The impedance of this transformer is: Z T
. | . | is powered by a 10250/400 V transformer of 250 kVA. k =4% and P k =2.8 kW). The impedance of this transformer is: Z T = 0.0072 + j0.0246 Ω
De laagspanningsstreng is 300 m lang. Het kabeltype is 4x95 VVMvKsas/Alk. | The low-voltage line is 300 meters long. The cable type is 4x95 VVMvKsas/Alk. | powered by a 10250/400 V transformer of 250 kVA. k =4% and P k =2.8 kW). The impedance of this transformer is: Z T = 0.0072 + j0.0246 Ω .
Figuur 5.23 Rekenvoorbeeld TN-stelsel | Figure 5.23 Calculation Example TN System | k =2.8 kW). The impedance of this transformer is: Z T = 0.0072 + j0.0246 Ω . The low-voltage line is 300 meters long. The cable type is 4x95 VVMvKsas/Alk.
De impedantie van de fasegeleider over 300 m is: | The impedance of the phase conductor over 300 meters is: | this transformer is: Z T = 0.0072 + j0.0246 Ω . The low-voltage line is 300 meters long. The cable type is 4x95 VVMvKsas/Alk. Figure 5.23 Calculation Example TN System
Z | Z | . The low-voltage line is 300 meters long. The cable type is 4x95 VVMvKsas/Alk. Figure 5.23 Calculation Example TN System The impedance of the phase conductor over 300 meters is:
L | L | The low-voltage line is 300 meters long. The cable type is 4x95 VVMvKsas/Alk. Figure 5.23 Calculation Example TN System The impedance of the phase conductor over 300 meters is: Z
low-voltage line is 300 meters long. The cable type is 4x95 VVMvKsas/Alk. Figure 5.23 Calculation Example TN System The impedance of the phase conductor over 300 meters is: Z L
. | . | long. The cable type is 4x95 VVMvKsas/Alk. Figure 5.23 Calculation Example TN System The impedance of the phase conductor over 300 meters is: Z L = 0.0960 + j0.0246 Ω
De impedantie van de nulgeleider is gelijk aan die van de fasegeleider: | The impedance of the neutral conductor is equal to that of the phase conductor: | The cable type is 4x95 VVMvKsas/Alk. Figure 5.23 Calculation Example TN System The impedance of the phase conductor over 300 meters is: Z L = 0.0960 + j0.0246 Ω .
Z | Z | of the phase conductor over 300 meters is: Z L = 0.0960 + j0.0246 Ω . The impedance of the neutral conductor is equal to that of the phase conductor:
N | N | the phase conductor over 300 meters is: Z L = 0.0960 + j0.0246 Ω . The impedance of the neutral conductor is equal to that of the phase conductor: Z
phase conductor over 300 meters is: Z L = 0.0960 + j0.0246 Ω . The impedance of the neutral conductor is equal to that of the phase conductor: Z N
L | L | over 300 meters is: Z L = 0.0960 + j0.0246 Ω . The impedance of the neutral conductor is equal to that of the phase conductor: Z N = Z
. | . | 300 meters is: Z L = 0.0960 + j0.0246 Ω . The impedance of the neutral conductor is equal to that of the phase conductor: Z N = Z L
De impedantie van de PE-geleider is: | The impedance of the PE conductor is: | meters is: Z L = 0.0960 + j0.0246 Ω . The impedance of the neutral conductor is equal to that of the phase conductor: Z N = Z L .
Z | Z | j0.0246 Ω . The impedance of the neutral conductor is equal to that of the phase conductor: Z N = Z L . The impedance of the PE conductor is:
PE | PE | Ω . The impedance of the neutral conductor is equal to that of the phase conductor: Z N = Z L . The impedance of the PE conductor is: Z
. The impedance of the neutral conductor is equal to that of the phase conductor: Z N = Z L . The impedance of the PE conductor is: Z PE
. | . | of the neutral conductor is equal to that of the phase conductor: Z N = Z L . The impedance of the PE conductor is: Z PE = 0.15 Ω
Vanwege de verbindingen tussen de nulgeleider en de PE-geleider zijn zij parallel geschakeld. | Due to the connections between the neutral conductor and the PE conductor, they are connected in parallel. | the neutral conductor is equal to that of the phase conductor: Z N = Z L . The impedance of the PE conductor is: Z PE = 0.15 Ω .
Als voorbeeld wordt een fase-aardsluiting aan het einde van de laagspanningsstreng doorgerekend: | As an example, a phase-to-earth fault at the end of the low-voltage line is calculated: | The impedance of the PE conductor is: Z PE = 0.15 Ω . Due to the connections between the neutral conductor and the PE conductor, they are connected in parallel.
[ | [ | the connections between the neutral conductor and the PE conductor, they are connected in parallel. As an example, a phase-to-earth fault at the end of the low-voltage line is calculated:
5.16 | 5.16 | connections between the neutral conductor and the PE conductor, they are connected in parallel. As an example, a phase-to-earth fault at the end of the low-voltage line is calculated: [
] | ] | between the neutral conductor and the PE conductor, they are connected in parallel. As an example, a phase-to-earth fault at the end of the low-voltage line is calculated: [ 5.16
Door een fase-aardsluiting ontstaat bij de aangeslotene een foutspanning | A phase-to-earth fault causes a fault voltage at the connected party. | the neutral conductor and the PE conductor, they are connected in parallel. As an example, a phase-to-earth fault at the end of the low-voltage line is calculated: [ 5.16 ]
U | U | parallel. As an example, a phase-to-earth fault at the end of the low-voltage line is calculated: [ 5.16 ] A phase-to-earth fault causes a fault voltage at the connected party.
f | f | As an example, a phase-to-earth fault at the end of the low-voltage line is calculated: [ 5.16 ] A phase-to-earth fault causes a fault voltage at the connected party. U
met een absolute waarde van 80 V. | with an absolute value of 80 V. | an example, a phase-to-earth fault at the end of the low-voltage line is calculated: [ 5.16 ] A phase-to-earth fault causes a fault voltage at the connected party. U f
De schoeiselweerstand | The footwear resistance | end of the low-voltage line is calculated: [ 5.16 ] A phase-to-earth fault causes a fault voltage at the connected party. U f with an absolute value of 80 V.
R | R | low-voltage line is calculated: [ 5.16 ] A phase-to-earth fault causes a fault voltage at the connected party. U f with an absolute value of 80 V. The footwear resistance
sch | sch | line is calculated: [ 5.16 ] A phase-to-earth fault causes a fault voltage at the connected party. U f with an absolute value of 80 V. The footwear resistance R
is 1000 Ω. | is 1000 Ω. | is calculated: [ 5.16 ] A phase-to-earth fault causes a fault voltage at the connected party. U f with an absolute value of 80 V. The footwear resistance R sch
De toegepaste curve voor de lichaamsweerstand is de 5%-curve. | The applied curve for body resistance is the 5% curve. | 5.16 ] A phase-to-earth fault causes a fault voltage at the connected party. U f with an absolute value of 80 V. The footwear resistance R sch is 1000 Ω.
De aanrakingswijze is met twee handen en twee voeten. Hierdoor wordt de lichaamsweerstand door 2 gedeeld: | The method of contact is with two hands and two feet. As a result, the body resistance is divided by 2: | the connected party. U f with an absolute value of 80 V. The footwear resistance R sch is 1000 Ω. The applied curve for body resistance is the 5% curve.
R | R | applied curve for body resistance is the 5% curve. The method of contact is with two hands and two feet. As a result, the body resistance is divided by 2:
m | m | curve for body resistance is the 5% curve. The method of contact is with two hands and two feet. As a result, the body resistance is divided by 2: R
’ = R | ' = R | for body resistance is the 5% curve. The method of contact is with two hands and two feet. As a result, the body resistance is divided by 2: R m
m | m | is the 5% curve. The method of contact is with two hands and two feet. As a result, the body resistance is divided by 2: R m ' = R
/ 2 | / 2 | the 5% curve. The method of contact is with two hands and two feet. As a result, the body resistance is divided by 2: R m ' = R m
. | . | curve. The method of contact is with two hands and two feet. As a result, the body resistance is divided by 2: R m ' = R m / 2
De lichaamsweerstand van de mens hangt af van de te berekenen aanrakingsspanning | The body resistance of a human depends on the contact voltage to be calculated. | The method of contact is with two hands and two feet. As a result, the body resistance is divided by 2: R m ' = R m / 2 .
U | U | the body resistance is divided by 2: R m ' = R m / 2 . The body resistance of a human depends on the contact voltage to be calculated.
a | a | body resistance is divided by 2: R m ' = R m / 2 . The body resistance of a human depends on the contact voltage to be calculated. U
en moet eerst geschat worden. Neem bijvoorbeeld aan dat de weerstand | must first be estimated. For example, assume that the resistance | resistance is divided by 2: R m ' = R m / 2 . The body resistance of a human depends on the contact voltage to be calculated. U a
R | R | m / 2 . The body resistance of a human depends on the contact voltage to be calculated. U a must first be estimated. For example, assume that the resistance
m | m | / 2 . The body resistance of a human depends on the contact voltage to be calculated. U a must first be estimated. For example, assume that the resistance R
gelijk is aan de schoeiselweerstand | is equal to the footwear resistance | 2 . The body resistance of a human depends on the contact voltage to be calculated. U a must first be estimated. For example, assume that the resistance R m
R | R | a human depends on the contact voltage to be calculated. U a must first be estimated. For example, assume that the resistance R m is equal to the footwear resistance
sch | sch | human depends on the contact voltage to be calculated. U a must first be estimated. For example, assume that the resistance R m is equal to the footwear resistance R
, waardoor: | , resulting in: | depends on the contact voltage to be calculated. U a must first be estimated. For example, assume that the resistance R m is equal to the footwear resistance R sch
U | U | contact voltage to be calculated. U a must first be estimated. For example, assume that the resistance R m is equal to the footwear resistance R sch , resulting in:
a | a | voltage to be calculated. U a must first be estimated. For example, assume that the resistance R m is equal to the footwear resistance R sch , resulting in: U
to be calculated. U a must first be estimated. For example, assume that the resistance R m is equal to the footwear resistance R sch , resulting in: U a
f | f | calculated. U a must first be estimated. For example, assume that the resistance R m is equal to the footwear resistance R sch , resulting in: U a = U
/ 2 = 40 V | / 2 = 40 V | U a must first be estimated. For example, assume that the resistance R m is equal to the footwear resistance R sch , resulting in: U a = U f
. | . | estimated. For example, assume that the resistance R m is equal to the footwear resistance R sch , resulting in: U a = U f / 2 = 40 V
Uit de 5%-curve volgt: R | From the 5% curve, it follows: R | For example, assume that the resistance R m is equal to the footwear resistance R sch , resulting in: U a = U f / 2 = 40 V .
m | m | m is equal to the footwear resistance R sch , resulting in: U a = U f / 2 = 40 V . From the 5% curve, it follows: R
(40) = 1500 Ω. | (40) = 1500 Ω. | is equal to the footwear resistance R sch , resulting in: U a = U f / 2 = 40 V . From the 5% curve, it follows: R m
Uit de gekozen aanrakingswijze volgt: | From the chosen method of contact, it follows: | footwear resistance R sch , resulting in: U a = U f / 2 = 40 V . From the 5% curve, it follows: R m (40) = 1500 Ω.
R | R | a = U f / 2 = 40 V . From the 5% curve, it follows: R m (40) = 1500 Ω. From the chosen method of contact, it follows:
m | m
(40)’ = 1500 / 2 = 750 Ω | (40)’ = 1500 / 2 = 750 Ω | U f / 2 = 40 V . From the 5% curve, it follows: R m (40) = 1500 Ω. From the chosen method of contact, it follows: R m
. | . | From the 5% curve, it follows: R m (40) = 1500 Ω. From the chosen method of contact, it follows: R m (40)’ = 1500 / 2 = 750 Ω
Uit de spanningsdeling volgt voor de aanrakingsspanning: | From the voltage division, it follows for the touch voltage: | the 5% curve, it follows: R m (40) = 1500 Ω. From the chosen method of contact, it follows: R m (40)’ = 1500 / 2 = 750 Ω .
U | U | Ω. From the chosen method of contact, it follows: R m (40)’ = 1500 / 2 = 750 Ω . From the voltage division, it follows for the touch voltage:
a | a | From the chosen method of contact, it follows: R m (40)’ = 1500 / 2 = 750 Ω . From the voltage division, it follows for the touch voltage: U
the chosen method of contact, it follows: R m (40)’ = 1500 / 2 = 750 Ω . From the voltage division, it follows for the touch voltage: U a
f | f | method of contact, it follows: R m (40)’ = 1500 / 2 = 750 Ω . From the voltage division, it follows for the touch voltage: U a = U
· R | · R | of contact, it follows: R m (40)’ = 1500 / 2 = 750 Ω . From the voltage division, it follows for the touch voltage: U a = U f
m | m | it follows: R m (40)’ = 1500 / 2 = 750 Ω . From the voltage division, it follows for the touch voltage: U a = U f · R
(40)’ / (R | (40)’ / (R | follows: R m (40)’ = 1500 / 2 = 750 Ω . From the voltage division, it follows for the touch voltage: U a = U f · R m
m | m | (40)’ = 1500 / 2 = 750 Ω . From the voltage division, it follows for the touch voltage: U a = U f · R m (40)’ / (R
(40)’ + R | (40)’ + R
sch | sch | 2 = 750 Ω . From the voltage division, it follows for the touch voltage: U a = U f · R m (40)’ / (R m (40)’ + R
) = 80 · 750 / (750+1000) = 34 V | ) = 80 · 750 / (750+1000) = 34 V
Dit is een eerste benadering van de waarde van de aanrakingsspanning. Met deze waarde kan de lichaamsweerstand van de mens worden gecorrigeerd. Volgens de 5%-curve uit figuur 5.15 is de lichaamsweerstand: | This is a first approximation of the value of the touch voltage. With this value, the human body resistance can be corrected. According to the 5% curve from figure 5.15, the body resistance is: | for the touch voltage: U a = U f · R m (40)’ / (R m (40)’ + R sch ) = 80 · 750 / (750+1000) = 34 V
R | R | approximation of the value of the touch voltage. With this value, the human body resistance can be corrected. According to the 5% curve from figure 5.15, the body resistance is:
m | m | of the value of the touch voltage. With this value, the human body resistance can be corrected. According to the 5% curve from figure 5.15, the body resistance is: R
(34) = 1600 Ω | (34) = 1600 Ω | the value of the touch voltage. With this value, the human body resistance can be corrected. According to the 5% curve from figure 5.15, the body resistance is: R m
. | . | touch voltage. With this value, the human body resistance can be corrected. According to the 5% curve from figure 5.15, the body resistance is: R m (34) = 1600 Ω
Uit de gekozen aanrakingswijze volgt: | From the chosen method of contact follows: | voltage. With this value, the human body resistance can be corrected. According to the 5% curve from figure 5.15, the body resistance is: R m (34) = 1600 Ω .
R | R | resistance can be corrected. According to the 5% curve from figure 5.15, the body resistance is: R m (34) = 1600 Ω . From the chosen method of contact follows:
m | m | can be corrected. According to the 5% curve from figure 5.15, the body resistance is: R m (34) = 1600 Ω . From the chosen method of contact follows: R
(34)’ = 1600 / 2 = 800 Ω | (34)’ = 1600 / 2 = 800 Ω | be corrected. According to the 5% curve from figure 5.15, the body resistance is: R m (34) = 1600 Ω . From the chosen method of contact follows: R m
. | . | figure 5.15, the body resistance is: R m (34) = 1600 Ω . From the chosen method of contact follows: R m (34)’ = 1600 / 2 = 800 Ω
Uit de spanningsdeling volgt voor de aanrakingsspanning: | From the voltage division, the touch voltage is: | 5.15, the body resistance is: R m (34) = 1600 Ω . From the chosen method of contact follows: R m (34)’ = 1600 / 2 = 800 Ω .
U | U
a | a | 1600 Ω . From the chosen method of contact follows: R m (34)’ = 1600 / 2 = 800 Ω . From the voltage division, the touch voltage is: U
Ω . From the chosen method of contact follows: R m (34)’ = 1600 / 2 = 800 Ω . From the voltage division, the touch voltage is: U a
f | f | From the chosen method of contact follows: R m (34)’ = 1600 / 2 = 800 Ω . From the voltage division, the touch voltage is: U a = U
· R | · R | the chosen method of contact follows: R m (34)’ = 1600 / 2 = 800 Ω . From the voltage division, the touch voltage is: U a = U f
m | m | method of contact follows: R m (34)’ = 1600 / 2 = 800 Ω . From the voltage division, the touch voltage is: U a = U f · R
(34)’ / (R | (34)’ / (R | of contact follows: R m (34)’ = 1600 / 2 = 800 Ω . From the voltage division, the touch voltage is: U a = U f · R m
m | m | R m (34)’ = 1600 / 2 = 800 Ω . From the voltage division, the touch voltage is: U a = U f · R m (34)’ / (R
(34)’ + R | (34)’ + R | m (34)’ = 1600 / 2 = 800 Ω . From the voltage division, the touch voltage is: U a = U f · R m (34)’ / (R m
sch | sch | 1600 / 2 = 800 Ω . From the voltage division, the touch voltage is: U a = U f · R m (34)’ / (R m (34)’ + R
) = 80 · 800 / (800+1000) = 35 V | ) = 80 · 800 / (800+1000) = 35 V | / 2 = 800 Ω . From the voltage division, the touch voltage is: U a = U f · R m (34)’ / (R m (34)’ + R sch
De berekening moet net zolang herhaald worden tot dat de aanrakingsspanning niet meer verandert. In bovenstaand rekenvoorbeeld wordt ervan uitgegaan dat de juiste aanrakingsspanning 35 V is. Voor het gemak wordt ook uitgegaan van | The calculation must be repeated until the touch voltage no longer changes. In the above calculation example, it is assumed that the correct touch voltage is 35 V. For convenience, it is also assumed that | the touch voltage is: U a = U f · R m (34)’ / (R m (34)’ + R sch ) = 80 · 800 / (800+1000) = 35 V
R | R | until the touch voltage no longer changes. In the above calculation example, it is assumed that the correct touch voltage is 35 V. For convenience, it is also assumed that
m | m | the touch voltage no longer changes. In the above calculation example, it is assumed that the correct touch voltage is 35 V. For convenience, it is also assumed that R
(35)’ » R | (35)’ » R | touch voltage no longer changes. In the above calculation example, it is assumed that the correct touch voltage is 35 V. For convenience, it is also assumed that R m
m | m | longer changes. In the above calculation example, it is assumed that the correct touch voltage is 35 V. For convenience, it is also assumed that R m (35)’ » R
(34)’ | (34)’ | changes. In the above calculation example, it is assumed that the correct touch voltage is 35 V. For convenience, it is also assumed that R m (35)’ » R m
. Nu kan de stroom door het lichaam van de mens berekend worden: | . Now the current through the human body can be calculated: | In the above calculation example, it is assumed that the correct touch voltage is 35 V. For convenience, it is also assumed that R m (35)’ » R m (34)’
[ | [ | touch voltage is 35 V. For convenience, it is also assumed that R m (35)’ » R m (34)’ . Now the current through the human body can be calculated:
5.17 | 5.17 | voltage is 35 V. For convenience, it is also assumed that R m (35)’ » R m (34)’ . Now the current through the human body can be calculated: [
] | ] | is 35 V. For convenience, it is also assumed that R m (35)’ » R m (34)’ . Now the current through the human body can be calculated: [ 5.17
Deze stroomwaarde kan worden opgezocht in de stroom-tijd gevarencurves van figuur 5.14. Hieruit volgt bij toepassing van de C1-curve dat deze stroom ongeveer binnen 1400 ms moet worden afgeschakeld. | This current value can be looked up in the current-time hazard curves of figure 5.14. From this, it follows that using the C1 curve, this current must be switched off within approximately 1400 ms. | 35 V. For convenience, it is also assumed that R m (35)’ » R m (34)’ . Now the current through the human body can be calculated: [ 5.17 ]
Hoe snel bij een fout in het LS-net de kortsluiting daadwerkelijk wordt afgeschakeld, hangt af van het kortsluitvermogen, het type van de kabel, de afstand van de foutplaats tot de bron en de toegepaste beveiliging. Een fout in de installatie van de aangeslotene wordt altijd selectief afgeschakeld door de smeltveiligheid van de aangeslotene zelf. | How quickly a short circuit is actually disconnected in the low-voltage network in the event of a fault depends on the short-circuit power, the type of cable, the distance from the fault location to the source, and the applied protection. A fault in the installation of the connected party is always selectively disconnected by the fuse of the connected party itself. | be looked up in the current-time hazard curves of figure 5.14. From this, it follows that using the C1 curve, this current must be switched off within approximately 1400 ms.
5.7.3 Kortsluitingen in het MS-net | 5.7.3 Short Circuits in the Medium Voltage Network | fault location to the source, and the applied protection. A fault in the installation of the connected party is always selectively disconnected by the fuse of the connected party itself.
Niet alleen fase-aardsluitingen in het LS-net, maar ook fase-aardsluitingen in het MS-net hebben invloed op de potentiaalverhoging in de installaties van de aangeslotenen. De fase-aardfout kan optreden aan de primaire zijde van de transformator in het netstation of elders in het middenspanningsnet. De fout in het netstation heeft de grootste invloed op de potentiaalverhoging van de beschermingsleiding in het netstation en in het LS-net dat door het netstation gevoed wordt. Dergelijke fouten leiden ertoe dat er een stroom loopt in de aardelektrode waarmee de metalen delen van het netstation zijn verbonden. De grootte van de foutstroom hangt af van de impedantie van de foutstroomketen en de wijze waarop het hoogspanningssysteem is geaard. | Not only phase-to-ground faults in the low voltage (LV) network, but also phase-to-ground faults in the medium voltage (MV) network affect the potential rise in the installations of the connected parties. The phase-to-ground fault can occur on the primary side of the transformer in the substation or elsewhere in the medium voltage network. The fault in the substation has the greatest impact on the potential rise of the protective conductor in the substation and in the LV network fed by the substation. Such faults cause a current to flow in the grounding electrode to which the metallic parts of the substation are connected. The magnitude of the fault current depends on the impedance of the fault current path and the manner in which the high voltage system is grounded. | protection. A fault in the installation of the connected party is always selectively disconnected by the fuse of the connected party itself. 5.7.3 Short Circuits in the Medium Voltage Network
De foutstroom die loopt in de aardingsvoorziening van het netstation veroorzaakt een aanzienlijke verhoging van de potentiaal ten opzichte van aarde, waarbij de hoogte is bepaald door de grootte van de foutstroom en de impedantie van de aardingsvoorziening van het netstation. In een systeem waarbij de nulleiding en beschermingsleiding van het laagspanningsnet zijn verbonden met het aardingssysteem van het netstation, kan de foutstroom als gevolg hebben dat de potentiaal in het laagspanningsnet zodanig verhoogt, dat de isolatie beschadigt of dat de potentiaal van de beschermende leiding en alle verbonden metalen gestellen verhoogt. De grootte en duur van de spanning over de isolatie van het laagspanningsmaterieel in de laagspanningsinstallatie als gevolg van een aardfout in het hoogspanningssysteem zijn vastgelegd in de norm NEN 1010. Indien het voedende MS-net een zwevend sterpunt heeft, wordt toegestaan dat een fase-aardfout enkele uren blijft bestaan. In dat geval mag de fasespanning in het LS-net volgens de norm met maximaal 250 V verhoogd worden. Indien het LS-net wordt gevoed door een met lage impedantie geaard MS-net, wordt een kortsluiting binnen 5 seconden afgeschakeld en mag de fasespanning volgens de norm met maximaal 1200 V verhoogd worden. | The fault current flowing in the grounding system of the substation causes a significant increase in potential relative to the earth, determined by the magnitude of the fault current and the impedance of the substation's grounding system. In a system where the neutral and protective conductors of the low-voltage network are connected to the substation's grounding system, the fault current can result in such an increase in potential in the low-voltage network that it damages the insulation or raises the potential of the protective conductor and all connected metal frames. The magnitude and duration of the voltage across the insulation of the low-voltage equipment in the low-voltage installation due to a ground fault in the high-voltage system are specified in the NEN 1010 standard. If the supplying medium-voltage (MV) network has a floating neutral point, a phase-to-ground fault is allowed to persist for several hours. In that case, the phase voltage in the low-voltage (LV) network may be increased by up to 250 V according to the standard. If the LV network is supplied by a low-impedance grounded MV network, a short circuit must be disconnected within 5 seconds, and the phase voltage may be increased by up to 1200 V according to the standard. | the substation are connected. The magnitude of the fault current depends on the impedance of the fault current path and the manner in which the high voltage system is grounded.
Figuur 5.24 Model van een HS/MS-onderstation met achterliggend MS-net | Figure 5.24 Model of a HV/MV substation with a downstream MV network | a low-impedance grounded MV network, a short circuit must be disconnected within 5 seconds, and the phase voltage may be increased by up to 1200 V according to the standard.
De grootte van de potentiaalverhoging op de beschermingsleidingen is evenredig met de grootte van de stroom door de aardverspreidingsweerstand in het netstation. Daarom is het effect groter indien het netstation gevoed wordt door een geaard MS-net dan indien het door een zwevend MS-net gevoed wordt. De potentiaalverhoging in het LS-net als gevolg van een fase-aardsluiting in een impedantiegeaard MS-net wordt aan de hand van het voorbeeld van figuur 5.24 geïllustreerd. Het MS-net is met behulp van een aardingstransformator met lage impedantie geaard. Het net wordt gevoed door een 50 MVA voedingsbron. De aardingstransformator heeft een reactantie van 7 Ω. Op het net is 200 km kabel van het type 3x95 mm | The magnitude of the potential increase on the protective conductors is proportional to the magnitude of the current through the ground spreading resistance in the substation. Therefore, the effect is greater if the substation is fed by a grounded MV network than if it is fed by an ungrounded MV network. The potential increase in the LV network as a result of a phase-to-ground fault in an impedance-grounded MV network is illustrated using the example in Figure 5.24. The MV network is grounded using a grounding transformer with low impedance. The network is fed by a 50 MVA power source. The grounding transformer has a reactance of 7 Ω. The network includes 200 km of cable of the type 3x95 mm². | 5 seconds, and the phase voltage may be increased by up to 1200 V according to the standard. Figure 5.24 Model of a HV/MV substation with a downstream MV network
2 | 2 | network is fed by a 50 MVA power source. The grounding transformer has a reactance of 7 Ω. The network includes 200 km of cable of the type 3x95 mm².
Cu XLPE 6/10 kV aangesloten, die de capaciteit van alle op het onderstation aangesloten kabels representeert. Een enkele MS-streng van 15 km kabel van het type 3x95 mm | Cu XLPE 6/10 kV connected, which represents the capacity of all cables connected to the substation. A single medium-voltage strand of 15 km of cable of the type 3x95 mm² | is fed by a 50 MVA power source. The grounding transformer has a reactance of 7 Ω. The network includes 200 km of cable of the type 3x95 mm². 2
2 | 2 | Cu XLPE 6/10 kV connected, which represents the capacity of all cables connected to the substation. A single medium-voltage strand of 15 km of cable of the type 3x95 mm²
Cu XLPE 6/10 kV is specifiek gemodelleerd om de potentiaalverhoging als gevolg van de fase-aardsluiting te demonstreren. Aan het einde van deze MS-streng is een netstation gemodelleerd met MS-rail, transformator en LS-rail. Het onderstation heeft een aardingsvoorziening met een weerstand van 0,2 Ω. Het netstation heeft een aardingsvoorziening met een weerstand van 2 Ω. | Cu XLPE 6/10 kV is specifically modeled to demonstrate the potential increase as a result of the phase-to-ground fault. At the end of this medium-voltage strand, a substation is modeled with a medium-voltage busbar, transformer, and low-voltage busbar. The substation has a grounding system with a resistance of 0.2 Ω. The network station has a grounding system with a resistance of 2 Ω. | XLPE 6/10 kV connected, which represents the capacity of all cables connected to the substation. A single medium-voltage strand of 15 km of cable of the type 3x95 mm² 2
Op de MS-rail van het netstation wordt een fase-aardsluiting aangebracht. Als gevolg hiervan gaat in dit voorbeeld een kortsluitstroom lopen met een grootte van 677 A. Deze kortsluitstroom vloeit langs twee wegen terug naar de bron: 576 A vloeit door de afscherming van de kabel en 230 A vloeit door de aarde. Deze situatie is in detail afgebeeld in figuur 5.25. De verdeling van de stroom door de afscherming en de stroom door de aarde wordt bepaald door de kabelimpedanties en de aardverspreidingsweerstanden. Als gevolg van de stroom door de aardverspreidingsweerstand in het netstation ontstaat een potentiaalverhoging op de beschermingsleiding, die gelijk is aan het product van de aardverspreidingsweerstand en de erdoor vloeiende stroom. De potentiaalverhoging is theoretisch gelijk aan: | A phase-to-ground fault is applied to the medium-voltage busbar of the network station. As a result, in this example, a short-circuit current of 677 A flows. This short-circuit current returns to the source via two paths: 576 A flows through the cable shielding and 230 A flows through the ground. This situation is depicted in detail in figure 5.25. The distribution of the current through the shielding and the current through the ground is determined by the cable impedances and the ground spreading resistances. Due to the current through the ground spreading resistance in the network station, a potential rise occurs on the protective conductor, which is equal to the product of the ground spreading resistance and the current flowing through it. The potential rise is theoretically equal to: | busbar, transformer, and low-voltage busbar. The substation has a grounding system with a resistance of 0.2 Ω. The network station has a grounding system with a resistance of 2 Ω.
in het onderstation: | in the substation: | rise occurs on the protective conductor, which is equal to the product of the ground spreading resistance and the current flowing through it. The potential rise is theoretically equal to:
U | U | the protective conductor, which is equal to the product of the ground spreading resistance and the current flowing through it. The potential rise is theoretically equal to: in the substation:
f | f | protective conductor, which is equal to the product of the ground spreading resistance and the current flowing through it. The potential rise is theoretically equal to: in the substation: U
conductor, which is equal to the product of the ground spreading resistance and the current flowing through it. The potential rise is theoretically equal to: in the substation: U f
in het netstation: | in the substation: | of the ground spreading resistance and the current flowing through it. The potential rise is theoretically equal to: in the substation: U f = 0.2 · 230 = 46 V
U | U | spreading resistance and the current flowing through it. The potential rise is theoretically equal to: in the substation: U f = 0.2 · 230 = 46 V in the substation:
f | f | resistance and the current flowing through it. The potential rise is theoretically equal to: in the substation: U f = 0.2 · 230 = 46 V in the substation: U
and the current flowing through it. The potential rise is theoretically equal to: in the substation: U f = 0.2 · 230 = 46 V in the substation: U f
Figuur 5.25 Model van een HS/MS-onderstation met achterliggend MS-net | Figure 5.25 Model of a HV/MV substation with a connected MV network | potential rise is theoretically equal to: in the substation: U f = 0.2 · 230 = 46 V in the substation: U f = 2 · 230 = 460 V.
Deze spanning is aanwezig op alle verbonden beschermingsleidingen in het met het netstation verbonden laagspanningsnet. In de praktijk is een laagspanningsnet op meerdere plaatsen geaard en bevinden zich in het achterliggende LS-net door de toegepaste potentiaalvereffening op meerdere locaties bij aangeslotenen contacten met aarde, de zogenaamde verborgen aardcontacten, die parallel geschakeld zijn met de in het netstation aanwezige aardverspreidingsweerstand | This voltage is present on all connected protective conductors in the low-voltage network linked to the substation. In practice, a low-voltage network is grounded at multiple points, and in the underlying LV network, due to the applied potential equalization, there are contacts with the earth at several locations for connected users, the so-called hidden earth contacts, which are connected in parallel with the earth distribution resistance present in the substation. | 0.2 · 230 = 46 V in the substation: U f = 2 · 230 = 460 V. Figure 5.25 Model of a HV/MV substation with a connected MV network
R | R | are contacts with the earth at several locations for connected users, the so-called hidden earth contacts, which are connected in parallel with the earth distribution resistance present in the substation.
a | a | contacts with the earth at several locations for connected users, the so-called hidden earth contacts, which are connected in parallel with the earth distribution resistance present in the substation. R
. Hierdoor wordt de waarde van de equivalente aardverspreidingsweerstand aan de laagspanningszijde van het netstation verlaagd. Een exacte waarde is niet te geven, zodat de waarde moet worden geschat op basis van het aantal aansluitingen in het achterliggende LS-net. Indien hierdoor bijvoorbeeld de aardverspreidingsweerstand in het LS-net van figuur 5.25 zou halveren, halveert ook de potentiaalverhoging op de beschermingsleiding. Het is dus belangrijk hier rekening mee te houden. | This reduces the value of the equivalent earth distribution resistance on the low-voltage side of the substation. An exact value cannot be provided, so the value must be estimated based on the number of connections in the underlying low-voltage network. If, for example, this causes the earth distribution resistance in the low-voltage network of figure 5.25 to be halved, the potential increase on the protective conductor is also halved. It is therefore important to take this into account. | with the earth at several locations for connected users, the so-called hidden earth contacts, which are connected in parallel with the earth distribution resistance present in the substation. R a
In de norm NEN 1010 is een verband aangegeven tussen de hoogte van de foutspanning op de beschermingsleiding in het LS-net en de duur waarbinnen deze spanning in verband met de aanrakingsveiligheid moet worden afgeschakeld, zie figuur 5.26. In de figuur is af te lezen dat een foutspanning van 460 V binnen 0,25 s moet worden afgeschakeld en dat een foutspanning van 230 V binnen 0,45 s moet worden afgeschakeld. Het is hierom belangrijk om met de verborgen aardelektrodes rekening te houden. | In the NEN 1010 standard, a relationship is indicated between the level of fault voltage on the protective conductor in the low-voltage network and the duration within which this voltage must be disconnected for touch safety, see figure 5.26. The figure shows that a fault voltage of 460 V must be disconnected within 0.25 seconds and that a fault voltage of 230 V must be disconnected within 0.45 seconds. Therefore, it is important to take hidden grounding electrodes into account. | resistance in the low-voltage network of figure 5.25 to be halved, the potential increase on the protective conductor is also halved. It is therefore important to take this into account.
Figuur 5.26 Maximale tijd voor spanning U | Figure 5.26 Maximum time for voltage U | be disconnected within 0.25 seconds and that a fault voltage of 230 V must be disconnected within 0.45 seconds. Therefore, it is important to take hidden grounding electrodes into account.
f | f | a fault voltage of 230 V must be disconnected within 0.45 seconds. Therefore, it is important to take hidden grounding electrodes into account. Figure 5.26 Maximum time for voltage U
als gevolg van een aardfout in het MS-net | as a result of a ground fault in the medium voltage network | fault voltage of 230 V must be disconnected within 0.45 seconds. Therefore, it is important to take hidden grounding electrodes into account. Figure 5.26 Maximum time for voltage U f