## Sheet1
Original Text | Translated Text | Previous Context
Bedrijfsvoering van de MS- en LS-netten | Operation of the MV and LV networks
Hoofdstuk 14 gaat in op de bedrijfsvoering van de distributienetten. Na de beschrijving van de huidige wijze van bedrijfsvoeren, wordt ingegaan op aandachtspunten betreffende spanningshuishouding, decentrale opwekking en netverlies. | Chapter 14 discusses the operation of the distribution networks. After describing the current method of operation, it addresses key points concerning voltage management, decentralized generation, and network losses. | Operation of the MV and LV networks
14 Bedrijfsvoering van de MS- en LS-netten | 14 Operation of the MV and LV networks | LV networks Chapter 14 discusses the operation of the distribution networks. After describing the current method of operation, it addresses key points concerning voltage management, decentralized generation, and network losses.
14.1 Huidige wijze van bedrijfsvoering | 14.1 Current Method of Operation | the distribution networks. After describing the current method of operation, it addresses key points concerning voltage management, decentralized generation, and network losses. 14 Operation of the MV and LV networks
14.2 Systemen en hulpmiddelen | 14.2 Systems and Tools | the current method of operation, it addresses key points concerning voltage management, decentralized generation, and network losses. 14 Operation of the MV and LV networks 14.1 Current Method of Operation
14.2.1 Netschema’s | 14.2.1 Network Schematics | operation, it addresses key points concerning voltage management, decentralized generation, and network losses. 14 Operation of the MV and LV networks 14.1 Current Method of Operation 14.2 Systems and Tools
14.2.2 Systeem voor het registreren en afhandelen van storingen | 14.2.2 System for recording and handling faults | key points concerning voltage management, decentralized generation, and network losses. 14 Operation of the MV and LV networks 14.1 Current Method of Operation 14.2 Systems and Tools 14.2.1 Network Schematics
14.2.3 Distributie Management systeem | 14.2.3 Distribution Management System | and network losses. 14 Operation of the MV and LV networks 14.1 Current Method of Operation 14.2 Systems and Tools 14.2.1 Network Schematics 14.2.2 System for recording and handling faults
14.2.4 Systeem ten behoeve van het koppelen van deelnetten | 14.2.4 System for connecting subnetworks | Operation of the MV and LV networks 14.1 Current Method of Operation 14.2 Systems and Tools 14.2.1 Network Schematics 14.2.2 System for recording and handling faults 14.2.3 Distribution Management System
14.2.5 Systeem voor op afstand uitleesbare storingsverklikkers | 14.2.5 System for remotely readable fault indicators | LV networks 14.1 Current Method of Operation 14.2 Systems and Tools 14.2.1 Network Schematics 14.2.2 System for recording and handling faults 14.2.3 Distribution Management System 14.2.4 System for connecting subnetworks
14.2.6 Foutplaatslokalisatie | 14.2.6 Fault Location | 14.2 Systems and Tools 14.2.1 Network Schematics 14.2.2 System for recording and handling faults 14.2.3 Distribution Management System 14.2.4 System for connecting subnetworks 14.2.5 System for remotely readable fault indicators
14.2.7 Digitale secundaire techniek | 14.2.7 Digital Secondary Technology | Tools 14.2.1 Network Schematics 14.2.2 System for recording and handling faults 14.2.3 Distribution Management System 14.2.4 System for connecting subnetworks 14.2.5 System for remotely readable fault indicators 14.2.6 Fault Location
14.2.8 Power Quality | 14.2.8 Power Quality | 14.2.2 System for recording and handling faults 14.2.3 Distribution Management System 14.2.4 System for connecting subnetworks 14.2.5 System for remotely readable fault indicators 14.2.6 Fault Location 14.2.7 Digital Secondary Technology
14.3 Statische en dynamische gegevens | 14.3 Static and dynamic data | recording and handling faults 14.2.3 Distribution Management System 14.2.4 System for connecting subnetworks 14.2.5 System for remotely readable fault indicators 14.2.6 Fault Location 14.2.7 Digital Secondary Technology 14.2.8 Power Quality
14.3.1 Meetdata | 14.3.1 Measurement Data | Distribution Management System 14.2.4 System for connecting subnetworks 14.2.5 System for remotely readable fault indicators 14.2.6 Fault Location 14.2.7 Digital Secondary Technology 14.2.8 Power Quality 14.3 Static and dynamic data
14.3.2 Netdata | 14.3.2 Network Data | 14.2.4 System for connecting subnetworks 14.2.5 System for remotely readable fault indicators 14.2.6 Fault Location 14.2.7 Digital Secondary Technology 14.2.8 Power Quality 14.3 Static and dynamic data 14.3.1 Measurement Data
14.4 Spanningshuishouding | 14.4 Voltage Management | connecting subnetworks 14.2.5 System for remotely readable fault indicators 14.2.6 Fault Location 14.2.7 Digital Secondary Technology 14.2.8 Power Quality 14.3 Static and dynamic data 14.3.1 Measurement Data 14.3.2 Network Data
14.5 Decentrale opwekking | 14.5 Decentralized Generation | System for remotely readable fault indicators 14.2.6 Fault Location 14.2.7 Digital Secondary Technology 14.2.8 Power Quality 14.3 Static and dynamic data 14.3.1 Measurement Data 14.3.2 Network Data 14.4 Voltage Management
14.6 Netverliezen | 14.6 Network Losses | readable fault indicators 14.2.6 Fault Location 14.2.7 Digital Secondary Technology 14.2.8 Power Quality 14.3 Static and dynamic data 14.3.1 Measurement Data 14.3.2 Network Data 14.4 Voltage Management 14.5 Decentralized Generation
14.7 Regulering | 14.7 Regulation | 14.2.6 Fault Location 14.2.7 Digital Secondary Technology 14.2.8 Power Quality 14.3 Static and dynamic data 14.3.1 Measurement Data 14.3.2 Network Data 14.4 Voltage Management 14.5 Decentralized Generation 14.6 Network Losses
14.8 Ontwikkelingen | 14.8 Developments | Location 14.2.7 Digital Secondary Technology 14.2.8 Power Quality 14.3 Static and dynamic data 14.3.1 Measurement Data 14.3.2 Network Data 14.4 Voltage Management 14.5 Decentralized Generation 14.6 Network Losses 14.7 Regulation
14 Bedrijfsvoering van de MS- en LS-netten | 14 Operation of the Medium Voltage and Low Voltage Networks | Digital Secondary Technology 14.2.8 Power Quality 14.3 Static and dynamic data 14.3.1 Measurement Data 14.3.2 Network Data 14.4 Voltage Management 14.5 Decentralized Generation 14.6 Network Losses 14.7 Regulation 14.8 Developments
Het MS-net is een uitgestrekt systeem dat in alle gevallen de levering van elektriciteit moet garanderen. Zo bevinden zich in het Nederlandse elektriciteitsnet ongeveer 1000 MS-distributienetten en 200000 MS/LS-netstations. In de uitgestrekte MS- en LS-netten is het onvermijdelijk dat componenten door een spontane storing of door invloeden van buitenaf, zoals graafwerkzaamheden, buiten bedrijf raken en dat daardoor de levering onderbroken wordt. In die gevallen wordt de fout gelokaliseerd en wordt de levering zo snel mogelijk door omschakelacties hersteld (enkelvoudige storingsreserve). Ook tijdens het plegen van onderhoud moet het uitgestrekte systeem goed blijven functioneren. De schakeling van het net wordt dan zodanig aangepast dat de werkzaamheden veilig kunnen plaatsvinden en de levering niet wordt onderbroken. De bedrijfsvoerder is bij de netbeheerder de aangewezen persoon of instantie om deze werkzaamheden te coördineren en uit te (laten) voeren. Dankzij de structuur en de flexibiliteit van het MS-net kan hij deze taken uitvoeren. De LS-distributienetten kennen vanwege hun radiale opzet minder flexibiliteit en hebben meestal geen omschakelmogelijkheden. Mede hierom concentreren de werkzaamheden van de bedrijfsvoerder zich meestal in de distributienetten tussen de onderstations (de MS-rail) en de netstations (de LS-zijde van de MS/LS-transformator). | The medium voltage (MV) network is an extensive system that must guarantee the delivery of electricity in all cases. In the Dutch electricity grid, there are approximately 1,000 MV distribution networks and 200,000 MV/low voltage (LV) substations. In the extensive MV and LV networks, it is inevitable that components will go out of service due to spontaneous failures or external influences, such as excavation work, resulting in interrupted delivery. In such cases, the fault is localized, and delivery is restored as quickly as possible through switching actions (single fault reserve). Even during maintenance, the extensive system must continue to function properly. The network configuration is then adjusted so that the work can be carried out safely and delivery is not interrupted. The operator at the network operator is the designated person or entity to coordinate and (have) perform these tasks. Thanks to the structure and flexibility of the MV network, he can carry out these tasks. The LV distribution networks, due to their radial design, have less flexibility and usually lack switching options. For this reason, the operator's activities are mostly concentrated in the distribution networks between the substations (the MV rail) and the substations (the LV side of the MV/LV transformer). | data 14.3.1 Measurement Data 14.3.2 Network Data 14.4 Voltage Management 14.5 Decentralized Generation 14.6 Network Losses 14.7 Regulation 14.8 Developments 14 Operation of the Medium Voltage and Low Voltage Networks
Figuur 14.1 Concentratie van de werkzaamheden van de bedrijfsvoerder | Figure 14.1 Concentration of the operator's activities | options. For this reason, the operator's activities are mostly concentrated in the distribution networks between the substations (the MV rail) and the substations (the LV side of the MV/LV transformer).
De doelstelling van de bedrijfsvoerder is het beheersen van het transport en de distributie van de elektrische energie (het primaire proces) met behulp van de in het net ter beschikking staande bedrijfsmiddelen. Hierbij wordt gestreefd naar de best haalbare borging van de continuïteit en kwaliteit van de energielevering, waarbij rekening gehouden wordt met randvoorwaarden op het gebied van veiligheid, milieu en bedrijfseconomie. Om zijn werk goed uit te kunnen voeren heeft de bedrijfsvoerder de beschikking over actuele informatie omtrent het primaire proces en de bedrijfsmiddelen. Deze informatie wordt via signalering en meting verkregen. Voor het beheersen van het primaire proces zijn een goede beveiliging en diverse bedieningsmogelijkheden noodzakelijk. De beveiliging werkt autonoom, zodat op dat punt geen ingrijpen van de bedrijfsvoerder mogelijk is. De bedieningsmogelijkheden bestaan voornamelijk uit schakelmogelijkheden waarmee de actuele netconfiguratie bepaald wordt en daarnaast spanningsregeling met behulp van regeltransformatoren, spoelen en condensatorbanken. De bedieningsmogelijkheden zijn te onderscheiden in drie niveaus: | The objective of the operator is to manage the transport and distribution of electrical energy (the primary process) using the resources available in the network. The aim is to achieve the best possible assurance of continuity and quality of energy supply, taking into account safety, environmental, and economic constraints. To perform his job effectively, the operator has access to up-to-date information about the primary process and the resources. This information is obtained through signaling and measurement. Effective management of the primary process requires good security and various control options. The security operates autonomously, so no intervention by the operator is possible in that regard. The control options mainly consist of switching capabilities that determine the current network configuration and voltage regulation using regulating transformers, coils, and capacitor banks. The control options can be distinguished into three levels: | are mostly concentrated in the distribution networks between the substations (the MV rail) and the substations (the LV side of the MV/LV transformer). Figure 14.1 Concentration of the operator's activities
verre: bediening vanuit het bedrijfsvoeringscentrum (net-niveau) | remote: control from the operations center (network level) | mainly consist of switching capabilities that determine the current network configuration and voltage regulation using regulating transformers, coils, and capacitor banks. The control options can be distinguished into three levels:
afstand: bediening vanuit een centraal punt (stationsniveau) | remote: control from a central point (station level) | current network configuration and voltage regulation using regulating transformers, coils, and capacitor banks. The control options can be distinguished into three levels: remote: control from the operations center (network level)
lokaal: bediening op of bij de schakelaar (veldniveau). | local: control on or near the switch (field level). | transformers, coils, and capacitor banks. The control options can be distinguished into three levels: remote: control from the operations center (network level) remote: control from a central point (station level)
Kostprijsaspecten hebben in het verleden geleid tot verschillende opzet voor het HS-net en het MS-net. De bedrijfsvoering van de HS-netten maakt gebruik van geavanceerde bedrijfsvoeringsystemen, waardoor het net volledig meetbaar en bestuurbaar is. De belangrijke informatie is daarbij centraal in een bedrijfsvoeringcentrum aanwezig. In de MS-distributienetten is vooralsnog geen sprake geweest van een dergelijke bedrijfsvoering. De reden hiervoor lag in de grote aantallen MS-stations. Bedrijfsvoering betrof hier vooral een storings- en onderhoudscoördinatiedienst die werkte met papieren netkaarten en beslissingen nam op basis van periodieke lokaal opgenomen maximaalstroommetingen uit de stations. Aangezien het belang van een goed functionerend distributienet steeds vaker wordt erkend, vindt ook in deze netten langzamerhand modernisering van de bedrijfsvoeringsystemen plaats. | Cost considerations have historically led to different setups for the high-voltage (HV) network and the medium-voltage (MV) network. The operation of the HV networks utilizes advanced management systems, making the network fully measurable and controllable. The critical information is centrally located in an operations center. In the MV distribution networks, such management has not yet been implemented. The reason for this lies in the large number of MV stations. Operations here mainly involved a fault and maintenance coordination service that worked with paper network maps and made decisions based on periodically locally recorded maximum current measurements from the stations. As the importance of a well-functioning distribution network is increasingly recognized, modernization of the management systems is gradually taking place in these networks as well. | be distinguished into three levels: remote: control from the operations center (network level) remote: control from a central point (station level) local: control on or near the switch (field level).
De vernieuwde aandacht op middenspanningsniveau is een gevolg van de wisselwerking tussen voortschrijdende technologie op het gebied van meettechniek en telecommunicatie en de door de vrije markt gestelde eisen aan informatie over het distributienet en de aangeslotenen. Enerzijds heeft men te maken met technologische ontwikkelingen als: partiële ontladingsdetectie, stationsautomatisering, foutplaatslokalisatie, slimme meters, GSM-storingsverklikkers en fasormeetsysteem. Anderzijds vragen een vrije markt en de regulering om nieuwe oplossingen met betrekking tot de beheersbaarheid en betrouwbaarheid van de distributienetten tegen steeds betere prijs/prestatieverhouding. Daarnaast vindt steeds meer opwekking decentraal in de distributienetten plaats. Hierdoor kunnen de getransporteerde vermogens en de spanningsprofielen in het net sterk wisselen, afhankelijk van de momentane opwekking en verbruik. Juist in de midden- en laagspanningsnetten moeten variaties in de spanning binnen nauwe marges blijven om geen hinder te veroorzaken bij de aangeslotenen en te voldoen aan de eisen gesteld door de DTe. Met de huidige stand van de techniek vindt de spanningsregeling meestal nog in het HS/MS-onderstation plaats. Mede hierdoor is de noodzaak tot metingen en informatie uit de distributienetten nog nooit zo hoog geweest. | The renewed focus on medium voltage levels is a result of the interaction between advancing technology in the fields of measurement techniques and telecommunications, and the demands for information about the distribution network and its users set by the free market. On one hand, there are technological developments such as partial discharge detection, station automation, fault location, smart meters, GSM fault indicators, and phasor measurement systems. On the other hand, the free market and regulation demand new solutions regarding the manageability and reliability of the distribution networks with increasingly better price/performance ratios. Additionally, more and more generation is taking place decentrally within the distribution networks. As a result, the transmitted power and voltage profiles in the network can vary greatly, depending on the momentary generation and consumption. Especially in the medium and low voltage networks, voltage variations must remain within narrow margins to avoid inconvenience to users and to meet the requirements set by the DTe. With the current state of technology, voltage regulation usually still takes place in the HV/MV substation. Consequently, the need for measurements and information from the distribution networks has never been higher. | current measurements from the stations. As the importance of a well-functioning distribution network is increasingly recognized, modernization of the management systems is gradually taking place in these networks as well.
Bovenstaande ontwikkelingen onderstrepen het belang van een goed geoutilleerde bedrijfsvoering van de distributienetten. Tevens strekt een moderne bedrijfsvoering zich verder uit dan alleen het bedrijfsvoeringcentrum als centrale locatie. Zo is het belang van het inventariseren en onderzoeken van spanningsklachten noodzakelijk door het toezicht door de overheid op de kwaliteit van de levering. Hierdoor en door de periodieke stroommetingen komen knelpunten naar voren, die binnen de organisatie van de netbeheerder aan de asset managers worden gerapporteerd. Informatie uit het net is zeker zo relevant voor asset managers en analisten op het kantoor. | The above developments underscore the importance of a well-equipped operation of the distribution networks. Additionally, modern operations extend beyond just the operations center as the central location. For instance, the importance of inventorying and investigating voltage complaints is necessary due to government oversight on the quality of delivery. Consequently, periodic current measurements reveal bottlenecks, which are reported to asset managers within the network operator's organization. Information from the network is equally relevant for asset managers and analysts in the office. | the current state of technology, voltage regulation usually still takes place in the HV/MV substation. Consequently, the need for measurements and information from the distribution networks has never been higher.
14.1 Huidige wijze van bedrijfsvoering | 14.1 Current Mode of Operation | current measurements reveal bottlenecks, which are reported to asset managers within the network operator's organization. Information from the network is equally relevant for asset managers and analysts in the office.
De werkzaamheden van de bedrijfsvoering zijn onder te verdelen in planmatige en door incidenten aangestuurde werkzaamheden. De planmatige werkzaamheden betreffen het opstellen en coördineren van schakelplannen voor het uitvoeren van onderhoudswerkzaamheden en het bewaken van de kwaliteit van de levering. De door incidenten aangestuurde werkzaamheden betreffen het afhandelen van storingen in het net. | The operations can be divided into planned activities and incident-driven activities. The planned activities involve drafting and coordinating switching plans for performing maintenance work and monitoring the quality of supply. The incident-driven activities involve handling network failures. | are reported to asset managers within the network operator's organization. Information from the network is equally relevant for asset managers and analysts in the office. 14.1 Current Mode of Operation
Het planmatige werk omvat: | The planned work includes: | activities and incident-driven activities. The planned activities involve drafting and coordinating switching plans for performing maintenance work and monitoring the quality of supply. The incident-driven activities involve handling network failures.
voorbereiden van schakelhandelingen met schakelplannen | preparing switching operations with switching plans | The planned activities involve drafting and coordinating switching plans for performing maintenance work and monitoring the quality of supply. The incident-driven activities involve handling network failures. The planned work includes:
coördineren van de schakelhandelingen tijdens de uitvoering | coordinating switching operations during execution | coordinating switching plans for performing maintenance work and monitoring the quality of supply. The incident-driven activities involve handling network failures. The planned work includes: preparing switching operations with switching plans
bijhouden van alle schakelstanden in het net | keeping track of all switch positions in the network | maintenance work and monitoring the quality of supply. The incident-driven activities involve handling network failures. The planned work includes: preparing switching operations with switching plans coordinating switching operations during execution
verwerken van wijzigingen in de schakelschema's | processing changes in the switching plans | incident-driven activities involve handling network failures. The planned work includes: preparing switching operations with switching plans coordinating switching operations during execution keeping track of all switch positions in the network
verzorgen van periodieke stroommetingen in MS-kabels en bij nettransformatoren | conducting periodic current measurements in medium-voltage cables and at network transformers | The planned work includes: preparing switching operations with switching plans coordinating switching operations during execution keeping track of all switch positions in the network processing changes in the switching plans
inventariseren en onderzoeken van spanningsklachten | inventory and investigation of voltage complaints | switching operations during execution keeping track of all switch positions in the network processing changes in the switching plans conducting periodic current measurements in medium-voltage cables and at network transformers
rapporteren van knelpunten. | reporting bottlenecks. | of all switch positions in the network processing changes in the switching plans conducting periodic current measurements in medium-voltage cables and at network transformers inventory and investigation of voltage complaints
Omschakelingen zijn nodig om onderhoud, aanpassingen en vernieuwingen te plegen in het net. Bij geplande werkzaamheden in het MS-net wordt vooraf omgeschakeld. Hierbij worden schakelplannen gebruikt. Het belangrijkste hulpmiddel bij het opstellen van de schakelplannen is een actueel netschema van het HS/MS-onderstation en de afgaande richtingen met MS-ruimten. Deze schema's zijn meestal als papieren tekeningen beschikbaar. Met deze schema's en de actuele situatie wordt via vuistregels bepaald of en hoe schakelacties kunnen plaatsvinden. De bedrijfsvoerder bepaalt via welke weg de stroomomleiding geschiedt met aandacht voor de continuïteit en kwaliteit van de levering. Tevens registreert hij de nieuwe afwijkende schakelstanden. Er zijn dagelijks vele wijzigingen in het MS-distributienet, bijvoorbeeld voor het inpassen van nieuwe MS/LS-netstations. De bedrijfsvoerder verwerkt deze wijzigingen op de netschema's. Bij verdere automatisering van de bedrijfsvoering van de MS- en LS-netten zullen de papieren schema's vervangen worden door een digitale variant waarmee met behulp van software het distributienet eenvoudig doorgerekend kan worden. Het doorrekenen van de schakelplannen wordt steeds belangrijker. Dit kan in omvangrijke netten en in netten met veel decentrale opwekking niet meer uit het hoofd gedaan worden. | Switching is necessary to perform maintenance, adjustments, and upgrades in the network. For planned work in the medium-voltage (MV) network, switching is done in advance. Switching plans are used for this purpose. The most important tool in creating switching plans is a current network diagram of the high-voltage/medium-voltage (HV/MV) substation and the outgoing directions with MV rooms. These diagrams are usually available as paper drawings. Using these diagrams and the current situation, rules of thumb determine if and how switching actions can take place. The operator determines the path for the power rerouting, paying attention to the continuity and quality of the supply. He also records the new, deviating switch positions. There are daily changes in the MV distribution network, for example, to integrate new MV/low-voltage (LV) substations. The operator processes these changes on the network diagrams. With further automation of the operation of the MV and LV networks, the paper diagrams will be replaced by a digital version, allowing the distribution network to be easily calculated using software. Calculating the switching plans is becoming increasingly important. In large networks and networks with a lot of decentralized generation, this can no longer be done from memory. | switch positions in the network processing changes in the switching plans conducting periodic current measurements in medium-voltage cables and at network transformers inventory and investigation of voltage complaints reporting bottlenecks.
Het door incidenten gestuurde werk omvat: | The incident-driven work includes: | calculated using software. Calculating the switching plans is becoming increasingly important. In large networks and networks with a lot of decentralized generation, this can no longer be done from memory.
analyseren van storingsmeldingen en bepalen van de foutplaats | analyzing fault reports and determining the fault location | the switching plans is becoming increasingly important. In large networks and networks with a lot of decentralized generation, this can no longer be done from memory. The incident-driven work includes:
coördineren van schakelhandelingen die noodzakelijk zijn voor het herstel van de levering | coordinating switching operations necessary for the restoration of supply | large networks and networks with a lot of decentralized generation, this can no longer be done from memory. The incident-driven work includes: analyzing fault reports and determining the fault location
rapporteren over de omvang van de storing en het herstel van de levering | reporting on the extent of the outage and the restoration of supply | generation, this can no longer be done from memory. The incident-driven work includes: analyzing fault reports and determining the fault location coordinating switching operations necessary for the restoration of supply
bepalen van de urgentie van handelen (zoals reparatie). | determining the urgency of action (such as repair). | includes: analyzing fault reports and determining the fault location coordinating switching operations necessary for the restoration of supply reporting on the extent of the outage and the restoration of supply
Storingen zijn aan de orde van de dag. Op jaarbasis waren er in 2009 in Nederland 2221 storingen in de MS-netten en 16056 storingen in de LS-netten (Kema, 2010). Storingsafhandeling is dan ook een belangrijke taak van de bedrijfsvoering. Een storingsproces verloopt als volgt: | Outages are a daily occurrence. Annually, there were 2,221 outages in the medium voltage networks and 16,056 outages in the low voltage networks in the Netherlands in 2009 (Kema, 2010). Handling outages is therefore an important task in operations management. The outage process proceeds as follows: | location coordinating switching operations necessary for the restoration of supply reporting on the extent of the outage and the restoration of supply determining the urgency of action (such as repair).
Een klant belt met de storingsmeldpost om melding te maken van een storing. De meldpost doet de intake en voert de melding in het storingsregistratiesysteem in. De melding wordt nu zichtbaar bij de storingscoördinatie en bedrijfsvoering. | A customer calls the outage reporting center to report an outage. The reporting center handles the intake and enters the report into the outage registration system. The report is now visible to the outage coordination and operations management. | 16,056 outages in the low voltage networks in the Netherlands in 2009 (Kema, 2010). Handling outages is therefore an important task in operations management. The outage process proceeds as follows:
Het kan ook zijn dat bedrijfsvoering de storing al heeft opgemerkt via een melding uit het net of een onderstation. Vervolgens zal de bedrijfsvoerder de storingsaanpak coördineren en een monteur aan de storing toewijzen. Op basis van de door bedrijfsvoering verstrekte gegevens gaat de monteur op zoek naar het gestoorde deel en schakelt dit vrij. Daarna wordt de levering in de overige netdelen via omschakeling en wederinschakeling hersteld. De hiervoor benodigde handelingen kunnen vrijwel uitsluitend ter plaatse worden verricht, met uitzondering van die netgedeelten die zijn voorzien van verrebediening. Door al deze aspecten is de gemiddelde duur van een MS-storing ongeveer 1,5 uur. | It is also possible that operations management has already noticed the outage through a notification from the grid or a substation. Subsequently, the operations manager will coordinate the outage response and assign a technician to the issue. Based on the information provided by operations management, the technician will locate the affected section and isolate it. Then, the supply to the other parts of the grid will be restored through switching and re-energizing. The necessary actions for this can almost exclusively be performed on-site, except for those grid sections equipped with remote control. Due to all these aspects, the average duration of a medium voltage (MV) outage is approximately 1.5 hours. | report an outage. The reporting center handles the intake and enters the report into the outage registration system. The report is now visible to the outage coordination and operations management.
De rijtijden voor een monteur naar en tussen de netstations maken in toenemende mate een onevenredig deel uit van de hersteltijd na een storing en vormen een knelpunt in het herstel van de levering. Ook wordt de betrouwbaarheid van storingsverklikkers soms onvoldoende geacht. In die gevallen worden aanvullende isolatiecontroles uitgevoerd, die extra tijd kosten. Hulpmiddelen om het lokaliseren en afhandelen van storingen sneller en efficiënter te laten verlopen worden systematisch ingevoerd. De bedrijfsvoerder wil bij een storing snel inzicht hebben in onder andere de omvang van de storing en het aantal getroffen klanten per netstation. Dit inzicht kan worden verschaft met behulp van informatiebronnen als software voor het automatisch lokaliseren van de foutplaats en hulp bij herstel van het net, telefoontjes van klanten, GSM storingsverklikkers en intelligente meters. Herstel van de levering kan dan in de juiste volgorde plaatsvinden. | The travel times for a technician to and between substations increasingly constitute a disproportionate part of the recovery time after an outage and pose a bottleneck in the restoration of service. Additionally, the reliability of fault indicators is sometimes deemed insufficient. In such cases, additional insulation checks are performed, which take extra time. Tools to make the localization and handling of faults faster and more efficient are being systematically introduced. During an outage, the operator wants to quickly gain insight into, among other things, the extent of the outage and the number of affected customers per substation. This insight can be provided through information sources such as software for automatically locating the fault site and assisting in network recovery, customer phone calls, GSM fault indicators, and smart meters. Restoration of service can then take place in the correct order. | be performed on-site, except for those grid sections equipped with remote control. Due to all these aspects, the average duration of a medium voltage (MV) outage is approximately 1.5 hours.
14.2 Systemen en hulpmiddelen | 14.2 Systems and tools | automatically locating the fault site and assisting in network recovery, customer phone calls, GSM fault indicators, and smart meters. Restoration of service can then take place in the correct order.
De bedrijfsvoering wordt ondersteund door diverse hulpmiddelen en systemen, die elk zijn afgestemd op het type werkzaamheden. Met de toenemende complexiteit van de structuur van het MS-net en met het toenemend wisselende gedrag van de aangeslotenen, worden, mede vanwege de economische belangen, de voorheen handmatige processen voor probleemanalyse en herstel nu met behulp van software en visualisatietechnieken vervangen. Deze paragraaf geeft een aantal voorbeelden. | The operations are supported by various tools and systems, each tailored to the type of work. With the increasing complexity of the MS network structure and the increasingly variable behavior of the connected users, the previously manual processes for problem analysis and recovery are now being replaced by software and visualization techniques, partly due to economic interests. This paragraph provides several examples. | site and assisting in network recovery, customer phone calls, GSM fault indicators, and smart meters. Restoration of service can then take place in the correct order. 14.2 Systems and tools
14.2.1 Netschema's | 14.2.1 Netschemas | connected users, the previously manual processes for problem analysis and recovery are now being replaced by software and visualization techniques, partly due to economic interests. This paragraph provides several examples.
De netschema's zijn nog vaak uitgevoerd als papieren wandkaarten. Bij sommige netbeheerders zeggen de plaatsen van de knooppunten op de kaarten weinig tot niets over de geografische ligging ten opzichte van elkaar. Daarmee hebben die netschema's geen of weinig geografische betekenis, zoals afgebeeld in figuur 14.2. De afgaande richtingen staan in een volgorde die wordt bepaald door zoveel mogelijk zonder kruisingen te tekenen. | The network diagrams are still often created as paper wall charts. For some network operators, the positions of the nodes on the maps say little to nothing about their geographical location relative to each other. As a result, these network diagrams have little to no geographical significance, as shown in figure 14.2. The outgoing directions are arranged in an order that is determined by drawing with as few crossings as possible. | the previously manual processes for problem analysis and recovery are now being replaced by software and visualization techniques, partly due to economic interests. This paragraph provides several examples. 14.2.1 Netschemas
Figuur 14.2 Netschema zonder geografische koppeling | Figure 14.2 Network diagram without geographical linkage | have little to no geographical significance, as shown in figure 14.2. The outgoing directions are arranged in an order that is determined by drawing with as few crossings as possible.
Bij andere netbeheerders gebruikt men kaarten waarop de geografische ligging van de afgaande richtingen met de netstations wel is gevisualiseerd. In het net van figuur 14.3 is een onderstation getekend als een sterpunt van waaruit de verbindingen radiaal afgaand vertrekken. Ook in deze vorm komen zo weinig mogelijk kruisingen voor. Omdat deze vorm van representeren enigszins gelijkenis vertoont met de werkelijke situatie, wordt dit een zwak geografische koppeling genoemd. | Other network operators use maps that visualize the geographical location of the outgoing directions with the network stations. In the network of figure 14.3, a substation is drawn as a star point from which the connections radiate outward. Even in this form, as few crossings as possible occur. Because this form of representation somewhat resembles the actual situation, it is called a weak geographical linkage. | shown in figure 14.2. The outgoing directions are arranged in an order that is determined by drawing with as few crossings as possible. Figure 14.2 Network diagram without geographical linkage
Figuur 14.3 Netschema met zwak geografische koppeling | Figure 14.3 Network diagram with weak geographical linkage | connections radiate outward. Even in this form, as few crossings as possible occur. Because this form of representation somewhat resembles the actual situation, it is called a weak geographical linkage.
Vanaf het ontstaan van de MS-distributie zijn deze netkaarten, als wandkaarten uitgevoerd, het belangrijkste bedrijfsvoeringmiddel. Op deze kaarten geeft men de netopeningen weer. De afwijkende schakelstanden worden geaccentueerd, bijvoorbeeld met spelden op de papieren kaart. Vaak staan ook kabeltype, doorlaatwaarde, installatietype, beveiligingsinstellingen en storingsverklikkers op het schema. Ook decentrale opwekking moet aangegeven zijn om adequaat te kunnen reageren. | Since the inception of the MV distribution, these network maps, executed as wall maps, have been the primary operational tool. These maps display the network openings. Deviating switch positions are highlighted, for example, with pins on the paper map. Often, the cable type, throughput value, installation type, protection settings, and fault indicators are also shown on the diagram. Decentralized generation must also be indicated to respond adequately. | few crossings as possible occur. Because this form of representation somewhat resembles the actual situation, it is called a weak geographical linkage. Figure 14.3 Network diagram with weak geographical linkage
Deze kaarten worden uit een tekenomgeving gegenereerd en bevatten weinig elektrotechnische informatie. Hierdoor zijn de netten in dit systeem zuiver voor presentatiedoeleinden en kan er niet mee gerekend worden. Indien de netschema's met een programma voor netberekeningen geografisch worden gevisualiseerd en indien de actuele situatie wordt bijgehouden, kunnen er ook berekeningen gedaan worden, zoals voor het analyseren van de schakelplannen en de herstelacties na een storing. Tevens kan het netschema gebruikt worden voor de visualisatie van berekende resultaten zoals van de automatische foutplaatslokalisatie. Ook verschaft het aan bedrijfsvoering meer inzicht over de spanningskwaliteit. | These maps are generated from a drawing environment and contain little electrical engineering information. As a result, the networks in this system are purely for presentation purposes and cannot be used for calculations. If the network diagrams are geographically visualized with a network calculation program and the current situation is monitored, calculations can also be performed, such as analyzing switching plans and recovery actions after a fault. Additionally, the network diagram can be used to visualize calculated results, such as automatic fault location. It also provides operations with more insight into voltage quality. | paper map. Often, the cable type, throughput value, installation type, protection settings, and fault indicators are also shown on the diagram. Decentralized generation must also be indicated to respond adequately.
Vooral bij het juist inschatten van de consequenties van schakelplannen zijn netberekeningen van belang bij de bedrijfsvoering. Bedrijfsvoerders zijn vaak geïnteresseerd in what-if scenario's. Voorbeelden zijn het berekenen van de vereffeningstroom bij het sluiten van netopeningen en de toename van de kabelbelasting bij het verleggen van een netopening. Een stap verder is het toepassen van pseudo state estimation ( | Especially in accurately assessing the consequences of switching plans, network calculations are important in operations management. Operators are often interested in what-if scenarios. Examples include calculating the equalization current when closing network openings and the increase in cable load when relocating a network opening. A step further is the application of pseudo state estimation. | actions after a fault. Additionally, the network diagram can be used to visualize calculated results, such as automatic fault location. It also provides operations with more insight into voltage quality.
paragraaf 9.7 | paragraph 9.7 | include calculating the equalization current when closing network openings and the increase in cable load when relocating a network opening. A step further is the application of pseudo state estimation.
), waarmee het mogelijk is om op ieder moment stromen en spanningen in het net te berekenen op basis van profielen en bedrijfsmetingen. | ), which makes it possible to calculate currents and voltages in the network at any time based on profiles and operational measurements. | the equalization current when closing network openings and the increase in cable load when relocating a network opening. A step further is the application of pseudo state estimation. paragraph 9.7
14.2.2 Systeem voor het registreren en afhandelen van storingen | 14.2.2 System for Recording and Handling Faults | the application of pseudo state estimation. paragraph 9.7 ), which makes it possible to calculate currents and voltages in the network at any time based on profiles and operational measurements.
Elke netbeheerder heeft een databasesysteem dat wordt gebruikt om het afhandelingproces van storingen te faciliteren. In dit systeem worden de omvang en de voortgang van het herstel van een storing vastgelegd. De gegevens van de gestoorde componenten en netdelen worden vastgelegd en bij bijzondere storingen, qua omvang en aard, kan een incidentenanalyse worden uitgevoerd. Ook worden het tijdstip, de duur van de onderbreking van de levering en het aantal getroffen klanten vastgelegd. Hiermee kan worden vastgesteld welke klanten voor een compensatieregeling in aanmerking komen. Daarnaast kan het systeem gebruikt worden om schakelplannen in op te stellen. | Each network operator has a database system that is used to facilitate the fault handling process. In this system, the extent and progress of the fault recovery are recorded. The data of the faulty components and network sections are documented, and for special faults, in terms of size and nature, an incident analysis can be conducted. The time, duration of the supply interruption, and the number of affected customers are also recorded. This allows for the determination of which customers are eligible for a compensation scheme. Additionally, the system can be used to create switching plans. | 9.7 ), which makes it possible to calculate currents and voltages in the network at any time based on profiles and operational measurements. 14.2.2 System for Recording and Handling Faults
Het systeem kan gekoppeld worden met andere systemen. Zo kan de informatie gebruikt worden om het getroffen (postcode) gebied geografisch te visualiseren. Hiermee wordt veelal een goed beeld van de storing en de directe gevolgen verkregen. Tevens kan informatie zodanig worden voorbereid dat informatie met betrekking tot een storing in een standaard rapportvorm beschikbaar komt. | The system can be integrated with other systems. This allows the information to be used to geographically visualize the affected (postal code) area. This often provides a clear picture of the outage and its immediate consequences. Additionally, information can be prepared in such a way that details regarding an outage are available in a standard report format. | of affected customers are also recorded. This allows for the determination of which customers are eligible for a compensation scheme. Additionally, the system can be used to create switching plans.
14.2.3 Distributie Management systeem | 14.2.3 Distribution Management System | clear picture of the outage and its immediate consequences. Additionally, information can be prepared in such a way that details regarding an outage are available in a standard report format.
Het Distributie Management systeem (DMS) verzamelt de bedrijfsmetingen uit de stations in één centraal systeem en visualiseert deze op de bedienschermen van bedrijfsvoering. Ook de actuele schakeltoestand en alarmen in het distributienet kunnen met dit systeem worden bijgehouden. De wandkaarten met de netschema's worden op termijn vervangen door op grote beeldschermen gepresenteerde netschema's met een geografische ondergrond. Daarnaast kan het DMS gebruikt worden om schakelhandelingen in de MS-installaties te verrichten voor zover deze installaties met verrebediening zijn uitgerust. Een DMS zal naar verwachting op termijn bij elke netbeheerder worden ingevoerd. | The Distribution Management System (DMS) collects operational measurements from the stations into one central system and visualizes them on the control screens of operations management. The current switching status and alarms in the distribution network can also be monitored with this system. The wall maps with network diagrams will eventually be replaced by network diagrams presented on large screens with a geographical background. Additionally, the DMS can be used to perform switching operations in the medium-voltage installations, provided these installations are equipped with remote control. A DMS is expected to be implemented by every network operator in the long term. | outage and its immediate consequences. Additionally, information can be prepared in such a way that details regarding an outage are available in a standard report format. 14.2.3 Distribution Management System
Niet alleen bedrijfsmetingen kunnen aan het DMS gekoppeld worden, maar ook technische gegevens van het distributienet kan men in het DMS invoeren en bijhouden. Door koppeling met andere systemen kunnen diverse netwerkapplicaties, zoals state-estimator, loadflowberekeningen en contingency analyses geïntegreerd worden. | Not only can operational measurements be linked to the DMS, but technical data of the distribution network can also be entered and maintained in the DMS. By integrating with other systems, various network applications, such as state estimators, load flow calculations, and contingency analyses, can be incorporated. | perform switching operations in the medium-voltage installations, provided these installations are equipped with remote control. A DMS is expected to be implemented by every network operator in the long term.
De belastingen in het distributienet kunnen door de bedrijfsvoerder bewaakt worden. De on-line metingen en de verzamelde periodieke metingen uit de netstations worden in het DMS vastgelegd. Aan de hand van deze gegevens kan bedrijfsvoering zien of de belasting in het net toeneemt en kan zij beoordelen of deze toename veroorzaakt wordt door een groei of door een omschakeling in het net. Hiermee kunnen knelpunten worden gesignaleerd en verbetervoorstellen worden ingediend. | The loads in the distribution network can be monitored by the operator. The online measurements and the collected periodic measurements from the substations are recorded in the DMS. Based on this data, the operations team can see if the load in the network is increasing and can assess whether this increase is caused by growth or by a switching in the network. This allows bottlenecks to be identified and improvement proposals to be submitted. | can also be entered and maintained in the DMS. By integrating with other systems, various network applications, such as state estimators, load flow calculations, and contingency analyses, can be incorporated.
Beschikbare gegevens in een DMS hebben betrekking op de velden van onderstations (MS-zijde), regelstations en schakelstations. Voorbeelden zijn: | Available data in a DMS pertains to the fields of substations (MV side), control stations, and switching stations. Examples include: | increasing and can assess whether this increase is caused by growth or by a switching in the network. This allows bottlenecks to be identified and improvement proposals to be submitted.
metingen van de voedende en afgaande MS-velden: | measurements of the incoming and outgoing MV fields: | bottlenecks to be identified and improvement proposals to be submitted. Available data in a DMS pertains to the fields of substations (MV side), control stations, and switching stations. Examples include:
stroommetingen | stroommetingen | be submitted. Available data in a DMS pertains to the fields of substations (MV side), control stations, and switching stations. Examples include: measurements of the incoming and outgoing MV fields:
vermogensmetingen voor voedende transformatoren, regeltransformatoren en velden met decentrale opwekking | power measurements for feeding transformers, regulating transformers, and fields with decentralized generation | submitted. Available data in a DMS pertains to the fields of substations (MV side), control stations, and switching stations. Examples include: measurements of the incoming and outgoing MV fields: stroommetingen
schakelstanden van alle velden | switch positions of all fields | (MV side), control stations, and switching stations. Examples include: measurements of the incoming and outgoing MV fields: stroommetingen power measurements for feeding transformers, regulating transformers, and fields with decentralized generation
alarmen die betrekking hebben op alle velden | alarms related to all fields | switching stations. Examples include: measurements of the incoming and outgoing MV fields: stroommetingen power measurements for feeding transformers, regulating transformers, and fields with decentralized generation switch positions of all fields
bediening van alle velden | operation of all fields | of the incoming and outgoing MV fields: stroommetingen power measurements for feeding transformers, regulating transformers, and fields with decentralized generation switch positions of all fields alarms related to all fields
toestand van verre uitleesbare storingsverklikkers in MS-ruimten. | status of remotely readable fault indicators in MV rooms. | outgoing MV fields: stroommetingen power measurements for feeding transformers, regulating transformers, and fields with decentralized generation switch positions of all fields alarms related to all fields operation of all fields
14.2.4 Systeem ten behoeve van het koppelen van deelnetten | 14.2.4 System for the coupling of subnetworks | regulating transformers, and fields with decentralized generation switch positions of all fields alarms related to all fields operation of all fields status of remotely readable fault indicators in MV rooms.
Bij de bedrijfsvoering van radiaal bedreven ringnetten komt het regelmatig voor dat ten behoeve van onderhouds- of uitbreidingswerkzaamheden in het MS-net moet worden omgeschakeld. Een onderdeel van het omschakelen is eerst tijdelijk een netopening te sluiten, waardoor twee MS-strengen worden gekoppeld. Dit waarborgt de continuïteit van de levering tijdens het schakelen. Het kan voorkomen dat hierdoor twee deelnetten moeten worden gekoppeld die vanuit verschillende onderstations worden gevoed. Op de plaats waar de netopening wordt gesloten, kan een spanningsverschil aanwezig zijn dat veroorzaakt wordt door een verschil in absolute waarden of door het faseverschil van de spanningen. Dit spanningsverschil kan dermate groot zijn dat tijdens het koppelen een grote vereffeningstroom gaat vloeien. De grootte van deze stroom wordt bepaald door het spanningsverschil over de te sluiten schakelaar en de kortsluitimpedantie van het net. Deze vereffeningstromen kunnen in combinatie met een zekere voorbelasting zo hoog zijn dat (delen van) netten door de beveiliging worden afgeschakeld, hetgeen onaanvaardbaar is. | In the operation of radially operated ring networks, it is common for switching to be required in the MV network for maintenance or expansion work. Part of the switching process involves temporarily closing a network opening, thereby coupling two MV sections. This ensures the continuity of supply during the switching. It may occur that two subnetworks need to be coupled, which are fed from different substations. At the point where the network opening is closed, a voltage difference may be present, caused by a difference in absolute values or by the phase difference of the voltages. This voltage difference can be so significant that a large equalizing current flows during the coupling. The magnitude of this current is determined by the voltage difference across the switch to be closed and the short-circuit impedance of the network. These equalizing currents, in combination with a certain pre-load, can be so high that (parts of) networks are disconnected by the protection system, which is unacceptable. | switch positions of all fields alarms related to all fields operation of all fields status of remotely readable fault indicators in MV rooms. 14.2.4 System for the coupling of subnetworks
Figuur 14.4 Schema fasormeetsysteem ten behoeve van het koppelen van deelnetten | Figure 14.4 Phasor measurement system diagram for the coupling of subnetworks | impedance of the network. These equalizing currents, in combination with a certain pre-load, can be so high that (parts of) networks are disconnected by the protection system, which is unacceptable.
Ook moet worden voorkomen dat bij het inschakelen en uitschakelen van lastscheiders een gevaarlijke situatie voor het bedienend personeel ontstaat. Bij het sluiten van de schakelaar op de plek van de netopening beoordeelt de bedrijfsvoerder eerst of dit zonder gevaar kan. Een spanningstester die de verschilspanning over de MS-schakelaar aangeeft (deltatester) ondersteunt hem hierbij. Een alternatief is een systeem dat van de spanningen in de onderstations de grootte en de fase meet (Nuijten, 2006). Figuur 14.4 geeft een schematisch voorbeeld van zo een systeem. | It must also be prevented that a dangerous situation arises for the operating personnel when switching on and off load disconnectors. When closing the switch at the location of the network opening, the operator first assesses whether this can be done safely. A voltage tester that indicates the differential voltage across the medium-voltage switch (delta tester) assists him in this. An alternative is a system that measures the magnitude and phase of the voltages in the substations (Nuijten, 2006). Figure 14.4 provides a schematic example of such a system. | certain pre-load, can be so high that (parts of) networks are disconnected by the protection system, which is unacceptable. Figure 14.4 Phasor measurement system diagram for the coupling of subnetworks
Nadat de netopening ten behoeve van het plegen van onderhoud is gesloten, moet op de onderhoudslocatie eerst een nieuwe netopening worden aangebracht, waarna het betreffende kabelsegment uit bedrijf kan worden genomen. Met de lastscheider mag een stroom tot een maximale gespecificeerde waarde worden onderbroken. De bedrijfsvoerder adviseert hierover. | After the network opening for maintenance purposes has been closed, a new network opening must first be created at the maintenance location, after which the relevant cable segment can be taken out of service. With the load switch, a current up to a maximum specified value may be interrupted. The operator advises on this. | this. An alternative is a system that measures the magnitude and phase of the voltages in the substations (Nuijten, 2006). Figure 14.4 provides a schematic example of such a system.
14.2.5 Systeem voor op afstand uitleesbare storingsverklikkers | 14.2.5 System for remotely readable fault indicators | the relevant cable segment can be taken out of service. With the load switch, a current up to a maximum specified value may be interrupted. The operator advises on this.
In de meeste MS-ruimtes zijn storingsverklikkers opgesteld, die op de fasen van de MS-kabels zijn aangebracht, zoals afgebeeld in figuur 14.5. Dit zijn overstroomverklikkers, die bij overschrijding van een bepaalde vaste stroomsterkte, zoals bijvoorbeeld 450 A op een 240 Al-kabel, een indicatie geven. Er bestaan ook verklikkers die reageren op een plotselinge toename van de stroomsterkte, van bijvoorbeeld 150 A. Nadat een kortsluiting heeft plaatsgevonden, worden bij het storingzoeken de MS-ruimten door personeel geïnspecteerd. Zonder indicatie wordt midden in de streng begonnen. De volgorde hangt af van: | In most MV rooms, fault indicators are installed on the phases of the MV cables, as shown in figure 14.5. These are overcurrent indicators that provide an indication when a certain fixed current strength is exceeded, such as 450 A on a 240 Al cable. There are also indicators that respond to a sudden increase in current strength, for example, 150 A. After a short circuit has occurred, personnel inspect the MV rooms during fault finding. Without an indication, the inspection starts in the middle of the string. The order depends on: | out of service. With the load switch, a current up to a maximum specified value may be interrupted. The operator advises on this. 14.2.5 System for remotely readable fault indicators
locatie waar de medewerker vandaan komt | location where the employee comes from | After a short circuit has occurred, personnel inspect the MV rooms during fault finding. Without an indication, the inspection starts in the middle of the string. The order depends on:
de indicatie ten aanzien van de fout: dichtbij of verder weg. | the indication regarding the fault: nearby or further away. | personnel inspect the MV rooms during fault finding. Without an indication, the inspection starts in the middle of the string. The order depends on: location where the employee comes from
Figuur 14.5 Storingsverklikkers op de aders van MS-kabels | Figure 14.5 Fault indicators on the conductors of MV cables | an indication, the inspection starts in the middle of the string. The order depends on: location where the employee comes from the indication regarding the fault: nearby or further away.
De storing zit in theorie tussen de laatste (vanaf het onderstation gezien) aangesproken storingsverklikker en de eerste niet aangesprokene. Met toenemende decentrale opwekking gaat dit principe echter steeds minder vaak op, doordat ook verder weg gelegen generatoren kunnen bijdragen aan de kortsluitstroom. | The fault is theoretically located between the last activated fault indicator (as seen from the substation) and the first non-activated one. However, with increasing decentralized generation, this principle is becoming less reliable, as generators located further away can also contribute to the short-circuit current. | string. The order depends on: location where the employee comes from the indication regarding the fault: nearby or further away. Figure 14.5 Fault indicators on the conductors of MV cables
Bij een spontane ondergrondse fase-aardfout in een kabel of in een verbindingsmof loopt er soms onvoldoende stroom om de storingsverklikkers aan te laten spreken. Dit is met name in MS-netten met zwevend sterpunt het geval. Een gestoorde kabelsectie moet dan opgespoord worden met behulp van een apparaat dat een hoge proefspanning op de kabel zet om te controleren of de isolatie van die sectie wel of niet in orde is. Dit proces kost aanzienlijk meer tijd dan wanneer de storingsverklikkers de te hoge stroom hadden gedetecteerd. Daarnaast speelt de lokale bekendheid ten aanzien van de ligging van de middenspanningsruimten voor de monteurs een belangrijke rol. | In the event of a spontaneous underground phase-to-ground fault in a cable or a connection joint, sometimes there is insufficient current to trigger the fault indicators. This is particularly the case in medium-voltage networks with an isolated neutral point. A faulty cable section must then be located using a device that applies a high test voltage to the cable to check whether the insulation of that section is intact. This process takes significantly more time than if the fault indicators had detected the excessive current. Additionally, local knowledge regarding the location of the medium-voltage rooms plays an important role for the technicians. | the substation) and the first non-activated one. However, with increasing decentralized generation, this principle is becoming less reliable, as generators located further away can also contribute to the short-circuit current.
Om de hersteltijd van een energieonderbreking te reduceren, worden elektronische storingsverklikkers toegepast die zijn voorzien van een GSM module. Indien als gevolg van een kortsluiting een netdeel is uitgevallen, dan wordt de kortsluitstroom door een of meerdere storingsverklikkers gedetecteerd. Deze informatie wordt vervolgens via het mobiele GSM netwerk naar bedrijfsvoering verstuurd. De storingsmonteur hoeft niet meer alle stations in het gestoorde netdeel te onderzoeken. Bedrijfsvoering kan met deze informatie de storingsmonteur direct naar de juiste locaties sturen, waardoor het herstel van de levering aanzienlijk wordt versneld. Extra voordeel van de GSM-storingsverklikker is dat de informatie actueel is, hetgeen de betrouwbaarheid ten goede komt. Bij de gewone storingsverklikker is dit namelijk niet altijd het geval. | To reduce the recovery time of a power outage, electronic fault indicators equipped with a GSM module are used. If a network segment is down due to a short circuit, the short-circuit current is detected by one or more fault indicators. This information is then sent to operations via the mobile GSM network. The fault technician no longer needs to inspect all stations in the affected network segment. Operations can use this information to direct the fault technician to the correct locations, significantly speeding up the restoration of service. An additional advantage of the GSM fault indicator is that the information is current, which enhances reliability. This is not always the case with regular fault indicators. | significantly more time than if the fault indicators had detected the excessive current. Additionally, local knowledge regarding the location of the medium-voltage rooms plays an important role for the technicians.
14.2.6 Foutplaatslokalisatie | 14.2.6 Fault Location | restoration of service. An additional advantage of the GSM fault indicator is that the information is current, which enhances reliability. This is not always the case with regular fault indicators.
Nadat een kortsluiting heeft plaatsgevonden moet eerst foutplaatslokalisatie worden toegepast om zo snel mogelijk het gestoorde kabelsegment op te sporen, waarna de levering kan worden hersteld. Daarna moet de locatie van de kortsluitplaats in het kabelsegment worden gevonden ten behoeve van de reparatie. | After a short circuit has occurred, fault location must first be applied to quickly locate the disrupted cable segment, after which the supply can be restored. Then, the location of the short circuit within the cable segment must be found for the purpose of repair. | An additional advantage of the GSM fault indicator is that the information is current, which enhances reliability. This is not always the case with regular fault indicators. 14.2.6 Fault Location
Foutplaatslokalisatie ten behoeve van herstel | Fault location for the purpose of repair | the disrupted cable segment, after which the supply can be restored. Then, the location of the short circuit within the cable segment must be found for the purpose of repair.
Zonder automatisering wordt bij een kortsluiting de foutplaats opgespoord door elk netstation in een MS-streng volgens een bepaald schema te inspecteren, hetgeen veel tijd kost. Het gestoorde gebied is in de praktijk binnen 5 tot 10 minuten bekend. Daarna volgt het zoeken naar de gestoorde kabelsectie, hetgeen tijd kost door het aanrijden, de inspectie van de storingsverklikkers en isolatiecontroles. | Without automation, in the event of a short circuit, the fault location is detected by inspecting each substation in an MV string according to a specific schedule, which is very time-consuming. In practice, the affected area is identified within 5 to 10 minutes. After that, locating the faulty cable section follows, which takes time due to travel, inspection of fault indicators, and insulation checks. | supply can be restored. Then, the location of the short circuit within the cable segment must be found for the purpose of repair. Fault location for the purpose of repair
Een hulpmiddel om de hersteltijd van een energieonderbreking in impedantiegeaarde netten te reduceren is de methode van foutplaatslokalisatie, zoals beschreven in paragraaf 10.7. Door de foutplaats te schatten aan de hand van metingen van spanning en stroom in het onderstation en deze te vergelijken met een kortsluitberekening aan het model van het net, kan veel tijd worden bespaard. De meting kan worden uitgevoerd met apparatuur voor stationsautomatisering of met digitale beveiligingsrelais. Hierbij worden spanning en stroom continu gemeten en gedurende korte tijd lokaal bewaard. Indien zich een verstoring heeft voorgedaan, dan worden de opgeslagen metingen doorgestuurd naar een centraal systeem. De foutplaats wordt berekend en weergegeven in het netschema en op een geografische ondergrond. | A tool to reduce the recovery time of a power outage in impedance-grounded networks is the fault location method, as described in paragraph 10.7. By estimating the fault location based on voltage and current measurements in the substation and comparing these with a short-circuit calculation on the network model, a lot of time can be saved. The measurement can be performed with station automation equipment or with digital protection relays. In this process, voltage and current are continuously measured and locally stored for a short period. If a disturbance has occurred, the stored measurements are sent to a central system. The fault location is then calculated and displayed in the network diagram and on a geographical map. | affected area is identified within 5 to 10 minutes. After that, locating the faulty cable section follows, which takes time due to travel, inspection of fault indicators, and insulation checks.
Indien de nauwkeurigheid van model of meting onvoldoende is, dan is de foutplaatslokatie niet duidelijk en worden meerdere kabelsecties aangewezen. Om het storingsafhandelingsproces en de foutplaatslokalisatiesoftware verder te ondersteunen, kunnen overige informatiebronnen als GSM-storingsverklikkers en intelligente meters ingezet worden. | If the accuracy of the model or measurement is insufficient, the fault location is unclear and multiple cable sections are indicated. To further support the fault handling process and fault location software, other information sources such as GSM fault indicators and smart meters can be used. | a disturbance has occurred, the stored measurements are sent to a central system. The fault location is then calculated and displayed in the network diagram and on a geographical map.
Foutplaatslokalisatie ten behoeve van reparatie | Fault location for repair | multiple cable sections are indicated. To further support the fault handling process and fault location software, other information sources such as GSM fault indicators and smart meters can be used.
Een manier om de foutplaats in een kabelsegment te detecteren werkt met behulp van pulsreflectie. Door een pulsvormig signaal op een losgekoppelde kabel aan te brengen kan de afstand eenvoudig berekend worden met behulp van de looptijd tussen verzenden, reflectie op de foutplaats en meting van de terugontvangen puls. Elk kabeltype heeft een eigen specifieke looptijd, variërend van 136 m/μs voor 25 kV Höchstädterkabel tot 168 m/μs voor GPLK- en moderne XLPE-kabels. De oudere generatie XLPE-kabels hebben een looptijd van 150 m/μs. | One way to detect the fault location in a cable segment is by using pulse reflection. By applying a pulse-shaped signal to a disconnected cable, the distance can be easily calculated using the travel time between sending, reflection at the fault location, and measuring the returned pulse. Each cable type has its own specific travel time, ranging from 136 m/μs for 25 kV Höchstädter cable to 168 m/μs for GPLK and modern XLPE cables. The older generation XLPE cables have a travel time of 150 m/μs. | indicated. To further support the fault handling process and fault location software, other information sources such as GSM fault indicators and smart meters can be used. Fault location for repair
14.2.7 Digitale secundaire techniek | 14.2.7 Digital Secondary Technology | ranging from 136 m/μs for 25 kV Höchstädter cable to 168 m/μs for GPLK and modern XLPE cables. The older generation XLPE cables have a travel time of 150 m/μs.
Er bestaan vele nieuwe systemen voor digitale secundaire techniek in de middenspanningsnetten. Een van deze systemen is de SASensor (Riet, 2005). Doelstelling van het concept is het analoge signaal zo snel mogelijk naar een digitaal signaal om te zetten, dat via glasverbindingen naar een centrale verwerkingseenheid wordt getransporteerd. Op deze manier ontstaat een galvanische scheiding tussen het primaire en het secundaire systeem. | There are many new systems for digital secondary technology in medium voltage networks. One of these systems is the SASensor (Riet, 2005). The objective of the concept is to convert the analog signal to a digital signal as quickly as possible, which is then transported via fiber optic connections to a central processing unit. This creates a galvanic isolation between the primary and secondary systems. | for 25 kV Höchstädter cable to 168 m/μs for GPLK and modern XLPE cables. The older generation XLPE cables have a travel time of 150 m/μs. 14.2.7 Digital Secondary Technology
Het systeem bevat een centrale verwerkingseenheid en drie typen interface-modules: één voor de driefasenstroom, één voor de driefasenspanning en één voor het signaleren en sturen. De stroommeetmodule (CIM) wordt aangesloten op de bestaande stroomtransformatoren. De spanningsmeetmodule (VIM) wordt aangesloten op de bestaande spanningstransformator. De ingangen van de CIM en de VIM zijn analoog; de uitgangen zijn digitaal. Met de module voor signaleren en sturen (BIM) wordt de stand van een schakelaar, scheider, aarder of trappenschakelaar uitgelezen en kunnen deze worden bediend. Daarnaast heeft de BIM aansluitingen voor diverse alarmen uit de installatie. De uitgangen van de interface modules zijn via glasvezel verbonden met de centrale verwerkingseenheid (CCU). | The system contains a central processing unit and three types of interface modules: one for three-phase current, one for three-phase voltage, and one for signaling and control. The current measurement module (CIM) is connected to the existing current transformers. The voltage measurement module (VIM) is connected to the existing voltage transformer. The inputs of the CIM and VIM are analog; the outputs are digital. The signaling and control module (BIM) reads the status of a switch, isolator, grounding switch, or tap changer and can control them. Additionally, the BIM has connections for various alarms from the installation. The outputs of the interface modules are connected to the central processing unit (CCU) via fiber optic cables. | digital signal as quickly as possible, which is then transported via fiber optic connections to a central processing unit. This creates a galvanic isolation between the primary and secondary systems.
Doordat met de SASensor stromen en spanningen en tevens signaleringen van het onderstation digitaal en centraal beschikbaar zijn, kunnen alle gewenste functies met software worden uitgevoerd. Dit concept maakt alle meetgegevens uit het systeem toegankelijk voor iedere geautoriseerde medewerker vanuit een willekeurige locatie. | Because currents and voltages, as well as signals from the substation, are digitally and centrally available with the SASensor, all desired functions can be executed with software. This concept makes all measurement data from the system accessible to any authorized employee from any location. | them. Additionally, the BIM has connections for various alarms from the installation. The outputs of the interface modules are connected to the central processing unit (CCU) via fiber optic cables.
14.2.8 Power Quality | 14.2.8 Power Quality | centrally available with the SASensor, all desired functions can be executed with software. This concept makes all measurement data from the system accessible to any authorized employee from any location.
Door nieuwe stationsautomatiseringstechnieken in te voeren, komt het monitoren van de Power Quality op het niveau van de middenspanning binnen handbereik. Een specifieke methode voor classificatie van de spanningskwaliteit is ontwikkeld om over grote aantallen locaties een eenduidig en snel overzicht te geven (Cobben, 2007). Deze methode is beschreven in paragraaf 11.7. De basis voor deze classificatiemethode zijn gemiddelde waarden en standaarddeviaties. De beoordelingsaspecten van de spanningskwaliteit zijn: spannings- en frequentievariatie, dips, flikker, THD en onbalans. | By implementing new station automation techniques, monitoring Power Quality at the medium voltage level becomes within reach. A specific method for classifying voltage quality has been developed to provide a clear and quick overview across a large number of locations (Cobben, 2007). This method is described in paragraph 11.7. The basis for this classification method is average values and standard deviations. The assessment aspects of voltage quality are: voltage and frequency variation, dips, flicker, THD, and imbalance. | the SASensor, all desired functions can be executed with software. This concept makes all measurement data from the system accessible to any authorized employee from any location. 14.2.8 Power Quality
De presentatie van de Power Quality is zodanig opgezet dat men overzichten heeft van globaal naar detail. Figuur 14.6 toont linksboven het overzicht van de spanningskwaliteit over alle aspecten. In een oogopslag is duidelijk welke meetpunten niet voldoen aan de gestelde norm. Het tweede scherm, rechtsboven, geeft specifieke informatie over een gekozen kwaliteitsaspect (de spanning). De onderste twee schermen tonen de gedetailleerde metingen en de 10-minutengemiddelde waarden over een opgevraagde week, voor verdere analyse. Getoond zijn de spanning als functie van de tijd en de harmonische vervuiling per harmonische. | The presentation of Power Quality is designed to provide overviews from general to detailed. Figure 14.6 shows the overview of voltage quality across all aspects in the top left corner. At a glance, it is clear which measurement points do not meet the specified standard. The second screen, in the top right corner, provides specific information about a chosen quality aspect (the voltage). The bottom two screens display the detailed measurements and the 10-minute average values over a requested week for further analysis. Shown are the voltage as a function of time and the harmonic distortion per harmonic. | paragraph 11.7. The basis for this classification method is average values and standard deviations. The assessment aspects of voltage quality are: voltage and frequency variation, dips, flicker, THD, and imbalance.
Figuur 14.6 Presentatie van Power Quality aspecten | Figure 14.6 Presentation of Power Quality aspects | the detailed measurements and the 10-minute average values over a requested week for further analysis. Shown are the voltage as a function of time and the harmonic distortion per harmonic.
14.3 Statische en dynamische gegevens | 14.3 Static and dynamic data | values over a requested week for further analysis. Shown are the voltage as a function of time and the harmonic distortion per harmonic. Figure 14.6 Presentation of Power Quality aspects
Systemen voor het maken van netberekeningen en analyses, zoals genoemd in de vorige paragrafen, moeten gevuld en gevoed worden met gegevens. Onder statische gegevens vallen de structuur van het distributienet en de elektrotechnische eigenschappen van de bedrijfsmiddelen. Onder dynamische gegevens vallen enerzijds de gegevens die de gebruikers invoeren (zoals actuele locaties van de netopeningen, actuele storingen en (tijdelijke) schakelstanden) en anderzijds gegevens die automatisch in deze systemen terechtkomen (zoals bedrijfsmetingen). Het is belangrijk om goed om te gaan met de groeiende hoeveelheid informatie uit diverse systemen. Tegelijkertijd moeten de systemen zodanig zijn ontworpen dat er gemakkelijk mee genavigeerd kan worden, zowel door de software als door het distributiesysteem. | Systems for performing network calculations and analyses, as mentioned in the previous paragraphs, need to be populated and fed with data. Static data includes the structure of the distribution network and the electrical properties of the assets. Dynamic data includes, on the one hand, the data entered by users (such as current locations of network openings, current faults, and (temporary) switch positions) and, on the other hand, data that automatically enters these systems (such as operational measurements). It is important to manage the growing amount of information from various systems effectively. At the same time, the systems must be designed in such a way that they can be easily navigated, both by the software and by the distribution system. | for further analysis. Shown are the voltage as a function of time and the harmonic distortion per harmonic. Figure 14.6 Presentation of Power Quality aspects 14.3 Static and dynamic data
14.3.1 Meetdata | 14.3.1 Measurement Data | systems effectively. At the same time, the systems must be designed in such a way that they can be easily navigated, both by the software and by the distribution system.
Onder meetdata worden de bedrijfsmetingen in de (onder)stations verstaan van de afgaande richtingen, zoals momentane spanning, stroom en vermogen. Deze metingen zijn gekoppeld aan het DMS en zijn dus beschikbaar op het bedrijfsvoeringcentrum. De metingen zijn meestal beschikbaar als 5-minuten gemiddelden. Niet alle MS-stations zijn voorzien van moderne meetsystemen. Dieper in het MS-net zijn middenspanningsruimten met MS/LS-transformatoren voorzien van lokale maximaalstroommetingen, uitleesbaar via sleepwijzers op de installatie. Deze worden hooguit een paar maal per jaar handmatig uitgelezen en ingevoerd in de database. Dit is ook het geval voor onderstations, regelstations en schakelstations waar verremeting ontbreekt. Bij de beveiligingen van subnetten ontbreekt vaak de mogelijkheid om te meten. | Measurement data refers to the operational measurements in the (sub)stations of the outgoing directions, such as instantaneous voltage, current, and power. These measurements are linked to the DMS and are therefore available at the operations center. The measurements are usually available as 5-minute averages. Not all medium-voltage (MV) stations are equipped with modern measurement systems. Deeper in the MV network, medium-voltage spaces with MV/low-voltage (LV) transformers are equipped with local maximum current measurements, readable via drag pointers on the installation. These are read manually at most a few times a year and entered into the database. This is also the case for substations, control stations, and switching stations where remote measurement is lacking. In the protections of subnetworks, the ability to measure is often missing. | the same time, the systems must be designed in such a way that they can be easily navigated, both by the software and by the distribution system. 14.3.1 Measurement Data
Naast de traditionele bedrijfsmetingen van spanningen en stromen komen er steeds meer nieuwe vormen van metingen voorhanden. Zo worden in het SASensor systeem ook Power Quality gegevens gemeten. De metingen moeten op het bedrijfsvoeringcentrum opvraagbaar zijn via zogenaamde weekfiles, die lokaal bewaard worden. Ook zijn op diverse locaties Power Quality meters geïnstalleerd die hun data rechtstreeks doorsturen naar een centrale database op het bedrijfsvoeringcentrum. Een belangrijke ontwikkeling is dat de gegevens niet alleen van belang zijn voor de directe bedrijfsvoering maar ook gebruikt zullen gaan worden door asset managers op kantoor. | In addition to the traditional operational measurements of voltages and currents, more and more new forms of measurements are becoming available. For example, in the SASensor system, Power Quality data is also measured. The measurements must be retrievable at the operations center via so-called week files, which are stored locally. Additionally, Power Quality meters have been installed at various locations that send their data directly to a central database at the operations center. An important development is that the data is not only relevant for direct operations but will also be used by asset managers in the office. | database. This is also the case for substations, control stations, and switching stations where remote measurement is lacking. In the protections of subnetworks, the ability to measure is often missing.
14.3.2 Netdata | 14.3.2 Net Data | database at the operations center. An important development is that the data is not only relevant for direct operations but will also be used by asset managers in the office.
Netdata beschrijven het distributienet, zoals de structuur en de eigenschappen van de bedrijfsmiddelen. Bovendien vallen de schakelstanden hieronder. Belangrijke aspecten bij het verzamelen en opslaan van netdata zijn toegankelijkheid, beschikbaarheid en kwaliteit van de gegevens bij het gebruik ervan in de organisatie. Er moet worden voorkomen dat versnippering van de data optreedt en dat deze gegevens overlappen bij diverse afdelingen en werkplekken binnen de organisatie. Er moet naar worden gestreefd deze gegevens te betrekken van één bron. | Net data describe the distribution network, such as the structure and properties of the assets. Additionally, switch positions are included under this category. Important aspects in collecting and storing net data are accessibility, availability, and quality of the data when used within the organization. It is essential to prevent data fragmentation and overlap across various departments and workplaces within the organization. Efforts should be made to source this data from a single origin. | operations center. An important development is that the data is not only relevant for direct operations but will also be used by asset managers in the office. 14.3.2 Net Data
De noodzaak tot het rekenen aan netten bij de bedrijfsvoering is hoog. De gevolgen van (om)schakelacties voor optredende spanningen en stromen is niet altijd op voorhand duidelijk. De MS-netten zijn complex geworden en bevatten toenemende concentraties decentrale opwekkers waarvan het vermogen en het patroon niet of nauwelijks bekend zijn. | The necessity for calculating networks in operations is high. The consequences of switching actions for occurring voltages and currents are not always clear in advance. The medium-voltage networks have become complex and contain increasing concentrations of decentralized generators whose power and patterns are barely known. | organization. It is essential to prevent data fragmentation and overlap across various departments and workplaces within the organization. Efforts should be made to source this data from a single origin.
14.4 Spanningshuishouding | 14.4 Voltage Management | occurring voltages and currents are not always clear in advance. The medium-voltage networks have become complex and contain increasing concentrations of decentralized generators whose power and patterns are barely known.
Tot het planmatige werk van bedrijfsvoering behoren het verzorgen van periodieke stroommetingen in MS-kabels en bij nettransformatoren, het inventariseren en onderzoeken van spanningsklachten en het rapporteren van knelpunten. Hierbij wordt uitgegaan van de internationale standaard IEC 50160, die de randvoorwaarden specificeert waaraan de spanning in Europese LS-netten tijdens normaal bedrijf moeten voldoen. Meestal is dit uitgebreid met bedrijfseigen voorschriften. De standaard behandelt vele Power Quality aspecten, zoals beschreven in hoofdstuk 11. Ten aanzien van de spanning in LS-netten worden in Europa onderstaande eisen gehanteerd voor de spanning tussen fase en nul: | The planned work of operations management includes conducting periodic current measurements in medium-voltage cables and at network transformers, inventorying and investigating voltage complaints, and reporting bottlenecks. This is based on the international standard IEC 50160, which specifies the conditions that the voltage in European low-voltage networks must meet during normal operation. This is usually supplemented with company-specific regulations. The standard addresses many Power Quality aspects, as described in chapter 11. Regarding the voltage in low-voltage networks, the following requirements are applied in Europe for the voltage between phase and neutral: | currents are not always clear in advance. The medium-voltage networks have become complex and contain increasing concentrations of decentralized generators whose power and patterns are barely known. 14.4 Voltage Management
altijd lager dan 253 V (230+10%) | always lower than 253 V (230+10%) | addresses many Power Quality aspects, as described in chapter 11. Regarding the voltage in low-voltage networks, the following requirements are applied in Europe for the voltage between phase and neutral:
gedurende 95% van de tijd hoger dan 207 V (230-10%) | for 95% of the time higher than 207 V (230-10%) | described in chapter 11. Regarding the voltage in low-voltage networks, the following requirements are applied in Europe for the voltage between phase and neutral: always lower than 253 V (230+10%)
altijd hoger dan 196 V (230-15%) | always higher than 196 V (230-15%) | the following requirements are applied in Europe for the voltage between phase and neutral: always lower than 253 V (230+10%) for 95% of the time higher than 207 V (230-10%)
De mogelijkheid dat de spanning gedurende enige tijd lager dan 207 V kan zijn, is bedoeld voor tijdelijke situaties van onderhoud of storing. | The possibility that the voltage may be lower than 207 V for some time is intended for temporary situations of maintenance or malfunction. | Europe for the voltage between phase and neutral: always lower than 253 V (230+10%) for 95% of the time higher than 207 V (230-10%) always higher than 196 V (230-15%)
Figuur 14.7 Voorbeeld van spanningsvariaties in een radiaal distributienet | Figure 14.7 Example of voltage variations in a radial distribution network | (230-10%) always higher than 196 V (230-15%) The possibility that the voltage may be lower than 207 V for some time is intended for temporary situations of maintenance or malfunction.
De spanningsvariaties in een distributienet zijn afhankelijk van de hoeveelheid getransporteerd vermogen, de componenten in het netwerk, de actuele netconfiguratie en de marge in de HS/MS-transformatorregeling (bijvoorbeeld 10,5 kV +/- 1%). Figuur 14.7 toont een voorbeeld van de spanningsvariaties in een gewoon radiaal distributienet zonder decentrale opwekking, vanaf het onderstation (OS) tot aan een LS-aansluiting. Het onderstation kan ook een regelstation (RS) zijn. | The voltage variations in a distribution network depend on the amount of power transported, the components in the network, the current network configuration, and the margin in the HV/MV transformer regulation (for example, 10.5 kV +/- 1%). Figure 14.7 shows an example of voltage variations in a typical radial distribution network without decentralized generation, from the substation (SS) to an LV connection. The substation can also be a regulation station (RS). | voltage may be lower than 207 V for some time is intended for temporary situations of maintenance or malfunction. Figure 14.7 Example of voltage variations in a radial distribution network
De spanningsvariatie in het HS-net kan aanzienlijk zijn, maar dankzij de spanningsregeling op de HS/MS-voedingstransformator worden deze variaties gecorrigeerd en zijn deze nauwelijks van invloed op de spanning in het MS-distributienet. De spanningsvariatie op de MS-rail van het onderstation wordt bepaald door de spanningsband van de spanningsregeling, die bij 10 kV in veel gevallen 0,2 kV (2%) groot is. Door de impedanties van het MS-net, de MS/LS-transformatoren en het LS-net nemen de spanningsvariaties als gevolg van wisselende belastingen toe. | The voltage variation in the HV network can be significant, but thanks to the voltage regulation on the HV/MV supply transformer, these variations are corrected and have little impact on the voltage in the MV distribution network. The voltage variation on the MV busbar of the substation is determined by the voltage regulation band, which at 10 kV is often 0.2 kV (2%). Due to the impedances of the MV network, the MV/LV transformers, and the LV network, the voltage variations increase as a result of fluctuating loads. | example of voltage variations in a typical radial distribution network without decentralized generation, from the substation (SS) to an LV connection. The substation can also be a regulation station (RS).
Volgens paragraaf 9.1 is de spanningsdaling achter een kabel bij benadering afhankelijk van het getransporteerde vermogen en de impedantie: | According to paragraph 9.1, the voltage drop behind a cable is approximately dependent on the transmitted power and the impedance: | is often 0.2 kV (2%). Due to the impedances of the MV network, the MV/LV transformers, and the LV network, the voltage variations increase as a result of fluctuating loads.
[ | [ | the voltage variations increase as a result of fluctuating loads. According to paragraph 9.1, the voltage drop behind a cable is approximately dependent on the transmitted power and the impedance:
14.1 | 14.1 | voltage variations increase as a result of fluctuating loads. According to paragraph 9.1, the voltage drop behind a cable is approximately dependent on the transmitted power and the impedance: [
] | ] | variations increase as a result of fluctuating loads. According to paragraph 9.1, the voltage drop behind a cable is approximately dependent on the transmitted power and the impedance: [ 14.1
Dit houdt in dat de invloed van het actieve en reactieve vermogen op de spanningsdaling afhangt van de R/X verhouding van de kabel. In hoogspanningsnetten met voornamelijk bovengrondse lijnen is de reactantie meestal veel groter dan de weerstand. Daarom is in transportnetten de spanningsvariatie sterk afhankelijk van het getransporteerde blindvermogen. | This means that the influence of active and reactive power on the voltage drop depends on the R/X ratio of the cable. In high-voltage networks with mainly overhead lines, the reactance is usually much greater than the resistance. Therefore, in transmission networks, the voltage variation is strongly dependent on the transported reactive power. | increase as a result of fluctuating loads. According to paragraph 9.1, the voltage drop behind a cable is approximately dependent on the transmitted power and the impedance: [ 14.1 ]
In laagspanningsnetten daarentegen, is de weerstand veel groter dan de reactantie. Hierdoor is in laagspanningsdistributienetten de spanningsvariatie voornamelijk afhankelijk van het actieve vermogen en veel minder van het blindvermogen. | In low-voltage networks, on the other hand, the resistance is much greater than the reactance. Therefore, in low-voltage distribution networks, the voltage variation is mainly dependent on the active power and much less on the reactive power. | high-voltage networks with mainly overhead lines, the reactance is usually much greater than the resistance. Therefore, in transmission networks, the voltage variation is strongly dependent on the transported reactive power.
In middenspanningsnetten is het moeilijker om één enkele oorzaak voor de spanningsdaling aan te wijzen. In middenspanningstransportnetten worden doorgaans kabels met een grote geleiderdoorsnede (150 mm | In medium-voltage networks, it is more difficult to pinpoint a single cause for the voltage drop. In medium-voltage transmission networks, cables with a large conductor cross-section (150 mm | the resistance is much greater than the reactance. Therefore, in low-voltage distribution networks, the voltage variation is mainly dependent on the active power and much less on the reactive power.
2 | 2 | reactive power. In medium-voltage networks, it is more difficult to pinpoint a single cause for the voltage drop. In medium-voltage transmission networks, cables with a large conductor cross-section (150 mm
of meer) toegepast, waarvan de R/X verhouding zich tussen 0,5 en 2 bevindt. Hierdoor hebben het actieve vermogen en het blindvermogen beide ongeveer gelijke invloed op de spanningsdaling. Zeer veel toegepaste kabels in MS-distributienetten hebben een geleiderdoorsnede van 240 mm | or more) are used, with an R/X ratio between 0.5 and 2. As a result, both active power and reactive power have approximately equal influence on the voltage drop. Many commonly used cables in medium-voltage distribution networks have a conductor cross-section of 240 mm² or more. | power. In medium-voltage networks, it is more difficult to pinpoint a single cause for the voltage drop. In medium-voltage transmission networks, cables with a large conductor cross-section (150 mm 2
2 | 2 | active power and reactive power have approximately equal influence on the voltage drop. Many commonly used cables in medium-voltage distribution networks have a conductor cross-section of 240 mm² or more.
Al of minder, waarvan de R/X verhouding groter dan 2 is. Hierdoor heeft het actieve vermogen meer invloed op de spanningsdaling dan het blindvermogen. De invloed van het blindvermogen kan echter niet verwaarloosd worden. | More or less, where the R/X ratio is greater than 2. As a result, active power has more influence on the voltage drop than reactive power. However, the influence of reactive power cannot be neglected. | power and reactive power have approximately equal influence on the voltage drop. Many commonly used cables in medium-voltage distribution networks have a conductor cross-section of 240 mm² or more. 2
Tabel 14.1 Invloed van het vermogen op de spanningsval over een kabel en een bovengrondse lijn | Table 14.1 Influence of power on the voltage drop over a cable and an overhead line | R/X ratio is greater than 2. As a result, active power has more influence on the voltage drop than reactive power. However, the influence of reactive power cannot be neglected.
Spanningsniveau | Spanningsniveau | voltage drop than reactive power. However, the influence of reactive power cannot be neglected. Table 14.1 Influence of power on the voltage drop over a cable and an overhead line
Type | Type | drop than reactive power. However, the influence of reactive power cannot be neglected. Table 14.1 Influence of power on the voltage drop over a cable and an overhead line Spanningsniveau
R/X | R/X | than reactive power. However, the influence of reactive power cannot be neglected. Table 14.1 Influence of power on the voltage drop over a cable and an overhead line Spanningsniveau Type
Belangrijkste invloed | Main influence | reactive power. However, the influence of reactive power cannot be neglected. Table 14.1 Influence of power on the voltage drop over a cable and an overhead line Spanningsniveau Type R/X
HS | HS | However, the influence of reactive power cannot be neglected. Table 14.1 Influence of power on the voltage drop over a cable and an overhead line Spanningsniveau Type R/X Main influence
bovengrondse lijn | overhead line | the influence of reactive power cannot be neglected. Table 14.1 Influence of power on the voltage drop over a cable and an overhead line Spanningsniveau Type R/X Main influence HS
< 0,5 | < 0.5 | of reactive power cannot be neglected. Table 14.1 Influence of power on the voltage drop over a cable and an overhead line Spanningsniveau Type R/X Main influence HS overhead line
Q | Q | power cannot be neglected. Table 14.1 Influence of power on the voltage drop over a cable and an overhead line Spanningsniveau Type R/X Main influence HS overhead line < 0.5
MS | MS | cannot be neglected. Table 14.1 Influence of power on the voltage drop over a cable and an overhead line Spanningsniveau Type R/X Main influence HS overhead line < 0.5 Q
kabel > 150 mm | cable > 150 mm | be neglected. Table 14.1 Influence of power on the voltage drop over a cable and an overhead line Spanningsniveau Type R/X Main influence HS overhead line < 0.5 Q MS
2 | 2 | Influence of power on the voltage drop over a cable and an overhead line Spanningsniveau Type R/X Main influence HS overhead line < 0.5 Q MS cable > 150 mm
0,5 ... 2 | 0.5 ... 2 | of power on the voltage drop over a cable and an overhead line Spanningsniveau Type R/X Main influence HS overhead line < 0.5 Q MS cable > 150 mm 2
P en Q | P and Q | the voltage drop over a cable and an overhead line Spanningsniveau Type R/X Main influence HS overhead line < 0.5 Q MS cable > 150 mm 2 0.5 ... 2
MS | MS | over a cable and an overhead line Spanningsniveau Type R/X Main influence HS overhead line < 0.5 Q MS cable > 150 mm 2 0.5 ... 2 P and Q
kabel ≤ 150 mm | cable ≤ 150 mm | a cable and an overhead line Spanningsniveau Type R/X Main influence HS overhead line < 0.5 Q MS cable > 150 mm 2 0.5 ... 2 P and Q MS
2 | 2 | overhead line Spanningsniveau Type R/X Main influence HS overhead line < 0.5 Q MS cable > 150 mm 2 0.5 ... 2 P and Q MS cable ≤ 150 mm
> 2 | > 2 | line Spanningsniveau Type R/X Main influence HS overhead line < 0.5 Q MS cable > 150 mm 2 0.5 ... 2 P and Q MS cable ≤ 150 mm 2
P | P | Type R/X Main influence HS overhead line < 0.5 Q MS cable > 150 mm 2 0.5 ... 2 P and Q MS cable ≤ 150 mm 2 > 2
LS | LS | R/X Main influence HS overhead line < 0.5 Q MS cable > 150 mm 2 0.5 ... 2 P and Q MS cable ≤ 150 mm 2 > 2 P
kabel | kabel | Main influence HS overhead line < 0.5 Q MS cable > 150 mm 2 0.5 ... 2 P and Q MS cable ≤ 150 mm 2 > 2 P LS
> 2 | > 2 | influence HS overhead line < 0.5 Q MS cable > 150 mm 2 0.5 ... 2 P and Q MS cable ≤ 150 mm 2 > 2 P LS kabel
P | P | overhead line < 0.5 Q MS cable > 150 mm 2 0.5 ... 2 P and Q MS cable ≤ 150 mm 2 > 2 P LS kabel > 2
Een voedingstransformator heeft in het algemeen een veel grotere reactantie dan weerstand. Dit heeft tot gevolg dat de spanningsdaling over de transformator voornamelijk beïnvloed wordt door het transport van blindvermogen. | A power transformer generally has a much higher reactance than resistance. As a result, the voltage drop across the transformer is mainly influenced by the transport of reactive power. | line < 0.5 Q MS cable > 150 mm 2 0.5 ... 2 P and Q MS cable ≤ 150 mm 2 > 2 P LS kabel > 2 P
14.5 Decentrale opwekking | 14.5 Decentralized Generation | P A power transformer generally has a much higher reactance than resistance. As a result, the voltage drop across the transformer is mainly influenced by the transport of reactive power.
De definitie van decentrale opwekking is niet altijd even duidelijk. Eenvoudig kan gesteld worden dat decentrale opwekking een zodanige omvang heeft dat ze aangesloten kan worden op het distributienet en dat ze over het algemeen niet centraal wordt aangestuurd. Voorbeelden zijn zonnecentrales en generatoren die worden aangedreven door gasmotoren, diesels, kleine gasturbines, microturbines, kleinschalige waterkracht, brandstofcellen en windturbines. | The definition of decentralized generation is not always clear. Simply put, decentralized generation is of such a size that it can be connected to the distribution network and is generally not centrally controlled. Examples include solar power plants and generators driven by gas engines, diesels, small gas turbines, microturbines, small-scale hydropower, fuel cells, and wind turbines. | transformer generally has a much higher reactance than resistance. As a result, the voltage drop across the transformer is mainly influenced by the transport of reactive power. 14.5 Decentralized Generation
Decentrale opwekking heeft grote invloed op de spanningshuishouding, de verliezen en de werking van de beveiliging in het distributienet. In een distributienet met alleen belasting zal in het algemeen de spanning dalen bij toenemende afstand van de belastingen tot de voeding. Decentrale opwekking in dat net zal de spanningsdaling doen afnemen. In bijzondere situaties kan de spanning zelfs toenemen. De door decentrale opwekking opgewekte elektrische energie wordt direct door de lokaal aanwezige belastingen opgenomen. | Decentralized generation has a significant impact on voltage regulation, losses, and the operation of protection systems in the distribution network. In a distribution network with only loads, the voltage generally decreases with increasing distance from the loads to the power source. Decentralized generation in that network will reduce the voltage drop. In special situations, the voltage can even increase. The electrical energy generated by decentralized generation is directly consumed by the locally present loads. | network and is generally not centrally controlled. Examples include solar power plants and generators driven by gas engines, diesels, small gas turbines, microturbines, small-scale hydropower, fuel cells, and wind turbines.
Als gevolg hiervan is de grootte van de door de voeding te leveren stroom kleiner, waardoor de verliezen in het distributienet kunnen afnemen. Ideaal zou het zijn dat de decentrale opwekking en de belasting met elkaar in balans zijn. In dat geval is er weinig vermogenstransport en dus ook weinig netverlies. Praktijk is echter dat de veel voorkomende vormen van decentrale opwekking, zoals windturbines en tuinder-WKK's, ten gevolge van vergunningsaspecten bij elkaar geconcentreerd staan. Daardoor is er vaak lokaal een fors overschot aan geproduceerd vermogen, hetgeen leidt tot een vermogenstransport, dat weer gepaard gaat met spanningsopdrijving en netverlies. Ten aanzien van tuinder-WKK's zijn er voorbeelden in de grote kassen-projecten en ten aanzien van wind rondom het IJsselmeer. | As a result, the amount of current supplied by the power source is smaller, which can reduce losses in the distribution network. Ideally, decentralized generation and load should be balanced. In that case, there is little power transport and thus minimal network loss. However, in practice, common forms of decentralized generation, such as wind turbines and greenhouse CHP (Combined Heat and Power) systems, are often concentrated together due to permitting aspects. This often results in a significant local surplus of generated power, leading to power transport, which in turn causes voltage rise and network loss. Examples of this can be seen with greenhouse CHP systems in large greenhouse projects and with wind power around the IJsselmeer. | that network will reduce the voltage drop. In special situations, the voltage can even increase. The electrical energy generated by decentralized generation is directly consumed by the locally present loads.
Decentrale opwekking beïnvloedt de werking van de beveiliging, zoals beschreven in | Decentralized generation affects the operation of the protection systems, as described in | which in turn causes voltage rise and network loss. Examples of this can be seen with greenhouse CHP systems in large greenhouse projects and with wind power around the IJsselmeer.
paragraaf 6.7 | paragraph 6.7 | can be seen with greenhouse CHP systems in large greenhouse projects and with wind power around the IJsselmeer. Decentralized generation affects the operation of the protection systems, as described in
. Is het geproduceerde decentrale vermogen aanzienlijk en heeft dit invloed op optredende kortsluitstromen (met het oog op de kortsluitvastheid) of op de richting van het vermogenstransport in het distributienet, dan moet het beveiligingssysteem hierop worden aangepast. In geval van een kortsluiting kan de decentrale opwekking een verandering van richting en grootte van de kortsluitstroom veroorzaken. Daardoor is de stroomverdeling in het betreffende netgedeelte niet meer eenduidig bepaald. Hierdoor kan het voorkomen dat een traditioneel beveiligingssysteem niet selectief afschakelt of weigert. | If the generated decentralized power is significant and affects the occurring short-circuit currents (with regard to short-circuit strength) or the direction of power transport in the distribution network, then the protection system must be adjusted accordingly. In the event of a short circuit, decentralized generation can cause a change in the direction and magnitude of the short-circuit current. As a result, the current distribution in the relevant network section is no longer uniquely determined. This can lead to a traditional protection system not selectively disconnecting or failing. | seen with greenhouse CHP systems in large greenhouse projects and with wind power around the IJsselmeer. Decentralized generation affects the operation of the protection systems, as described in paragraph 6.7
Decentrale opwekking maakt de vraag naar metingen en informatie vanuit het distributienet noodzakelijk. Deze zijn noodzakelijk voor het maken van de netberekeningen voor het doorrekenen van de consequenties van schakelplannen. Dit betekent dat netgegevens zowel actueel als correct moeten zijn. | Decentralized generation necessitates the demand for measurements and information from the distribution network. These are essential for performing network calculations to assess the consequences of switching plans. This means that network data must be both current and accurate. | current. As a result, the current distribution in the relevant network section is no longer uniquely determined. This can lead to a traditional protection system not selectively disconnecting or failing.
14.6 Netverliezen | 14.6 Network Losses | information from the distribution network. These are essential for performing network calculations to assess the consequences of switching plans. This means that network data must be both current and accurate.
Bij transport en distributie van elektrische energie treden netverliezen op in kabels en transformatoren. De verliezen zijn gelijk aan het verschil tussen de opgewekte en opgenomen energie. Volgens de elektriciteitsbalans van CBS was in 2010 het totale elektriciteitsverbruik in Nederland 117563 GWh. Hierbij heeft het CBS becijferd dat het totale verlies in dat jaar 4450 GWh bedroeg (CBS, 2011). Hiervan bedroeg het verlies in het 220/380 kV koppelnet 525 GWh (TenneT, 2010) en wordt het verlies over het 110/150 kV transportnet geschat op 600 GWh. Hetgeen resteert is het verlies over de MS- en LS-distributienetten: 3325 GWh (2,8%). Dit wordt ongeveer gelijk verdeeld over de MS-netten, de LS-netten en de MS/LS-nettransformatoren (EnergieNed, 1996). | During the transport and distribution of electrical energy, network losses occur in cables and transformers. The losses are equal to the difference between the generated and consumed energy. According to the electricity balance of CBS, the total electricity consumption in the Netherlands in 2010 was 117,563 GWh. CBS calculated that the total loss that year amounted to 4,450 GWh (CBS, 2011). Of this, the loss in the 220/380 kV coupling network was 525 GWh (TenneT, 2010), and the loss over the 110/150 kV transmission network is estimated at 600 GWh. The remaining loss over the medium voltage (MV) and low voltage (LV) distribution networks is 3,325 GWh (2.8%). This is approximately equally distributed over the MV networks, the LV networks, and the MV/LV network transformers (EnergieNed, 1996). | distribution network. These are essential for performing network calculations to assess the consequences of switching plans. This means that network data must be both current and accurate. 14.6 Network Losses
Een van de mogelijkheden de netverliezen te beperken is het gunstig kiezen van de locaties van de netopeningen. Ten aanzien van de locaties van netopeningen moet naast het netverlies echter ook rekening gehouden worden met de spanningshuishouding en de betrouwbaarheid: | One of the ways to reduce network losses is to optimally choose the locations of the network openings. However, regarding the locations of network openings, consideration must also be given to voltage management and reliability in addition to network losses. | (MV) and low voltage (LV) distribution networks is 3,325 GWh (2.8%). This is approximately equally distributed over the MV networks, the LV networks, and the MV/LV network transformers (EnergieNed, 1996).
door de netopening aan te brengen in de kabel die in alle gevallen (belastingsgedrag) het minst wordt belast, wordt het transportverlies beperkt | by placing the network opening in the cable that is least loaded in all cases (load behavior), transport loss is minimized | optimally choose the locations of the network openings. However, regarding the locations of network openings, consideration must also be given to voltage management and reliability in addition to network losses.
op alle knooppunten mag de spanning de gestelde randvoorwaarden niet over- en onderschrijden | At all nodes, the voltage must not exceed or fall below the specified limits. | voltage management and reliability in addition to network losses. by placing the network opening in the cable that is least loaded in all cases (load behavior), transport loss is minimized
de kans op onderbreking en de gemiddelde onderbrekingsduur moet minimaal zijn. | the likelihood of interruption and the average interruption duration must be minimal. | in the cable that is least loaded in all cases (load behavior), transport loss is minimized At all nodes, the voltage must not exceed or fall below the specified limits.
De netopeningen worden zoveel mogelijk geconcentreerd in specifieke netstations, die snel bereikbaar zijn. Dit bespoedigt het herstelproces en is bij gepland omschakelen ook gemakkelijk. Ook worden de netopeningen geconcentreerd bij belangrijke klanten, die in geval van een storing snel kunnen worden overgeschakeld op een andere streng. | The network openings are concentrated as much as possible in specific substations that are easily accessible. This speeds up the recovery process and is also convenient for planned switching. Additionally, the network openings are concentrated near important customers, who can be quickly switched to another circuit in case of a failure. | transport loss is minimized At all nodes, the voltage must not exceed or fall below the specified limits. the likelihood of interruption and the average interruption duration must be minimal.
Figuur 14.8 Verdeling van het netverlies in het Nederlandse elektriciteitsnet | Figure 14.8 Distribution of network loss in the Dutch electricity grid | process and is also convenient for planned switching. Additionally, the network openings are concentrated near important customers, who can be quickly switched to another circuit in case of a failure.
14.7 Regulering | 14.7 Regulation | openings are concentrated near important customers, who can be quickly switched to another circuit in case of a failure. Figure 14.8 Distribution of network loss in the Dutch electricity grid
Tijdens de liberalisering van energiebedrijven stond stroomlijning van het klantenproces, kostenbesparing en personeelsreductie centraal en was er minder belangstelling voor de netwerken. Door invoering van de kwaliteitsfactor (q-factor) wordt goede kwaliteit van het elektriciteitsnet, in casu de betrouwbaarheid, financieel beloond via de toegestane tarieven die een netbeheerder mag hanteren. In een regio functioneert de netbeheerder als monopolist. Om te voorkomen dat de netbeheerder als gevolg van het ontbreken van concurrentieprikkels onvoldoende doelmatig werkt, te hoge tarieven vaststelt of tussen verschillende typen afnemers gaat discrimineren, stelt de DTe jaarlijks de tarieven vast. | During the liberalization of energy companies, streamlining the customer process, cost savings, and staff reduction were central, and there was less interest in the networks. With the introduction of the quality factor (q-factor), good quality of the electricity grid, specifically reliability, is financially rewarded through the allowable rates that a grid operator may charge. In a region, the grid operator functions as a monopolist. To prevent the grid operator from working inefficiently due to the lack of competitive incentives, setting excessively high rates, or discriminating between different types of consumers, the DTe sets the rates annually. | concentrated near important customers, who can be quickly switched to another circuit in case of a failure. Figure 14.8 Distribution of network loss in the Dutch electricity grid 14.7 Regulation
Dit reguleringssysteem bestaat uit twee componenten: | This regulatory system consists of two components: | the grid operator from working inefficiently due to the lack of competitive incentives, setting excessively high rates, or discriminating between different types of consumers, the DTe sets the rates annually.
Een prijscomponent: om de doelmatigheid te bevorderen wordt aan de netbeheerders een doelmatigheidskorting (hierna: de 'x-factor') opgelegd. De x-factor symboliseert de doelmatigheidswinst die de netbeheerders kunnen behalen gedurende de reguleringsperiode. Regionale netbeheerders die hun kosten per eenheid output meer verlagen dan een gemiddelde netbeheerder realiseren een relatief hogere winst. Dit prikkelt de netbeheerders om zo doelmatig mogelijk te handelen. | A price component: to promote efficiency, a productivity discount (hereinafter referred to as the 'x-factor') is imposed on the network operators. The x-factor symbolizes the efficiency gains that network operators can achieve during the regulatory period. Regional network operators who reduce their costs per unit of output more than an average network operator realize a relatively higher profit. This incentivizes the network operators to act as efficiently as possible. | to the lack of competitive incentives, setting excessively high rates, or discriminating between different types of consumers, the DTe sets the rates annually. This regulatory system consists of two components:
Een kwaliteitscomponent: deze vorm van regulering is geïntroduceerd om er voor te zorgen dat de netbeheerders niet te veel nadruk op kostenefficiëntie leggen. Er moet ook aandacht zijn voor de kwaliteit van het netwerk. Met kwaliteit wordt hier alleen gedoeld op de continuïteit. De 'belevenis' van de consument met betrekking tot de betrouwbaarheid van het netwerk van de desbetreffende netbeheerder (vertaald in het aantal storingsminuten) staat daarbij centraal. Om hieraan recht te doen wordt per netbeheerder de q-factor vastgesteld. De werking van deze q-factor is als volgt: als een netbeheerder meer investeert in kwaliteit, zal het aantal storingsminuten naar beneden gaan. De netbeheerder zal dan meer kwaliteit leveren dan de andere netbeheerders (hij presteert beter dan het gemiddelde). De netbeheerder mag dan hogere tarieven vragen. De kwaliteit in de zin van Power Quality zal in de toekomst meer aandacht vragen. | A quality component: this form of regulation has been introduced to ensure that network operators do not place too much emphasis on cost efficiency. Attention must also be given to the quality of the network. Here, quality refers solely to continuity. The consumer's experience regarding the reliability of the network of the respective network operator (translated into the number of outage minutes) is central to this. To address this, the q-factor is determined for each network operator. The operation of this q-factor is as follows: if a network operator invests more in quality, the number of outage minutes will decrease. The network operator will then deliver more quality than the other network operators (performing better than the average). The network operator may then charge higher rates. Quality in terms of Power Quality will require more attention in the future. | who reduce their costs per unit of output more than an average network operator realize a relatively higher profit. This incentivizes the network operators to act as efficiently as possible.
Met dit reguleringssysteem wordt als het ware het effect van marktwerking gesimuleerd, ondanks dat er feitelijk geen marktwerking is tussen netbeheerders. | With this regulatory system, the effect of market forces is essentially simulated, even though there is actually no market competition between network operators. | the other network operators (performing better than the average). The network operator may then charge higher rates. Quality in terms of Power Quality will require more attention in the future.
De bedrijfsvoering van de netten moet dus zodanig zijn ingericht met systemen en procedures dat een positieve bijdrage geleverd wordt aan de beide componenten (q- en x-factor) van het reguleringssysteem. Door te investeren in systemen zoals voor foutplaatslokalisatie, toegespitst op het herstellen van de levering, en in systemen voor centrale (GSM) kortsluitverklikkers, kan direct invloed op de q-factor worden uitgeoefend door het omlaag brengen van de storingsminuten. De bedrijfsvoerder wordt dan voorzien van informatie en hulpmiddelen om de omschakelacties vlot en optimaal te laten gebeuren. | The operation of the networks must therefore be organized with systems and procedures in such a way that a positive contribution is made to both components (q- and x-factor) of the regulatory system. By investing in systems such as fault location systems, focused on restoring supply, and in systems for central (GSM) short-circuit indicators, direct influence can be exerted on the q-factor by reducing outage minutes. The operator is then provided with information and tools to ensure that switching actions are carried out smoothly and optimally. | will require more attention in the future. With this regulatory system, the effect of market forces is essentially simulated, even though there is actually no market competition between network operators.
14.8 Ontwikkelingen | 14.8 Developments | can be exerted on the q-factor by reducing outage minutes. The operator is then provided with information and tools to ensure that switching actions are carried out smoothly and optimally.
Bedrijfsvoering voert haar taak uit met allerhande systemen en hulpmiddelen. Deze systemen zijn in de loop van tijd ontstaan en al dan niet verder ontwikkeld. Zo vormen de papieren wandkaarten met netschema's al jarenlang het belangrijkste hulpmiddel. Via spelden wordt hierop de actuele netsituatie met betrekking tot netopeningen weergegeven. Een ander belangrijk hulpmiddel is een systeem voor storingsafhandeling en het opmaken van schakelplannen. | Operations perform their tasks using various systems and tools. These systems have emerged over time and have been developed to varying extents. For years, paper wall maps with network diagrams have been the most important tool. Pins are used on these maps to display the current network situation regarding network openings. Another important tool is a system for handling outages and creating switching plans. | exerted on the q-factor by reducing outage minutes. The operator is then provided with information and tools to ensure that switching actions are carried out smoothly and optimally. 14.8 Developments
De mate en snelheid waarmee verbeteringen en vernieuwingen voor de bedrijfsvoering van distributienetten zijn door te voeren, wordt mede bepaald door de mogelijkheden van de installaties en systemen in het veld. Er ontbreekt in de meeste MS-installaties een aantal zaken om centraal bedrijf te kunnen voeren zoals in het HS-net. Zo zijn nog lang niet alle afgaande MS-velden in de onderstations verre bemeten en verre bedienbaar. Nieuwe automatiseringssystemen zoals het SASensor systeem kunnen hier verandering in brengen. Met dit systeem is op een relatief eenvoudige manier een complete MS-installatie uit te rusten met bedrijfsmetingen (spanning, stroom en vermogen), DFR (Digital Fault Recording), power quality registratie en verrebediening, inclusief verresignalering van schakelstanden en beveiligingsalarmen. | The degree and speed at which improvements and innovations for the operation of distribution networks can be implemented are partly determined by the capabilities of the installations and systems in the field. Most medium-voltage (MV) installations lack several elements necessary for centralized operation, as seen in the high-voltage (HV) network. For instance, not all outgoing MV fields in substations are remotely measured and controlled. New automation systems, such as the SASensor system, can bring about change in this area. With this system, it is relatively easy to equip a complete MV installation with operational measurements (voltage, current, and power), Digital Fault Recording (DFR), power quality registration, and remote control, including remote signaling of switch positions and security alarms. | important tool. Pins are used on these maps to display the current network situation regarding network openings. Another important tool is a system for handling outages and creating switching plans.
Men wordt zich steeds meer bewust van het belang van een gezond en beheersbaar MS-net. Enerzijds komt dit door de technologische ontwikkelingen die de laatste jaren een flinke vaart hebben genomen in het MS-net. Anderzijds is deze bewustwording afgedwongen door de eisen die van buiten af gesteld worden aan de kwaliteit van deze netten en dus ook aan de bedrijfsvoering ervan. Een moderne bedrijfsvoering strekt zich verder uit dan alleen het bedrijfsvoeringcentrum als centrale locatie. Informatie uit en over het net is in de huidige vrije markt zeker zo relevant voor asset managers en analisten op het kantoor. | People are becoming increasingly aware of the importance of a healthy and manageable MV network. On one hand, this is due to the technological advancements that have rapidly progressed in the MV network in recent years. On the other hand, this awareness has been driven by external demands on the quality of these networks and thus also on their operation. Modern operations extend beyond just the operations center as the central location. Information from and about the network is equally relevant for asset managers and analysts in the office in today's open market. | a complete MV installation with operational measurements (voltage, current, and power), Digital Fault Recording (DFR), power quality registration, and remote control, including remote signaling of switch positions and security alarms.
Ontwikkelingen die op diverse plaatsen zijn ingezet betreffen onder andere: | Developments that have been initiated in various locations include, among others: | beyond just the operations center as the central location. Information from and about the network is equally relevant for asset managers and analysts in the office in today's open market.
digitaliseren van de netschema's met geografische visualisatie | digitizing the network diagrams with geographical visualization | and about the network is equally relevant for asset managers and analysts in the office in today's open market. Developments that have been initiated in various locations include, among others:
invoeren van functionaliteiten voor netanalyse | implementing functionalities for network analysis | for asset managers and analysts in the office in today's open market. Developments that have been initiated in various locations include, among others: digitizing the network diagrams with geographical visualization
invoeren van een systeem voor foutplaatslokalisatie | implementing a system for fault location detection | in the office in today's open market. Developments that have been initiated in various locations include, among others: digitizing the network diagrams with geographical visualization implementing functionalities for network analysis
invoeren van een systeem voor het monitoren van de power quality | implementing a system for monitoring power quality | Developments that have been initiated in various locations include, among others: digitizing the network diagrams with geographical visualization implementing functionalities for network analysis implementing a system for fault location detection
monitoren van bedrijfsmetingen. | monitoring operational measurements. | locations include, among others: digitizing the network diagrams with geographical visualization implementing functionalities for network analysis implementing a system for fault location detection implementing a system for monitoring power quality
De papieren wandkaarten worden op termijn vervangen door elektronische varianten, die op voldoende grote schermen kunnen worden geraadpleegd. Schakelstanden worden op een vergelijkbare wijze gepresenteerd als op de papieren wandkaarten. De netschema's kunnen zowel op schematische als op geografische wijze worden weergegeven. | The paper wall maps will eventually be replaced by electronic versions, which can be consulted on sufficiently large screens. Switch positions will be presented in a similar manner to the paper wall maps. The network diagrams can be displayed both schematically and geographically. | others: digitizing the network diagrams with geographical visualization implementing functionalities for network analysis implementing a system for fault location detection implementing a system for monitoring power quality monitoring operational measurements.
Zodra de netwerken gedigitaliseerd zijn, wordt de stap naar netanalyse berekeningen snel gemaakt. Berekeningsfuncties worden steeds belangrijker in het distributienet waarvan het gedrag, onder andere vanwege de toenemende decentrale opwekking, niet meer alleen op basis van ervaring te voorspellen is. | Once the networks are digitized, the step towards network analysis calculations is quickly made. Calculation functions are becoming increasingly important in the distribution network, whose behavior, among other things due to the increasing decentralized generation, can no longer be predicted based solely on experience. | be consulted on sufficiently large screens. Switch positions will be presented in a similar manner to the paper wall maps. The network diagrams can be displayed both schematically and geographically.
Met behulp van foutplaatslokalisatie wordt de hersteltijd van een energieonderbreking teruggebracht. Bij een storing wordt Digital Fault Recording informatie op het voedende station vergaard en verstuurd naar bedrijfsvoering. Hier wordt de informatie verwerkt tot visualisatie van de gestoorde component in een netschema en in een geografische weergave. Om echter de duur van storingen in het MS-net structureel te verlagen is ook verrebediening nodig, want het alternatief zou het ontwikkelen van N-1 systemen impliceren, zoals bij de vermaasde transportnetten. | With the help of fault location, the recovery time of a power outage is reduced. In the event of a fault, Digital Fault Recording information is gathered at the feeding station and sent to operations. Here, the information is processed into a visualization of the faulty component in a network diagram and a geographical display. However, to structurally reduce the duration of faults in the medium-voltage network, remote control is also necessary, as the alternative would imply developing N-1 systems, similar to meshed transmission networks. | Calculation functions are becoming increasingly important in the distribution network, whose behavior, among other things due to the increasing decentralized generation, can no longer be predicted based solely on experience.
Power Quality metingen vinden vooral plaats op laagspanningsniveau en dicht bij de klant, vaak naar aanleiding van een klacht. Gestuurd door de kwaliteitsregulering zal steeds vaker in de bedrijfsvoering gemonitord en gestuurd worden op power quality. | Power Quality measurements mainly take place at low voltage levels and close to the customer, often in response to a complaint. Driven by quality regulations, power quality will increasingly be monitored and managed in operations. | However, to structurally reduce the duration of faults in the medium-voltage network, remote control is also necessary, as the alternative would imply developing N-1 systems, similar to meshed transmission networks.
Het monitoren van bedrijfsmetingen vindt voornamelijk nog plaats in het bedrijfsvoeringcentrum van het transportnet. In nieuwe systemen voor bedrijfsvoering kunnen bedrijfsmetingen van een station worden geraadpleegd door het openen van de betreffende webinterface van dat station. In deze webinterface zijn momentane meetwaarden van spanning, stroom en vermogenstromen per fase voorhanden. Zodra de stations zijn uitgerust met verrebediening, biedt deze webinterface ook de mogelijkheid om te schakelen in de stations. Met name in dat geval moet het systeem beveiligd worden tegen indringers en ongewenst gebruik. | The monitoring of operational measurements primarily still takes place in the operations center of the transmission network. In new systems for operations, operational measurements from a station can be accessed by opening the relevant web interface of that station. In this web interface, instantaneous measurement values of voltage, current, and power flows per phase are available. Once the stations are equipped with remote control, this web interface also provides the ability to switch within the stations. Particularly in that case, the system must be secured against intruders and unauthorized use. | place at low voltage levels and close to the customer, often in response to a complaint. Driven by quality regulations, power quality will increasingly be monitored and managed in operations.
De functie van bedrijfsvoering is het beheersen van het primaire transport- en distributieproces met behulp van de ter beschikking staande bedrijfsmiddelen en daarmee de best haalbare continuïteit en kwaliteit van de energielevering te realiseren. De functionaliteit 'bedrijfsvoering' is in het algemeen breder dan het werkterrein van de afdeling 'bedrijfsvoering'. De oorzaak ligt in het ontbreken van de mogelijkheden 'van verre'. Het is de kunst om de organisatorische ontwikkeling in de pas te laten lopen met de technologische ontwikkelingen en ook de regelgeving daarin te optimaliseren. | The function of operations management is to control the primary transport and distribution process using the available resources and thereby achieve the best possible continuity and quality of energy supply. The functionality of 'operations management' is generally broader than the scope of the 'operations management' department. The reason lies in the lack of remote capabilities. The challenge is to align organizational development with technological advancements and also to optimize the regulations in this regard. | equipped with remote control, this web interface also provides the ability to switch within the stations. Particularly in that case, the system must be secured against intruders and unauthorized use.