## Sheet1
Original Text | Translated Text | Previous Context
Belasting en opwekking | Load and generation
Hoofdstuk 3 gaat uitgebreid in op de belastingen en de opwekking van het elektrische vermogen. Hierbij wordt aandacht besteed aan het lange, middellange en korte termijngedrag van de belasting. Met name voor de korte termijn wordt het stochastische gedrag van de belasting toegelicht. Verder worden nieuwe ontwikkelingen op het gebied van verbruik en decentrale opwekking toegelicht. | Chapter 3 delves extensively into the loads and generation of electrical power. It addresses the long-term, medium-term, and short-term behavior of the load. Specifically, the stochastic behavior of the load in the short term is explained. Additionally, new developments in consumption and decentralized generation are discussed. | Load and generation
3 Belasting en opwekking | 3 Load and Generation | medium-term, and short-term behavior of the load. Specifically, the stochastic behavior of the load in the short term is explained. Additionally, new developments in consumption and decentralized generation are discussed.
3.1 Inleiding | 3.1 Introduction | of the load. Specifically, the stochastic behavior of the load in the short term is explained. Additionally, new developments in consumption and decentralized generation are discussed. 3 Load and Generation
3.2 Belasting | 3.2 Load | load. Specifically, the stochastic behavior of the load in the short term is explained. Additionally, new developments in consumption and decentralized generation are discussed. 3 Load and Generation 3.1 Introduction
3.3 Lange termijngedrag van de belasting | 3.3 Long-term behavior of the load | the stochastic behavior of the load in the short term is explained. Additionally, new developments in consumption and decentralized generation are discussed. 3 Load and Generation 3.1 Introduction 3.2 Load
3.4 Middellange termijngedrag van de belasting | 3.4 Medium-term behavior of the load | in the short term is explained. Additionally, new developments in consumption and decentralized generation are discussed. 3 Load and Generation 3.1 Introduction 3.2 Load 3.3 Long-term behavior of the load
3.5 Korte termijngedrag van de belasting | 3.5 Short-term behavior of the load | Additionally, new developments in consumption and decentralized generation are discussed. 3 Load and Generation 3.1 Introduction 3.2 Load 3.3 Long-term behavior of the load 3.4 Medium-term behavior of the load
3.5.1 Het stochastische gedrag van de belasting | 3.5.1 The stochastic behavior of the load | decentralized generation are discussed. 3 Load and Generation 3.1 Introduction 3.2 Load 3.3 Long-term behavior of the load 3.4 Medium-term behavior of the load 3.5 Short-term behavior of the load
3.5.2 Gelijktijdigheid van de belasting en het model van Rusck | 3.5.2 Simultaneity of the load and the Rusck model | Generation 3.1 Introduction 3.2 Load 3.3 Long-term behavior of the load 3.4 Medium-term behavior of the load 3.5 Short-term behavior of the load 3.5.1 The stochastic behavior of the load
3.5.3 Relatie tussen elektriciteitsverbruik en de maximale belasting | 3.5.3 Relationship between electricity consumption and the maximum load | the load 3.4 Medium-term behavior of the load 3.5 Short-term behavior of the load 3.5.1 The stochastic behavior of the load 3.5.2 Simultaneity of the load and the Rusck model
3.5.4 Vaststellen van de parameters voor korte termijnvariaties met behulp van metingen | 3.5.4 Determining the parameters for short-term variations using measurements | Short-term behavior of the load 3.5.1 The stochastic behavior of the load 3.5.2 Simultaneity of the load and the Rusck model 3.5.3 Relationship between electricity consumption and the maximum load
3.6 Nieuwe ontwikkelingen | 3.6 New developments | of the load 3.5.2 Simultaneity of the load and the Rusck model 3.5.3 Relationship between electricity consumption and the maximum load 3.5.4 Determining the parameters for short-term variations using measurements
3.6.1 Warmtepompen | 3.6.1 Heat Pumps | 3.5.2 Simultaneity of the load and the Rusck model 3.5.3 Relationship between electricity consumption and the maximum load 3.5.4 Determining the parameters for short-term variations using measurements 3.6 New developments
3.6.2 Elektrische auto | 3.6.2 Electric Car | the load and the Rusck model 3.5.3 Relationship between electricity consumption and the maximum load 3.5.4 Determining the parameters for short-term variations using measurements 3.6 New developments 3.6.1 Heat Pumps
3.7 Decentrale opwekking | 3.7 Decentralized Generation | the Rusck model 3.5.3 Relationship between electricity consumption and the maximum load 3.5.4 Determining the parameters for short-term variations using measurements 3.6 New developments 3.6.1 Heat Pumps 3.6.2 Electric Car
3.7.1 Micro-WKK-systemen | 3.7.1 Micro-CHP Systems | 3.5.3 Relationship between electricity consumption and the maximum load 3.5.4 Determining the parameters for short-term variations using measurements 3.6 New developments 3.6.1 Heat Pumps 3.6.2 Electric Car 3.7 Decentralized Generation
3.7.2 PV-systemen | 3.7.2 PV Systems | electricity consumption and the maximum load 3.5.4 Determining the parameters for short-term variations using measurements 3.6 New developments 3.6.1 Heat Pumps 3.6.2 Electric Car 3.7 Decentralized Generation 3.7.1 Micro-CHP Systems
3.7.3 Windturbines | 3.7.3 Wind Turbines | the maximum load 3.5.4 Determining the parameters for short-term variations using measurements 3.6 New developments 3.6.1 Heat Pumps 3.6.2 Electric Car 3.7 Decentralized Generation 3.7.1 Micro-CHP Systems 3.7.2 PV Systems
3.7.4 Grote WKK-systemen | 3.7.4 Large CHP Systems | 3.5.4 Determining the parameters for short-term variations using measurements 3.6 New developments 3.6.1 Heat Pumps 3.6.2 Electric Car 3.7 Decentralized Generation 3.7.1 Micro-CHP Systems 3.7.2 PV Systems 3.7.3 Wind Turbines
3.8 Motoren | 3.8 Engines | for short-term variations using measurements 3.6 New developments 3.6.1 Heat Pumps 3.6.2 Electric Car 3.7 Decentralized Generation 3.7.1 Micro-CHP Systems 3.7.2 PV Systems 3.7.3 Wind Turbines 3.7.4 Large CHP Systems
3.9 Onderscheid problematiek op MS- en LS-niveau | 3.9 Distinction of issues at MV and LV levels | variations using measurements 3.6 New developments 3.6.1 Heat Pumps 3.6.2 Electric Car 3.7 Decentralized Generation 3.7.1 Micro-CHP Systems 3.7.2 PV Systems 3.7.3 Wind Turbines 3.7.4 Large CHP Systems 3.8 Engines
3 Belasting en opwekking | 3 Load and Generation | 3.6.2 Electric Car 3.7 Decentralized Generation 3.7.1 Micro-CHP Systems 3.7.2 PV Systems 3.7.3 Wind Turbines 3.7.4 Large CHP Systems 3.8 Engines 3.9 Distinction of issues at MV and LV levels
3.1 Inleiding | 3.1 Introduction | Decentralized Generation 3.7.1 Micro-CHP Systems 3.7.2 PV Systems 3.7.3 Wind Turbines 3.7.4 Large CHP Systems 3.8 Engines 3.9 Distinction of issues at MV and LV levels 3 Load and Generation
Kennis van de belasting en opwekking is een fundamentele voorwaarde voor het dimensioneren van elektriciteitsdistributienetten. Voor het ontwerpen van een distributienet, dat jaren in de toekomst economisch moet zijn, moet uit gegaan worden van gefundeerde aannames betreffende het gevraagde en het geproduceerde vermogen en de ontwikkeling ervan. De netplanner moet aan de hand van berekeningen aantonen dat het ontwerp zal resulteren in een economisch optimum. Bij deze berekeningen moet de planner kunnen omgaan met enerzijds grote hoeveelheden zich gelijksoortig gedragende belastingen en kleine decentrale opwekeenheden en anderzijds kleine hoeveelheden zich niet gelijksoortig gedragende grote belastingen en opwekeenheden. | Knowledge of load and generation is a fundamental requirement for sizing electricity distribution networks. For designing a distribution network that must be economically viable years into the future, it is necessary to base the design on well-founded assumptions regarding the demanded and produced power and their development. The network planner must demonstrate through calculations that the design will result in an economic optimum. In these calculations, the planner must be able to handle, on one hand, large quantities of similarly behaving loads and small decentralized generation units, and on the other hand, small quantities of dissimilarly behaving large loads and generation units. | 3.7.1 Micro-CHP Systems 3.7.2 PV Systems 3.7.3 Wind Turbines 3.7.4 Large CHP Systems 3.8 Engines 3.9 Distinction of issues at MV and LV levels 3 Load and Generation 3.1 Introduction
Een distributienet wordt ontworpen om tenminste gedurende 40 jaar in de toekomst ongestoord elektrisch vermogen van voldoende kwaliteit te leveren aan de aangeslotenen. De energietransitie zal in de toekomst leiden tot het aansluiten van nieuwe belastingen en opwekkers, zoals grote aantallen gelijksoortige warmtepompen, micro WKK’s, zonnepanelen, een geleidelijk groeiend aantal elektrische auto’s en airconditioning systemen. Het toekomstige distributienet moet zodanig ontworpen worden dat grote aanpassingen vermeden kunnen worden. Hierom is kennis van de ontwikkeling van belasting en opwekking van groot belang. | A distribution network is designed to provide uninterrupted electrical power of sufficient quality to its users for at least 40 years into the future. The energy transition will lead to the connection of new loads and generators, such as large numbers of similar heat pumps, micro-CHPs, solar panels, a gradually increasing number of electric cars, and air conditioning systems. The future distribution network must be designed in such a way that major adjustments can be avoided. Therefore, knowledge of the development of load and generation is of great importance. | handle, on one hand, large quantities of similarly behaving loads and small decentralized generation units, and on the other hand, small quantities of dissimilarly behaving large loads and generation units.
3.2 Belasting | 3.2 Load | The future distribution network must be designed in such a way that major adjustments can be avoided. Therefore, knowledge of the development of load and generation is of great importance.
De belasting is ingedeeld in diverse categorieën. Hierbij wordt een uitspraak gedaan over het gedrag als functie van de tijd en als functie van de netspanning. Het spanningsafhankelijke gedrag komt in het hoofdstuk over de modellering aan de orde. Dit hoofdstuk behandelt voornamelijk het gedrag in de tijd, voor de korte, de middellange en de lange termijnen. De korte termijn betreft het momentane gedrag binnen maximaal ongeveer één uur. De middellange termijn betreft het gedrag over een beperkte periode waarbinnen geen sprake is van groei, zoals één dag of één week. De lange termijn betreft een periode van meerdere jaren, eventueel in combinatie met een periodiek middellang termijngedrag. | The load is categorized into various types. This categorization includes an analysis of behavior as a function of time and as a function of the network voltage. The voltage-dependent behavior is discussed in the chapter on modeling. This chapter primarily addresses behavior over time, for short, medium, and long terms. The short term refers to the instantaneous behavior within a maximum of about one hour. The medium term refers to behavior over a limited period without growth, such as one day or one week. The long term refers to a period of several years, possibly in combination with periodic medium-term behavior. | distribution network must be designed in such a way that major adjustments can be avoided. Therefore, knowledge of the development of load and generation is of great importance. 3.2 Load
Er zijn veel manieren denkbaar om de belastingen in categorieën in te delen. Ieder bedrijf hanteert een eigen methode. Een veel gebruikte methode is (EnergieNed, 1996): | There are many conceivable ways to categorize the loads. Each company uses its own method. A commonly used method is (EnergieNed, 1996): | over a limited period without growth, such as one day or one week. The long term refers to a period of several years, possibly in combination with periodic medium-term behavior.
1. Zakelijk kleinverbruik | 1. Small business consumption | years, possibly in combination with periodic medium-term behavior. There are many conceivable ways to categorize the loads. Each company uses its own method. A commonly used method is (EnergieNed, 1996):
2. Huishoudelijk kleinverbruik | 2. Household small consumption | with periodic medium-term behavior. There are many conceivable ways to categorize the loads. Each company uses its own method. A commonly used method is (EnergieNed, 1996): 1. Small business consumption
a. vrijstaande woningen | a. detached houses | There are many conceivable ways to categorize the loads. Each company uses its own method. A commonly used method is (EnergieNed, 1996): 1. Small business consumption 2. Household small consumption
b. eengezinswoningen | b. single-family homes | conceivable ways to categorize the loads. Each company uses its own method. A commonly used method is (EnergieNed, 1996): 1. Small business consumption 2. Household small consumption a. detached houses
c. etagewoningen | c. apartments | categorize the loads. Each company uses its own method. A commonly used method is (EnergieNed, 1996): 1. Small business consumption 2. Household small consumption a. detached houses b. single-family homes
3. Gemengd kleinverbruik (zakelijk en huishoudelijk) | 3. Mixed small consumption (business and household) | loads. Each company uses its own method. A commonly used method is (EnergieNed, 1996): 1. Small business consumption 2. Household small consumption a. detached houses b. single-family homes c. apartments
Het is onvermijdelijk dat met name in de categorie ‘zakelijk kleinverbruik’ de diversiteit vrij groot kan zijn. Belastingen in de categorie ‘huishoudelijk kleinverbruik’ zullen een veel uniformer karakter vertonen. Over de categorie ‘gemengd kleinverbruik’ is op voorhand niets te zeggen, omdat deze afhangt zowel van de soort van zakelijk verbruik als van de verdeling tussen zakelijk en huishoudelijk verbruik. Een nadere definitie van deze categorieën zal door de netontwerper zelf gemaakt moeten worden. Een en ander hangt uiteraard af van de nauwkeurigheid die men verwacht te halen. | It is inevitable that particularly in the category of 'small business consumption,' the diversity can be quite large. Taxes in the category of 'household small consumption' will exhibit a much more uniform character. Nothing can be said in advance about the category of 'mixed small consumption,' as it depends both on the type of business consumption and the distribution between business and household consumption. A more precise definition of these categories will have to be made by the network designer themselves. This, of course, depends on the level of accuracy one expects to achieve. | A commonly used method is (EnergieNed, 1996): 1. Small business consumption 2. Household small consumption a. detached houses b. single-family homes c. apartments 3. Mixed small consumption (business and household)
Belastingen in de categorieën zakelijk of huishoudelijk verbruik vertonen door het hele jaar heen een gelijksoortig gedrag. Specifieke belastingen, zoals warmtepompen en elektrische auto’s stellen hoge eisen aan het distributienet en vragen om een speciale benadering. Belastingen in de categorie ‘warmtepompen’ zullen met name in de koude periode veel elektriciteit verbruiken. Belastingen in de categorie ‘elektrische auto’s’ zullen met name na de ochtend- en avondspits veel elektriciteit verbruiken. | Loads in the categories of commercial or household consumption exhibit similar behavior throughout the year. Specific loads, such as heat pumps and electric cars, place high demands on the distribution network and require a special approach. Loads in the 'heat pumps' category will consume a lot of electricity, particularly during the cold period. Loads in the 'electric cars' category will consume a lot of electricity, especially after the morning and evening rush hours. | A more precise definition of these categories will have to be made by the network designer themselves. This, of course, depends on the level of accuracy one expects to achieve.
Op deze plaats moet vermeld worden dat decentrale opwekking speciale aandacht verdient. Op locaties waar op grote schaal micro-warmte/kracht of zonnepanelen worden toegepast speelt decentrale opwekking een grote rol in de beschouwingen over de stroombelasting van het distributienet. Afhankelijk van de concentraties kan de belastingstroom in het distributienet worden gecompenseerd of zelfs van richting veranderen. Een aansluiting kan zowel vermogen ontvangen als leveren. | It should be noted here that decentralized generation deserves special attention. In locations where micro-CHP (Combined Heat and Power) or solar panels are widely used, decentralized generation plays a significant role in considerations regarding the power load on the distribution network. Depending on the concentrations, the load flow in the distribution network can be compensated or even change direction. A connection can both receive and supply power. | consume a lot of electricity, particularly during the cold period. Loads in the 'electric cars' category will consume a lot of electricity, especially after the morning and evening rush hours.
3.3 Lange termijngedrag van de belasting | 3.3 Long-term behavior of the load | on the distribution network. Depending on the concentrations, the load flow in the distribution network can be compensated or even change direction. A connection can both receive and supply power.
De belastingen in een distributienet vertonen een jaarlijkse groei (accres). Het accres wordt meestal in procenten ten opzichte van de uitgangsdatum aangegeven. Distributienetten worden zodanig gedimensioneerd dat het accres binnen de economische levensduur niet leidt tot grote aanpassingen. Dit betekent dat de netten worden ontworpen voor de maximale belasting die optreedt aan het einde van hun economische levensduur. Voor de prognose moet de netplanner inzicht hebben in: | The loads in a distribution network exhibit annual growth (accretion). The accretion is usually indicated as a percentage relative to the baseline date. Distribution networks are dimensioned in such a way that the accretion within the economic lifespan does not lead to major adjustments. This means that the networks are designed for the maximum load that occurs at the end of their economic lifespan. For the forecast, the network planner must have insight into: | the concentrations, the load flow in the distribution network can be compensated or even change direction. A connection can both receive and supply power. 3.3 Long-term behavior of the load
belastinggroei door toename van het aantal aansluitingen | load growth due to an increase in the number of connections | This means that the networks are designed for the maximum load that occurs at the end of their economic lifespan. For the forecast, the network planner must have insight into:
belastinggroei door groei als gevolg van wijzigend gedrag van de klant. | load growth due to an increase as a result of changing customer behavior. | that occurs at the end of their economic lifespan. For the forecast, the network planner must have insight into: load growth due to an increase in the number of connections
Het aantal aansluitingen wordt voornamelijk bepaald door de planologie van landelijk tot regionaal niveau. Voor de hogere netniveaus, zoals transformatoren en middenspanningsnetten, bestaat het accres voor een belangrijk deel uit belastingtoename als gevolg van groei in het aantal aansluitingen. Er bestaat een eenvoudige benadering, die gebruik maakt van de aantallen aansluitingen en het gemiddelde jaarverbruik van het specifieke type aansluiting. | The number of connections is primarily determined by planning from the national to the regional level. For the higher network levels, such as transformers and medium voltage networks, the increase is largely due to load growth resulting from the rise in the number of connections. There is a simple approach that uses the number of connections and the average annual consumption of the specific type of connection. | network planner must have insight into: load growth due to an increase in the number of connections load growth due to an increase as a result of changing customer behavior.
Naast de toename van het aantal aansluitingen is een prognose van de belastingontwikkeling van bestaande aansluitingen belangrijk. Hierbij moeten schattingen en keuzes gemaakt worden ten aanzien van: | In addition to the increase in the number of connections, a forecast of the load development of existing connections is important. This requires estimates and decisions regarding: | from the rise in the number of connections. There is a simple approach that uses the number of connections and the average annual consumption of the specific type of connection.
het toekomstige gedrag van de klant | the future behavior of the customer | type of connection. In addition to the increase in the number of connections, a forecast of the load development of existing connections is important. This requires estimates and decisions regarding:
technische ontwikkelingen in elektrische apparatuur | technical developments in electrical equipment | the increase in the number of connections, a forecast of the load development of existing connections is important. This requires estimates and decisions regarding: the future behavior of the customer
mogelijkheden voor belastingsturing. | possibilities for load control. | of connections, a forecast of the load development of existing connections is important. This requires estimates and decisions regarding: the future behavior of the customer technical developments in electrical equipment
Het toekomstige gedrag van de klant is vrijwel niet te voorspellen. Daarom wordt meestal volstaan met het extrapoleren van historische gegevens van categorieën van klanten, eventueel bijgestuurd door eigen inzicht. Hierbij baseert de netplanner zich op planologische informatie en marktanalyse. Er bestaat geen algemeen bruikbaar model of prognosticeringssysteem. De onzekerheden zijn het grootst in laagspanningsnetten. Hierom ontstaat de trend dat de netontwerper zich steeds meer gaat indekken voor toekomstige onzekerheden en zal hij het laagspanningsnet zo zwaar mogelijk gaan ontwerpen: met maximale kabeldoorsneden en een zo groot mogelijke distributietransformator, van bijvoorbeeld 630 kVA. Ook zal hij bij nieuwbouw extra ruimte claimen om in de toekomst, mocht het nodig blijken, extra netruimten te kunnen plaatsen en zo toekomstige kosten zoveel mogelijk te vermijden. | The future behavior of the customer is almost impossible to predict. Therefore, it is usually sufficient to extrapolate historical data from categories of customers, possibly adjusted by personal insight. In doing so, the network planner relies on planning information and market analysis. There is no universally applicable model or forecasting system. The uncertainties are greatest in low-voltage networks. As a result, there is a trend for the network designer to increasingly hedge against future uncertainties by designing the low-voltage network as robustly as possible: with maximum cable cross-sections and the largest possible distribution transformer, for example, 630 kVA. Additionally, in new constructions, the designer will claim extra space to potentially place additional network spaces in the future if necessary, thereby avoiding future costs as much as possible. | of the load development of existing connections is important. This requires estimates and decisions regarding: the future behavior of the customer technical developments in electrical equipment possibilities for load control.
De technische ontwikkelingen in apparatuur richten zich voornamelijk op het vergroten van de efficiëntie die moet leiden tot energiebesparing. Te denken valt aan energiezuinige verlichting. Aan de andere kant wordt nieuwe apparatuur ontwikkeld die weliswaar efficiënt met energie omgaat, maar wel veel meer elektriciteit verbruikt. De opkomst van nieuwe soorten belastingen zoals warmtepompen en elektrische auto’s heeft dan ook een grote impact op de groei. Hoe lager het netniveau, des te groter deze invloed is. Ook decentrale opwekking is een complicerende factor voor de prognose. | The technical developments in equipment are primarily focused on increasing efficiency, which should lead to energy savings. Think of energy-efficient lighting, for example. On the other hand, new equipment is being developed that, while efficient in energy use, consumes much more electricity. The rise of new types of loads such as heat pumps and electric cars also has a significant impact on growth. The lower the network level, the greater this influence is. Decentralized generation is also a complicating factor for the forecast. | kVA. Additionally, in new constructions, the designer will claim extra space to potentially place additional network spaces in the future if necessary, thereby avoiding future costs as much as possible.
De mogelijkheden voor belastingsturing worden weer actueel door de ontwikkelingen op het gebied van ‘intelligente netwerken’. De ontwikkelingen hebben meestal betrekking op het afstemmen van vraag en aanbod van elektrische energie. | The possibilities for load management are becoming relevant again due to developments in the field of 'smart grids.' These developments mostly pertain to balancing the supply and demand of electrical energy. | and electric cars also has a significant impact on growth. The lower the network level, the greater this influence is. Decentralized generation is also a complicating factor for the forecast.
Figuur 3.1 toont de ontwikkeling van het elektriciteitsverbruik in Nederland van 1938 tot 2008 (bron: CBS 2010). Opvallend is de trendbreuk, omstreeks het jaar 1973. Hierdoor is over de hele periode bezien de groei ruwweg in twee tijdvakken verdeeld. In het eerste gedeelte, van 1938 tot 1973 is de groei jaarlijks 8%. Van 1973 tot 2008 is de groei 2,4% per jaar. Hierbij is uitgegaan van een exponentiële groei: | Figure 3.1 shows the development of electricity consumption in the Netherlands from 1938 to 2008 (source: CBS 2010). Noteworthy is the trend break around the year 1973. As a result, the growth over the entire period is roughly divided into two time frames. In the first period, from 1938 to 1973, the growth is 8% annually. From 1973 to 2008, the growth is 2.4% per year. This is based on exponential growth: | possibilities for load management are becoming relevant again due to developments in the field of 'smart grids.' These developments mostly pertain to balancing the supply and demand of electrical energy.
[ | [ | frames. In the first period, from 1938 to 1973, the growth is 8% annually. From 1973 to 2008, the growth is 2.4% per year. This is based on exponential growth:
3.1 | 3.1 | In the first period, from 1938 to 1973, the growth is 8% annually. From 1973 to 2008, the growth is 2.4% per year. This is based on exponential growth: [
] | ] | the first period, from 1938 to 1973, the growth is 8% annually. From 1973 to 2008, the growth is 2.4% per year. This is based on exponential growth: [ 3.1
De grafiek toont de door de CBS geregistreerde cijfers en de berekende curve met de hierboven genoemde groeicijfers. | The graph shows the figures recorded by CBS and the calculated curve with the growth rates mentioned above. | first period, from 1938 to 1973, the growth is 8% annually. From 1973 to 2008, the growth is 2.4% per year. This is based on exponential growth: [ 3.1 ]
Figuur 3.1 Ontwikkeling van het elektriciteitsverbruik in Nederland tussen 1938 en 2008 | Figure 3.1 Development of electricity consumption in the Netherlands between 1938 and 2008 | 2.4% per year. This is based on exponential growth: [ 3.1 ] The graph shows the figures recorded by CBS and the calculated curve with the growth rates mentioned above.
Een periode van 70 jaren is meestal te lang voor een redelijke groeiprognose. Er is sprake van een duidelijke trendbreuk omstreeks 1973. Figuur 3.2 toont de ontwikkeling van het elektriciteitsverbruik in Nederland van 1995 tot 2008. Aan de grafiek is een lineaire trendlijn toegevoegd. Over deze periode van 13 jaar is de toename ten opzichte van 1995 bij benadering lineair met 2,4% per jaar. | A period of 70 years is usually too long for a reasonable growth forecast. There is a clear trend break around 1973. Figure 3.2 shows the development of electricity consumption in the Netherlands from 1995 to 2008. A linear trend line has been added to the graph. Over this 13-year period, the increase relative to 1995 is approximately linear at 2.4% per year. | graph shows the figures recorded by CBS and the calculated curve with the growth rates mentioned above. Figure 3.1 Development of electricity consumption in the Netherlands between 1938 and 2008
Figuur 3.2 Ontwikkeling van het elektriciteitsverbruik in Nederland tussen 1995 en 2008 | Figure 3.2 Development of electricity consumption in the Netherlands between 1995 and 2008 | from 1995 to 2008. A linear trend line has been added to the graph. Over this 13-year period, the increase relative to 1995 is approximately linear at 2.4% per year.
Figuur 3.3 toont het verbruik in Nederland in 2008. Het verschil tussen zomer en winter is een kleine 20 procent. Deze grafiek toont aan dat binnen het tijdsbestek van één jaar normaliter geen rekening wordt gehouden met de groei. Wel houdt men rekening met het seizoensafhankelijke gedrag. | Figure 3.3 shows the consumption in the Netherlands in 2008. The difference between summer and winter is about 20 percent. This graph indicates that within the span of one year, growth is typically not taken into account. However, seasonal behavior is considered. | graph. Over this 13-year period, the increase relative to 1995 is approximately linear at 2.4% per year. Figure 3.2 Development of electricity consumption in the Netherlands between 1995 and 2008
Figuur 3.3 Ontwikkeling van het elektriciteitsverbruik per maand in Nederland in 2008 | Figure 3.3 Development of monthly electricity consumption in the Netherlands in 2008 | between summer and winter is about 20 percent. This graph indicates that within the span of one year, growth is typically not taken into account. However, seasonal behavior is considered.
Figuur 3.4 Dagbelastingspatronen in een woonwijk in de winter (links) en in de zomer (rechts). Donkerblauw is maximum, rose is gemiddeld, zwart is minimum; de lichtblauwe lijn is de standaarddeviatie | Figure 3.4 Daily load patterns in a residential area in winter (left) and in summer (right). Dark blue is maximum, pink is average, black is minimum; the light blue line is the standard deviation. | within the span of one year, growth is typically not taken into account. However, seasonal behavior is considered. Figure 3.3 Development of monthly electricity consumption in the Netherlands in 2008
3.4 Middellange termijngedrag van de belasting | 3.4 Medium-term behavior of the load | patterns in a residential area in winter (left) and in summer (right). Dark blue is maximum, pink is average, black is minimum; the light blue line is the standard deviation.
De middellange termijn is een rekbaar begrip. De belasting kan in zekere zin bekend worden verondersteld in deze periode dat de groei en het willekeurige gedrag een minder grote rol spelen. Het gedrag van de belasting wordt dan deterministisch genoemd. Het middellange termijn gedrag beschrijft de belasting over een dag, een week, een maand of een gedeelte van een jaar. Naar gelang de toepassing gebruikt de netplanner de maximum en minimum waarden van de belasting of gebruikt hij belastingspatronen. | The medium term is a flexible concept. The load can be assumed to be known to some extent during this period, as growth and random behavior play a lesser role. The behavior of the load is then called deterministic. Medium-term behavior describes the load over a day, a week, a month, or a portion of a year. Depending on the application, the network planner uses the maximum and minimum values of the load or uses load patterns. | winter (left) and in summer (right). Dark blue is maximum, pink is average, black is minimum; the light blue line is the standard deviation. 3.4 Medium-term behavior of the load
De afbeeldingen links geven een voorbeeld van de belastingstromen in een woonwijk, gedurende de winter (links) en de zomer (rechts). Deze woonwijk heeft alleen ‘traditionele’ belastingen. Dat wil zeggen: gewone huishoudelijke apparatuur en verlichting en geen elektrische auto’s, warmtepompen, micro-WKK’s en zonnepanelen. De belastingen op zondag, op zaterdag en op werkdagen lijken sterk op elkaar, zowel in de winter als in de zomer. Voor alle dagen van de week bedraagt het maximum in de zomer ongeveer 60% van het wintermaximum. Het minimum in de zomer is ongeveer gelijk aan het winterminimum. In de vorm van de dagbelastingskromme in de winter is duidelijk het gedrag in de avonduren zichtbaar. Globaal tussen 17:00 en 22:00 uur is de belasting beduidend hoger dan overdag. | The images on the left provide an example of the load flows in a residential area during the winter (left) and the summer (right). This residential area only has 'traditional' loads. That is to say: regular household appliances and lighting, and no electric cars, heat pumps, micro-CHP units, or solar panels. The loads on Sunday, Saturday, and weekdays are very similar, both in winter and summer. For all days of the week, the maximum in the summer is approximately 60% of the winter maximum. The minimum in the summer is roughly equal to the winter minimum. In the shape of the daily load curve in the winter, the behavior in the evening hours is clearly visible. Generally, between 5:00 PM and 10:00 PM, the load is significantly higher than during the day. | a week, a month, or a portion of a year. Depending on the application, the network planner uses the maximum and minimum values of the load or uses load patterns.
Figuur 3.5 Dagpatronen van de cos(φ) van de belasting in een woonwijk in de winter (links) en in de zomer (rechts) | Figure 3.5 Daily patterns of the cos(φ) of the load in a residential area in winter (left) and in summer (right) | load curve in the winter, the behavior in the evening hours is clearly visible. Generally, between 5:00 PM and 10:00 PM, the load is significantly higher than during the day.
Figuur 3.5 illustreert het gedrag van de cos(φ) over de werkdagen in januari (links) en juli (rechts). Het valt op dat de cos(φ) in de winter gemiddeld 0,92 bedraagt en in de zomer 0,88. Tijdens de perioden van lage belasting vertoont de cos(φ) lagere waarden dan in perioden van hoge belasting. | Figure 3.5 illustrates the behavior of the cos(φ) over the weekdays in January (left) and July (right). It is noticeable that the cos(φ) averages 0.92 in the winter and 0.88 in the summer. During periods of low load, the cos(φ) shows lower values than during periods of high load. | the load is significantly higher than during the day. Figure 3.5 Daily patterns of the cos(φ) of the load in a residential area in winter (left) and in summer (right)
De belastingspatronen kunnen worden toegepast op een korte tijdspanne, zoals een dag, maar ook voor een langere tijdspanne, zoals een maand of een jaar. Figuur 3.6 toont het gedrag van de voedingsstroom vanuit het voedingsstation van een 20 kV-streng in een kassengebied gedurende drie weken in september. Een negatieve waarde van de stroom betekent een omgekeerde energierichting. Duidelijk is te zien dat de stroom dagelijks van teken wisselt. Dit betekent dat de som van de stroom van alle aangeslotenen dagelijks wisselt tussen afname en productie. In dit geval komt een belastingstroom van 100 A overeen met een driefasig vermogen van ongeveer 3,5 MVA. | The load patterns can be applied to a short time span, such as a day, but also for a longer time span, such as a month or a year. Figure 3.6 shows the behavior of the supply current from the substation of a 20 kV line in a greenhouse area over three weeks in September. A negative value of the current means a reverse energy direction. It is clearly visible that the current changes sign daily. This means that the sum of the current of all connected users alternates daily between consumption and production. In this case, a load current of 100 A corresponds to a three-phase power of approximately 3.5 MVA. | noticeable that the cos(φ) averages 0.92 in the winter and 0.88 in the summer. During periods of low load, the cos(φ) shows lower values than during periods of high load.
Meting van de belastingen op de individuele knooppunten toont aan hoe de totale voedingsstroom van de streng opgebouwd is uit de som van alle belastingen en generatoren. De grafieken van de generatorvermogens laten zien hoe het aan- en uitschakelen van decentrale opwekking leidt tot dagelijkse schommelingen tot ruim 5 MW per generator. | Measurement of the loads at the individual nodes shows how the total supply current of the feeder is composed of the sum of all loads and generators. The graphs of the generator capacities demonstrate how the switching on and off of decentralized generation leads to daily fluctuations of up to over 5 MW per generator. | the current of all connected users alternates daily between consumption and production. In this case, a load current of 100 A corresponds to a three-phase power of approximately 3.5 MVA.
Figuur 3.6 Belastingspatroon van een 20 kV-streng in een kassengebied | Figure 3.6 Load pattern of a 20 kV line in a greenhouse area | and generators. The graphs of the generator capacities demonstrate how the switching on and off of decentralized generation leads to daily fluctuations of up to over 5 MW per generator.
Figuur 3.7 Vermogenspatroon van individuele aansluitingen in een 20 kV-streng in een kassengebied | Figure 3.7 Power pattern of individual connections in a 20 kV line in a greenhouse area | and off of decentralized generation leads to daily fluctuations of up to over 5 MW per generator. Figure 3.6 Load pattern of a 20 kV line in a greenhouse area
3.5 Korte termijngedrag van de belasting | 3.5 Short-term behavior of the load | generator. Figure 3.6 Load pattern of a 20 kV line in a greenhouse area Figure 3.7 Power pattern of individual connections in a 20 kV line in a greenhouse area
Met het gedrag van de belasting in de korte termijn wordt geprobeerd een uitspraak te doen over de belasting ten tijde van het minimum, het maximum of een ander specifiek tijdstip. De belasting bestaat namelijk uit een gedeelte dat vrij goed voorspelbaar is (de middellange termijn) en een gedeelte dat de belasting zich willekeurig gedraagt. Het is voor een woonwijk redelijk goed bekend wanneer het minimum en het maximum van de belasting zich voordoet en hoe groot de waarde daarvan naar verwachting is. Daarbovenop is altijd een zekere willekeurige component die ervoor zorgt dat de maxima van alle individuele belastingen nooit tegelijkertijd optreden en waardoor het maximum van de som van alle belastingen nooit gelijk is aan de som van alle maxima. | The short-term behavior of the load aims to make a statement about the load at the time of the minimum, maximum, or another specific moment. The load consists of a portion that is fairly predictable (the medium term) and a portion where the load behaves randomly. For a residential area, it is reasonably well known when the minimum and maximum load occurs and what the expected value of that load is. Additionally, there is always a certain random component that ensures the maxima of all individual loads never occur simultaneously, and thus the maximum of the sum of all loads is never equal to the sum of all maxima. | a 20 kV line in a greenhouse area Figure 3.7 Power pattern of individual connections in a 20 kV line in a greenhouse area 3.5 Short-term behavior of the load
In de volgende paragrafen worden de begrippen ‘stochastisch gedrag’ en ‘gelijktijdigheid’ van de belasting nader toegelicht. In bestaande netten zonder elektrische auto’s, warmtepompen, micro-WKK’s en zonnepanelen wordt met de beschreven techniek rekening gehouden met de ongelijktijdigheid van de belastingen. In netten met elektrische auto’s, warmtepompen, micro-WKK’s en zonnepanelen kan echter niet alleen met de zich ongelijktijdig gedragende belasting worden gerekend en moet naast het stochastische gedrag ook rekening gehouden worden met een aanzienlijke component van de belasting die zich met een grote gelijktijdigheid gedraagt. Zo zullen elektrische auto’s worden opgeladen bij thuiskomst aan het einde van een werkdag en zullen warmtepompen met eventueel bijverwarming op koude dagen allemaal gelijktijdig in bedrijf zijn. Als gevolg hiervan zal bij nieuwbouw van netten steeds vaker ontworpen worden op basis van de som van de individuele maximale belastingen, waarbij maar in beperkte mate rekening gehouden wordt met het stochastische gedrag. | The following paragraphs will further explain the concepts of 'stochastic behavior' and 'simultaneity' of the load. In existing networks without electric cars, heat pumps, micro-CHPs, and solar panels, the described technique accounts for the non-simultaneity of the loads. However, in networks with electric cars, heat pumps, micro-CHPs, and solar panels, one cannot rely solely on the non-simultaneous behavior of the load. In addition to the stochastic behavior, a significant component of the load that behaves with high simultaneity must also be considered. For instance, electric cars will be charged upon returning home at the end of a workday, and heat pumps with possible auxiliary heating will all operate simultaneously on cold days. As a result, the design of new networks will increasingly be based on the sum of the individual maximum loads, with only limited consideration given to stochastic behavior. | that ensures the maxima of all individual loads never occur simultaneously, and thus the maximum of the sum of all loads is never equal to the sum of all maxima.
3.5.1 Het stochastische gedrag van de belasting | 3.5.1 The Stochastic Behavior of the Load | cold days. As a result, the design of new networks will increasingly be based on the sum of the individual maximum loads, with only limited consideration given to stochastic behavior.
Individuele klanten vertonen in het elektriciteitsverbruik over een etmaal beschouwd een zeker groepsgedrag, maar gedragen zich momen­taan gezien als onafhankelijke individuen. Immers, niet bij iedereen draait de wasmachine op hetzelfde moment. Maar toch vertonen de individuele gebruikers als functie van de tijd, verspreid over een etmaal, gemiddeld genomen grote overeenkomsten in het gedrag. Figuur 3.8, waarin de belastingscurven genormeerd zijn naar hun eigen gemiddelde, illustreert dit. Tussen 1:00 en 7:00 uur is de belasting minimaal. Tussen 7:00 en 9:00 uur neemt de belasting snel toe. ’s Avonds neemt de belasting nog meer toe, om daarna weer af te dalen tot het minimum. | Individual customers exhibit a certain group behavior in electricity consumption over a 24-hour period, but at any given moment, they behave as independent individuals. After all, not everyone runs their washing machine at the same time. However, individual users, as a function of time spread over a day, generally show significant similarities in behavior. Figure 3.8, where the load curves are normalized to their own average, illustrates this. Between 1:00 AM and 7:00 AM, the load is minimal. Between 7:00 AM and 9:00 AM, the load increases rapidly. In the evening, the load increases even more, only to decrease again to the minimum. | of new networks will increasingly be based on the sum of the individual maximum loads, with only limited consideration given to stochastic behavior. 3.5.1 The Stochastic Behavior of the Load
Figuur 3.8 Genormeerde stroomverdeling voor vier afnemers, verspreid over een dag | Figure 3.8 Normalized power distribution for four consumers, spread over a day | AM, the load is minimal. Between 7:00 AM and 9:00 AM, the load increases rapidly. In the evening, the load increases even more, only to decrease again to the minimum.
Het gedrag van de belastingen wordt beschreven door het deterministische gedrag als functie van de tijd en de momentane stochastische parameters, die onafhankelijk zijn. Het deterministische gedrag wordt beschreven met een patroon als functie van de tijd. Een voor de hand liggend patroon is een 24 uurs dagbelastingcurve. De belastingcurven voor groepen belastingen zijn door meetprojecten inmiddels redelijk bekend. | The behavior of the loads is described by the deterministic behavior as a function of time and the instantaneous stochastic parameters, which are independent. The deterministic behavior is described with a pattern as a function of time. An obvious pattern is a 24-hour daily load curve. The load curves for groups of loads are now reasonably well known through measurement projects. | load increases rapidly. In the evening, the load increases even more, only to decrease again to the minimum. Figure 3.8 Normalized power distribution for four consumers, spread over a day
Alle belastingen gedragen zich over de gehele dag genomen als onderling afhankelijke stochastische signalen, maar binnen een beperkt tijdvenster (van bijvoorbeeld één uur) gedragen zij zich als onafhankelijke stochastische signalen. Van die onafhankelijke stochastische signalen kan per tijdvenster een gemiddelde waarde en een spreiding (standaarddeviatie) worden uitgerekend. Figuur 3.9 illustreert dit. Van alle genormeerde belastingskrommen zijn eerst op uurgemiddelden gebaseerde belastings­krommen berekend. Vervolgens zijn deze uurcurven als functie van de tijd uitgezet. Voor elke uurwaarde is de spreiding uitgerekend tussen alle vier de curven. Deze spreiding is als functie van de tijd uitgezet. | All loads behave as mutually dependent stochastic signals over the entire day, but within a limited time window (for example, one hour), they behave as independent stochastic signals. For these independent stochastic signals, an average value and a spread (standard deviation) can be calculated per time window. Figure 3.9 illustrates this. From all normalized load curves, load curves based on hourly averages were first calculated. These hourly curves were then plotted as a function of time. For each hourly value, the spread between all four curves was calculated. This spread was plotted as a function of time. | pattern as a function of time. An obvious pattern is a 24-hour daily load curve. The load curves for groups of loads are now reasonably well known through measurement projects.
Figuur 3.9 Uurgemiddelden van de genormeerde stroom voor vier afnemers en spreiding | Figure 3.9 Hourly averages of the normalized current for four consumers and spread | curves were then plotted as a function of time. For each hourly value, the spread between all four curves was calculated. This spread was plotted as a function of time.
In figuur 3.9 is op | In figure 3.9, the | the spread between all four curves was calculated. This spread was plotted as a function of time. Figure 3.9 Hourly averages of the normalized current for four consumers and spread
t=12 hr | t=12 hrs | four curves was calculated. This spread was plotted as a function of time. Figure 3.9 Hourly averages of the normalized current for four consumers and spread In figure 3.9, the
een tijdvenster aangegeven. Binnen dat tijdvenster gedraagt de momentane belasting zich als een onafhankelijk stochastisch signaal. De belasting laat zich in ieder tijdvenster beschrijven als een stochastische variabele, met een gemiddelde waarde en een spreiding. Voor het aangegeven tijdvenster in figuur 3.9 is de gemiddelde waarde van de stroom ongeveer gelijk aan 1 pu en de spreiding ongeveer gelijk aan 0,2 pu. | a time window is indicated. Within that time window, the instantaneous load behaves as an independent stochastic signal. The load can be described in each time window as a stochastic variable, with an average value and a spread. For the indicated time window in figure 3.9, the average value of the current is approximately equal to 1 pu and the spread is approximately equal to 0.2 pu. | was calculated. This spread was plotted as a function of time. Figure 3.9 Hourly averages of the normalized current for four consumers and spread In figure 3.9, the t=12 hrs
De Centrale Limietstelling stelt dat de kansverdeling van de som van een voldoend groot aantal onafhankelijke stochastische variabelen bij benadering normaal verdeeld is. Dat betekent voor dit geval dat de som van een voldoende aantal onafhankelijke stochastische belastingsignalen zich bij benadering als een normale verdeling gedraagt. Dit wordt bevestigd door Engels (RWTH, 2000) en Livik (CIRED, 1993). | The Central Limit Theorem states that the probability distribution of the sum of a sufficiently large number of independent stochastic variables is approximately normally distributed. This means, in this case, that the sum of a sufficient number of independent stochastic load signals behaves approximately like a normal distribution. This is confirmed by Engels (RWTH, 2000) and Livik (CIRED, 1993). | spread. For the indicated time window in figure 3.9, the average value of the current is approximately equal to 1 pu and the spread is approximately equal to 0.2 pu.
Met deze aanname kan de belasting op een bepaald tijdstip | With this assumption, the load at a given point in time | case, that the sum of a sufficient number of independent stochastic load signals behaves approximately like a normal distribution. This is confirmed by Engels (RWTH, 2000) and Livik (CIRED, 1993).
t | t | load signals behaves approximately like a normal distribution. This is confirmed by Engels (RWTH, 2000) and Livik (CIRED, 1993). With this assumption, the load at a given point in time
beschreven worden door een normale kansverdeling met gemiddelde | can be described by a normal probability distribution with a mean | signals behaves approximately like a normal distribution. This is confirmed by Engels (RWTH, 2000) and Livik (CIRED, 1993). With this assumption, the load at a given point in time t
μ(t) | μ(t) | Engels (RWTH, 2000) and Livik (CIRED, 1993). With this assumption, the load at a given point in time t can be described by a normal probability distribution with a mean
en spreiding | and standard deviation | (RWTH, 2000) and Livik (CIRED, 1993). With this assumption, the load at a given point in time t can be described by a normal probability distribution with a mean μ(t)
σ(t) | σ(t) | Livik (CIRED, 1993). With this assumption, the load at a given point in time t can be described by a normal probability distribution with a mean μ(t) and standard deviation
. Figuur 3.10 geeft de kansverdeling weer voor een belasting met gemiddelde waarde 3 kW en een spreiding van 1 kW. | Figure 3.10 shows the probability distribution for a load with an average value of 3 kW and a standard deviation of 1 kW. | (CIRED, 1993). With this assumption, the load at a given point in time t can be described by a normal probability distribution with a mean μ(t) and standard deviation σ(t)
Het model van de belasting wordt gecom­pleteerd door de gemiddelde waarden en de spreidingen weer te geven als functies van de tijd. Hiermee is het gedrag van de belasting voor iedere gewenste periode beschreven door een profiel van stochastisch normale verdelingen, gekenmerkt door de tijdfuncties voor de gemiddelden | The load model is completed by representing the mean values and the standard deviations as functions of time. This describes the behavior of the load for any desired period through a profile of stochastic normal distributions, characterized by the time functions for the means. | a mean μ(t) and standard deviation σ(t) Figure 3.10 shows the probability distribution for a load with an average value of 3 kW and a standard deviation of 1 kW.
μ(t) | μ(t) | as functions of time. This describes the behavior of the load for any desired period through a profile of stochastic normal distributions, characterized by the time functions for the means.
en voor de spreidingen | and for the dispersions | functions of time. This describes the behavior of the load for any desired period through a profile of stochastic normal distributions, characterized by the time functions for the means. μ(t)
σ(t) | σ(t) | describes the behavior of the load for any desired period through a profile of stochastic normal distributions, characterized by the time functions for the means. μ(t) and for the dispersions
. | . | the behavior of the load for any desired period through a profile of stochastic normal distributions, characterized by the time functions for the means. μ(t) and for the dispersions σ(t)
Figuur 3.10 Belasting als normale kansverdeling | Figure 3.10 Load as a normal probability distribution | behavior of the load for any desired period through a profile of stochastic normal distributions, characterized by the time functions for the means. μ(t) and for the dispersions σ(t) .
Deze modellering gaat op voor gelijksoortige belastingen. Andere typen belastingen moeten separaat gemodelleerd worden, met ieder hun eigen tijdfuncties. Bij gemengde belastingen moet gewerkt worden met combinaties van de separate tijdfuncties. Bijzondere belastingen, zoals zware industrie, landbouwbedrijven en elektrische tractie, alsmede decentrale opwekkers blijven bijzondere aandacht vragen en kunnen niet met deze methode gemodelleerd worden. | This modeling applies to similar types of loads. Other types of loads must be modeled separately, each with their own time functions. For mixed loads, combinations of the separate time functions must be used. Special loads, such as heavy industry, agricultural enterprises, and electric traction, as well as decentralized generators, continue to require special attention and cannot be modeled using this method. | through a profile of stochastic normal distributions, characterized by the time functions for the means. μ(t) and for the dispersions σ(t) . Figure 3.10 Load as a normal probability distribution
In figuur 3.11 is de gemiddelde belastingscurve voor eerder genoemde vier belastingen afgebeeld. Deze kromme is gelabeld ‘mu’. Ook is er met behulp van de spreidingscurve een band aangegeven, waarbinnen zich met een zekere waarschijnlijkheid de individuele belastingscurven zullen bevinden. De boven- en ondergrenzen zijn berekend door de spreidingscurve bij de gemiddelde curve op te tellen (gelabeld ‘mu+s’), respectievelijk af te trekken (gelabeld ‘mu-s’). Indien de stochastische belasting zich op alle tijdstippen als een normaal verdeelde stochastische variabele zou gedragen, zou de werkelijke waarde van de belasting zich met een waarschijnlijkheid van 70% binnen de aangegeven grenzen bevinden. | Figure 3.11 shows the average load curve for the aforementioned four loads. This curve is labeled 'mu'. Additionally, a band has been indicated using the dispersion curve, within which the individual load curves will likely fall with a certain probability. The upper and lower limits are calculated by adding the dispersion curve to the average curve (labeled 'mu+s') and subtracting it (labeled 'mu-s'), respectively. If the stochastic load behaves as a normally distributed stochastic variable at all times, the actual value of the load would fall within the indicated limits with a probability of 70%. | be used. Special loads, such as heavy industry, agricultural enterprises, and electric traction, as well as decentralized generators, continue to require special attention and cannot be modeled using this method.
Figuur 3.11 Gemiddelde stroom en 1s grens, over een dag | Figure 3.11 Average current and 1s limit, over a day | the stochastic load behaves as a normally distributed stochastic variable at all times, the actual value of the load would fall within the indicated limits with a probability of 70%.
Alle op deze manier in een streng gemodelleerde belastingen kunnen worden gesommeerd volgens de theorie van de stochastische signalen. Dat heeft gevolgen voor het gemiddelde en de spreiding. | All loads modeled in this strict manner can be summed according to the theory of stochastic signals. This has implications for the mean and the variance. | at all times, the actual value of the load would fall within the indicated limits with a probability of 70%. Figure 3.11 Average current and 1s limit, over a day
Figuur 3.12 geeft aan hoe dit uitwerkt in een distributienet. Elk grafiekje geeft de kansverdeling weer van de belastingstroom voor respectievelijk het begin, het midden en het einde van een streng. De gemiddelde waarden zijn respectievelijk 50, 20 en 5. De spreiding neemt toe naar het einde van de streng. | Figure 3.12 illustrates how this works out in a distribution network. Each graph shows the probability distribution of the load flow for the beginning, middle, and end of a feeder, respectively. The average values are 50, 20, and 5, respectively. The spread increases towards the end of the feeder. | limit, over a day All loads modeled in this strict manner can be summed according to the theory of stochastic signals. This has implications for the mean and the variance.
Figuur 3.12 Kansverdelingen van de afnemende stroom in een richting van een distributienet | Figure 3.12 Probability distributions of the decreasing current in one direction of a distribution network | load flow for the beginning, middle, and end of a feeder, respectively. The average values are 50, 20, and 5, respectively. The spread increases towards the end of the feeder.
Dicht bij de voeding is het aantal belastingen, en dus het aantal onafhankelijke stochastische signalen, groot. Doordat de som van het aantal onafhankelijke belastingen verder in het net afneemt, neemt de onzekerheid (en dus de spreiding) toe. Dit komt omdat de maximale belasting bij de verschillende verbruikers op verschillende tijdstippen op zal treden. Dit verschijnsel is eerder beschreven door Rusck. We zien dus dat de gemiddelde waarde afneemt en dat de spreiding in verhouding toeneemt. Een onderzoek heeft aangetoond dat voor afgaande richtingen in het LS-net de aantallen aangeslotenen te klein zijn om de normale verdeling te mogen toepassen. Opvallend resultaat van dit onderzoek was dat rond momenten van de piekbelasting 20% van de aangeslotenen verantwoordelijk was voor 50% van die piek (Provoost, 2011). Voor een klein aantal verbruikers is het dus eigenlijk niet meer correct om de normale verdeling toe te passen. | Close to the feeder, the number of loads, and thus the number of independent stochastic signals, is large. As the sum of the number of independent loads decreases further in the network, the uncertainty (and thus the spread) increases. This is because the maximum load for different consumers will occur at different times. This phenomenon was previously described by Rusck. Therefore, we see that the average value decreases and the spread proportionally increases. A study has shown that for outgoing directions in the low-voltage network, the number of connections is too small to apply the normal distribution. A notable result of this study was that around peak load moments, 20% of the connections were responsible for 50% of that peak (Provoost, 2011). For a small number of consumers, it is therefore no longer correct to apply the normal distribution. | are 50, 20, and 5, respectively. The spread increases towards the end of the feeder. Figure 3.12 Probability distributions of the decreasing current in one direction of a distribution network
3.5.2 Gelijktijdigheid van de belasting en het model van Rusck | 3.5.2 Simultaneity of the load and the Rusck model | 20% of the connections were responsible for 50% of that peak (Provoost, 2011). For a small number of consumers, it is therefore no longer correct to apply the normal distribution.
Voor elk specifiek moment van de dag kan de grootte van de belasting van een specifieke categorie bij benadering voorspeld worden. Het deterministische deel wordt beschreven met behulp van patronen voor bijvoorbeeld een dag. Zo kunnen de momenten geschat worden waarop de belasting minimaal of juist maximaal is. Dit zijn belangrijke waarden voor het dimensioneren van een distributienet. Een distributienet wordt echter niet gedimensioneerd voor de som van de afzonderlijke maximale belastingwaarden van alle aansluitingen, want de maximale belasting van de afzonderlijke aansluitingen zal op verschillende tijdstippen optreden. Dit verschijnsel wordt diversiteit of ongelijktijdigheid genoemd. | For each specific moment of the day, the load size of a specific category can be approximately predicted. The deterministic part is described using patterns for, for example, a day. This way, the moments when the load is minimal or maximal can be estimated. These are important values for sizing a distribution network. However, a distribution network is not sized for the sum of the individual maximum load values of all connections, because the maximum load of the individual connections will occur at different times. This phenomenon is called diversity or non-simultaneity. | that peak (Provoost, 2011). For a small number of consumers, it is therefore no longer correct to apply the normal distribution. 3.5.2 Simultaneity of the load and the Rusck model
Ontwerpberekeningen voor LS- en MS-netten worden doorgaans uitgevoerd door gebruik te maken van maximale belastingen in combinatie met kengetallen voor de gelijktijdigheid ervan. De techniek is gebaseerd op de informatie die de distributiebedrijven jaarlijks vergaarden met verbruiks- en maximaalmetingen op diverse plaatsen in het net. | Design calculations for low-voltage (LV) and medium-voltage (MV) networks are typically performed using maximum loads in combination with diversity factors. The technique is based on information that distribution companies gather annually through consumption and maximum load measurements at various points in the network. | sum of the individual maximum load values of all connections, because the maximum load of the individual connections will occur at different times. This phenomenon is called diversity or non-simultaneity.
De maximale belasting | The maximum load | maximum loads in combination with diversity factors. The technique is based on information that distribution companies gather annually through consumption and maximum load measurements at various points in the network.
P | P | combination with diversity factors. The technique is based on information that distribution companies gather annually through consumption and maximum load measurements at various points in the network. The maximum load
max | max | with diversity factors. The technique is based on information that distribution companies gather annually through consumption and maximum load measurements at various points in the network. The maximum load P
is gedefinieerd als de grootste waarde van de belasting voor aansluitingen, kabels of transformatoren. Een index geeft aan op hoeveel aansluitingen de maximale belasting betrekking heeft. De waarde wordt uitgedrukt in kW. | is defined as the highest value of the load for connections, cables, or transformers. An index indicates the number of connections to which the maximum load applies. The value is expressed in kW. | diversity factors. The technique is based on information that distribution companies gather annually through consumption and maximum load measurements at various points in the network. The maximum load P max
Diversiteit (of ongelijktijdigheid) is het verschijnsel dat de maximale belasting op een punt in het distributienet kleiner is dan de som van de afzonderlijke maximale belastingen van de aansluitingen of van de punten die vanuit het beschouwde punt worden gevoed. De diversiteit treedt op zowel voor alle aansluitingen die op een streng of op een voedingsstation zijn aangesloten als voor alle strengen die op een voedingsstation zijn aangesloten. | Diversity (or non-coincidence) is the phenomenon where the maximum load at a point in the distribution network is smaller than the sum of the individual maximum loads of the connections or of the points fed from the considered point. Diversity occurs both for all connections that are connected to a feeder or a substation and for all feeders that are connected to a substation. | the highest value of the load for connections, cables, or transformers. An index indicates the number of connections to which the maximum load applies. The value is expressed in kW.
Figuur 3.13 Diversiteit van de belasting | Figure 3.13 Diversity of the load | fed from the considered point. Diversity occurs both for all connections that are connected to a feeder or a substation and for all feeders that are connected to a substation.
In figuur 3.13 is | In figure 3.13, the | occurs both for all connections that are connected to a feeder or a substation and for all feeders that are connected to a substation. Figure 3.13 Diversity of the load
P | P | connections that are connected to a feeder or a substation and for all feeders that are connected to a substation. Figure 3.13 Diversity of the load In figure 3.13, the
max | max | that are connected to a feeder or a substation and for all feeders that are connected to a substation. Figure 3.13 Diversity of the load In figure 3.13, the P
de voedingsstroom en | the feeder current and | are connected to a feeder or a substation and for all feeders that are connected to a substation. Figure 3.13 Diversity of the load In figure 3.13, the P max
P | P | feeder or a substation and for all feeders that are connected to a substation. Figure 3.13 Diversity of the load In figure 3.13, the P max the feeder current and
max | max | or a substation and for all feeders that are connected to a substation. Figure 3.13 Diversity of the load In figure 3.13, the P max the feeder current and P
(i) | (i) | a substation and for all feeders that are connected to a substation. Figure 3.13 Diversity of the load In figure 3.13, the P max the feeder current and P max
de maximale belasting in richting | the maximum load in direction | substation and for all feeders that are connected to a substation. Figure 3.13 Diversity of the load In figure 3.13, the P max the feeder current and P max (i)
i | i | that are connected to a substation. Figure 3.13 Diversity of the load In figure 3.13, the P max the feeder current and P max (i) the maximum load in direction
. Voor dit (radiaal bedreven) netwerk geldt: | . For this (radially operated) network, the following applies: | are connected to a substation. Figure 3.13 Diversity of the load In figure 3.13, the P max the feeder current and P max (i) the maximum load in direction i
[ | [ | the load In figure 3.13, the P max the feeder current and P max (i) the maximum load in direction i . For this (radially operated) network, the following applies:
3.2 | 3.2 | load In figure 3.13, the P max the feeder current and P max (i) the maximum load in direction i . For this (radially operated) network, the following applies: [
] | ] | In figure 3.13, the P max the feeder current and P max (i) the maximum load in direction i . For this (radially operated) network, the following applies: [ 3.2
De relatie die de maximale belasting van een deel van het distributienet berekent door gebruik te maken van de gelijktijdigheidsfactor is in 1956 beschreven door Rusck. Het model gaat ervan uit dat de belastingen zich gedragen als stochastisch onafhankelijke variabelen met een normale kansverdeling. Het doel van het model is met behulp van de diversiteit de maximale belasting van componenten, zoals kabels of een voedingstransformator, vast te stellen. De mate van diversiteit wordt beschreven met de gelijktijdigheidsfactor | The relationship that calculates the maximum load of a part of the distribution network using the coincidence factor was described by Rusck in 1956. The model assumes that the loads behave as statistically independent variables with a normal probability distribution. The purpose of the model is to determine the maximum load of components, such as cables or a supply transformer, using diversity. The degree of diversity is described by the coincidence factor. | figure 3.13, the P max the feeder current and P max (i) the maximum load in direction i . For this (radially operated) network, the following applies: [ 3.2 ]
g | g | of the model is to determine the maximum load of components, such as cables or a supply transformer, using diversity. The degree of diversity is described by the coincidence factor.
, die is gedefinieerd als het quotiënt van de maximale belasting | , which is defined as the quotient of the maximum load | the model is to determine the maximum load of components, such as cables or a supply transformer, using diversity. The degree of diversity is described by the coincidence factor. g
P | P | as cables or a supply transformer, using diversity. The degree of diversity is described by the coincidence factor. g , which is defined as the quotient of the maximum load
max,n | max,n | cables or a supply transformer, using diversity. The degree of diversity is described by the coincidence factor. g , which is defined as the quotient of the maximum load P
voor n aansluitingen en de som van de maximale waarden | for n connections and the sum of the maximum values | or a supply transformer, using diversity. The degree of diversity is described by the coincidence factor. g , which is defined as the quotient of the maximum load P max,n
P | P | is described by the coincidence factor. g , which is defined as the quotient of the maximum load P max,n for n connections and the sum of the maximum values
max | max | described by the coincidence factor. g , which is defined as the quotient of the maximum load P max,n for n connections and the sum of the maximum values P
(i) | (i) | by the coincidence factor. g , which is defined as the quotient of the maximum load P max,n for n connections and the sum of the maximum values P max
van de afzonderlijke belastingen die vanuit dit punt gevoed worden. | of the individual loads that are fed from this point. | the coincidence factor. g , which is defined as the quotient of the maximum load P max,n for n connections and the sum of the maximum values P max (i)
[ | [ | quotient of the maximum load P max,n for n connections and the sum of the maximum values P max (i) of the individual loads that are fed from this point.
3.3 | 3.3 | of the maximum load P max,n for n connections and the sum of the maximum values P max (i) of the individual loads that are fed from this point. [
] | ] | the maximum load P max,n for n connections and the sum of the maximum values P max (i) of the individual loads that are fed from this point. [ 3.3
Voor | Voor | maximum load P max,n for n connections and the sum of the maximum values P max (i) of the individual loads that are fed from this point. [ 3.3 ]
n | n | load P max,n for n connections and the sum of the maximum values P max (i) of the individual loads that are fed from this point. [ 3.3 ] Voor
gelijke belastingen met maximum vermogen | equal loads with maximum power | P max,n for n connections and the sum of the maximum values P max (i) of the individual loads that are fed from this point. [ 3.3 ] Voor n
P | P | and the sum of the maximum values P max (i) of the individual loads that are fed from this point. [ 3.3 ] Voor n equal loads with maximum power
max,1 | max,1 | the sum of the maximum values P max (i) of the individual loads that are fed from this point. [ 3.3 ] Voor n equal loads with maximum power P
gaat vergelijking 3.3 over in: | equation 3.3 becomes: | sum of the maximum values P max (i) of the individual loads that are fed from this point. [ 3.3 ] Voor n equal loads with maximum power P max,1
[ | [ | maximum values P max (i) of the individual loads that are fed from this point. [ 3.3 ] Voor n equal loads with maximum power P max,1 equation 3.3 becomes:
3.4 | 3.4 | values P max (i) of the individual loads that are fed from this point. [ 3.3 ] Voor n equal loads with maximum power P max,1 equation 3.3 becomes: [
] | ] | P max (i) of the individual loads that are fed from this point. [ 3.3 ] Voor n equal loads with maximum power P max,1 equation 3.3 becomes: [ 3.4
ofwel: | in other words: | max (i) of the individual loads that are fed from this point. [ 3.3 ] Voor n equal loads with maximum power P max,1 equation 3.3 becomes: [ 3.4 ]
[ | [ | the individual loads that are fed from this point. [ 3.3 ] Voor n equal loads with maximum power P max,1 equation 3.3 becomes: [ 3.4 ] in other words:
3.5 | 3.5 | individual loads that are fed from this point. [ 3.3 ] Voor n equal loads with maximum power P max,1 equation 3.3 becomes: [ 3.4 ] in other words: [
] | ] | loads that are fed from this point. [ 3.3 ] Voor n equal loads with maximum power P max,1 equation 3.3 becomes: [ 3.4 ] in other words: [ 3.5
Een van de voorwaarden voor het toepassen van het model van Rusck is dat alle belastingen zich gedragen als onderling onafhankelijke normaal verdeelde stochastische variabelen. Echter, over een heel etmaal beschouwd, gedraagt de belasting zich niet als een normaal verdeelde stochastische variabele. Zo kunnen globaal twee tijdvensters worden benoemd voor piek- en dalbelasting. Binnen één tijdvenster kan wel aangenomen worden dat de belasting zich als een normaal verdeelde stochastische variabele gedraagt. Dat specifieke tijdvenster vindt bij voorkeur plaats tijdens de piekbelasting. Volgens de kansrekening kan de stochastische variabele beschreven worden met de gemiddelde waarde in het tijdvenster en een bijbehorende spreiding (standaardafwijking). Het verschil tussen de maximale belasting en de gemiddelde belasting in het tijdvenster is dan evenredig met de spreiding. Voor één aansluiting geldt: | One of the conditions for applying Rusck's model is that all loads behave as mutually independent normally distributed stochastic variables. However, when considered over an entire day, the load does not behave as a normally distributed stochastic variable. Generally, two time windows can be identified for peak and off-peak loads. Within one time window, it can be assumed that the load behaves as a normally distributed stochastic variable. This specific time window preferably occurs during peak load. According to probability theory, the stochastic variable can be described with the average value in the time window and a corresponding spread (standard deviation). The difference between the maximum load and the average load in the time window is then proportional to the spread. For a single connection, the following applies: | that are fed from this point. [ 3.3 ] Voor n equal loads with maximum power P max,1 equation 3.3 becomes: [ 3.4 ] in other words: [ 3.5 ]
[ | [ | spread (standard deviation). The difference between the maximum load and the average load in the time window is then proportional to the spread. For a single connection, the following applies:
3.6 | 3.6 | (standard deviation). The difference between the maximum load and the average load in the time window is then proportional to the spread. For a single connection, the following applies: [
] | ] | deviation). The difference between the maximum load and the average load in the time window is then proportional to the spread. For a single connection, the following applies: [ 3.6
waarin: | in which: | The difference between the maximum load and the average load in the time window is then proportional to the spread. For a single connection, the following applies: [ 3.6 ]
P | P | between the maximum load and the average load in the time window is then proportional to the spread. For a single connection, the following applies: [ 3.6 ] in which:
max,1 | max,1 | the maximum load and the average load in the time window is then proportional to the spread. For a single connection, the following applies: [ 3.6 ] in which: P
maximale belasting van één verbruiker | maximum load of a single user | maximum load and the average load in the time window is then proportional to the spread. For a single connection, the following applies: [ 3.6 ] in which: P max,1
P | P | in the time window is then proportional to the spread. For a single connection, the following applies: [ 3.6 ] in which: P max,1 maximum load of a single user
gem,1 | avg,1 | the time window is then proportional to the spread. For a single connection, the following applies: [ 3.6 ] in which: P max,1 maximum load of a single user P
gemiddelde belasting van één verbruiker | average load of a single user | time window is then proportional to the spread. For a single connection, the following applies: [ 3.6 ] in which: P max,1 maximum load of a single user P avg,1
σ | σ | the spread. For a single connection, the following applies: [ 3.6 ] in which: P max,1 maximum load of a single user P avg,1 average load of a single user
1 | 1 | spread. For a single connection, the following applies: [ 3.6 ] in which: P max,1 maximum load of a single user P avg,1 average load of a single user σ
spreiding van één verbruiker | spread of a single user | For a single connection, the following applies: [ 3.6 ] in which: P max,1 maximum load of a single user P avg,1 average load of a single user σ 1
C | C | following applies: [ 3.6 ] in which: P max,1 maximum load of a single user P avg,1 average load of a single user σ 1 spread of a single user
een constante factor | a constant factor | applies: [ 3.6 ] in which: P max,1 maximum load of a single user P avg,1 average load of a single user σ 1 spread of a single user C
In een normale verdeling is, theoretisch gezien, het maximum van het argument van de normale verdeling (de belastingswaarde) oneindig. De maximale waarde van de belasting in het distributienet is echter wel degelijk eindig. De factor | In a normal distribution, theoretically, the maximum of the argument of the normal distribution (the load value) is infinite. However, the maximum value of the load in the distribution network is indeed finite. The factor | ] in which: P max,1 maximum load of a single user P avg,1 average load of a single user σ 1 spread of a single user C a constant factor
C | C | the maximum of the argument of the normal distribution (the load value) is infinite. However, the maximum value of the load in the distribution network is indeed finite. The factor
legt het verband tussen enerzijds het verschil tussen het maximum en gemiddelde van de belasting en anderzijds de spreiding uit het kansbegrip. Zie figuur 3.10, waar | establishes the relationship between, on the one hand, the difference between the maximum and the average of the load and, on the other hand, the dispersion from the probability concept. See figure 3.10, where | maximum of the argument of the normal distribution (the load value) is infinite. However, the maximum value of the load in the distribution network is indeed finite. The factor C
C=3 | C=3 | on the one hand, the difference between the maximum and the average of the load and, on the other hand, the dispersion from the probability concept. See figure 3.10, where
. | . | the one hand, the difference between the maximum and the average of the load and, on the other hand, the dispersion from the probability concept. See figure 3.10, where C=3
Voor een gelijktijdige belasting van n aansluitingen geldt, met dezelfde factor | For a simultaneous load of n connections, the same factor applies | one hand, the difference between the maximum and the average of the load and, on the other hand, the dispersion from the probability concept. See figure 3.10, where C=3 .
C | C | the load and, on the other hand, the dispersion from the probability concept. See figure 3.10, where C=3 . For a simultaneous load of n connections, the same factor applies
: | : | load and, on the other hand, the dispersion from the probability concept. See figure 3.10, where C=3 . For a simultaneous load of n connections, the same factor applies C
[ | [ | and, on the other hand, the dispersion from the probability concept. See figure 3.10, where C=3 . For a simultaneous load of n connections, the same factor applies C :
3.7 | 3.7 | on the other hand, the dispersion from the probability concept. See figure 3.10, where C=3 . For a simultaneous load of n connections, the same factor applies C : [
] | ] | the other hand, the dispersion from the probability concept. See figure 3.10, where C=3 . For a simultaneous load of n connections, the same factor applies C : [ 3.7
Omdat de belasting voor elke gelijksoortige aansluiting zich gedraagt als eenzelfde normale verdeling, geldt voor de spreiding bij | Because the load for each similar connection behaves as the same normal distribution, the dispersion applies to | other hand, the dispersion from the probability concept. See figure 3.10, where C=3 . For a simultaneous load of n connections, the same factor applies C : [ 3.7 ]
n | n | load of n connections, the same factor applies C : [ 3.7 ] Because the load for each similar connection behaves as the same normal distribution, the dispersion applies to
aansluitingen: | connections: | of n connections, the same factor applies C : [ 3.7 ] Because the load for each similar connection behaves as the same normal distribution, the dispersion applies to n
[ | [ | n connections, the same factor applies C : [ 3.7 ] Because the load for each similar connection behaves as the same normal distribution, the dispersion applies to n connections:
3.8 | 3.8 | connections, the same factor applies C : [ 3.7 ] Because the load for each similar connection behaves as the same normal distribution, the dispersion applies to n connections: [
] | ] | the same factor applies C : [ 3.7 ] Because the load for each similar connection behaves as the same normal distribution, the dispersion applies to n connections: [ 3.8
en voor de gemiddelde belasting van | and for the average load of | same factor applies C : [ 3.7 ] Because the load for each similar connection behaves as the same normal distribution, the dispersion applies to n connections: [ 3.8 ]
n | n | 3.7 ] Because the load for each similar connection behaves as the same normal distribution, the dispersion applies to n connections: [ 3.8 ] and for the average load of
aansluitingen: | connections: | ] Because the load for each similar connection behaves as the same normal distribution, the dispersion applies to n connections: [ 3.8 ] and for the average load of n
[ | [ | Because the load for each similar connection behaves as the same normal distribution, the dispersion applies to n connections: [ 3.8 ] and for the average load of n connections:
3.9 | 3.9 | the load for each similar connection behaves as the same normal distribution, the dispersion applies to n connections: [ 3.8 ] and for the average load of n connections: [
] | ] | load for each similar connection behaves as the same normal distribution, the dispersion applies to n connections: [ 3.8 ] and for the average load of n connections: [ 3.9
Na combinatie volgt uit bovenstaande vergelijkingen: | After combination, the following results from the above equations: | for each similar connection behaves as the same normal distribution, the dispersion applies to n connections: [ 3.8 ] and for the average load of n connections: [ 3.9 ]
[ | [ | distribution, the dispersion applies to n connections: [ 3.8 ] and for the average load of n connections: [ 3.9 ] After combination, the following results from the above equations:
3.10 | 3.10 | the dispersion applies to n connections: [ 3.8 ] and for the average load of n connections: [ 3.9 ] After combination, the following results from the above equations: [
] | ] | dispersion applies to n connections: [ 3.8 ] and for the average load of n connections: [ 3.9 ] After combination, the following results from the above equations: [ 3.10
Door vergelijking 3.10 te delen door | By dividing equation 3.10 by | applies to n connections: [ 3.8 ] and for the average load of n connections: [ 3.9 ] After combination, the following results from the above equations: [ 3.10 ]
n·P | n·P | 3.8 ] and for the average load of n connections: [ 3.9 ] After combination, the following results from the above equations: [ 3.10 ] By dividing equation 3.10 by
max,1 | max,1 | ] and for the average load of n connections: [ 3.9 ] After combination, the following results from the above equations: [ 3.10 ] By dividing equation 3.10 by n·P
volgt de uitdrukking voor de gelijktijdigheidsfactor: | the expression for the simultaneity factor follows: | and for the average load of n connections: [ 3.9 ] After combination, the following results from the above equations: [ 3.10 ] By dividing equation 3.10 by n·P max,1
[ | [ | connections: [ 3.9 ] After combination, the following results from the above equations: [ 3.10 ] By dividing equation 3.10 by n·P max,1 the expression for the simultaneity factor follows:
3.11 | 3.11 | [ 3.9 ] After combination, the following results from the above equations: [ 3.10 ] By dividing equation 3.10 by n·P max,1 the expression for the simultaneity factor follows: [
] | ] | 3.9 ] After combination, the following results from the above equations: [ 3.10 ] By dividing equation 3.10 by n·P max,1 the expression for the simultaneity factor follows: [ 3.11
Voor een oneindig aantal aansluitingen geldt: | For an infinite number of connections, the following applies: | ] After combination, the following results from the above equations: [ 3.10 ] By dividing equation 3.10 by n·P max,1 the expression for the simultaneity factor follows: [ 3.11 ]
[ | [ | equations: [ 3.10 ] By dividing equation 3.10 by n·P max,1 the expression for the simultaneity factor follows: [ 3.11 ] For an infinite number of connections, the following applies:
3.12 | 3.12 | [ 3.10 ] By dividing equation 3.10 by n·P max,1 the expression for the simultaneity factor follows: [ 3.11 ] For an infinite number of connections, the following applies: [
] | ] | 3.10 ] By dividing equation 3.10 by n·P max,1 the expression for the simultaneity factor follows: [ 3.11 ] For an infinite number of connections, the following applies: [ 3.12
De gelijktijdigheidsfactor voor een oneindig aantal aansluitingen beschrijft het gedrag voor een specifiek belastingstype, onafhankelijk van het aantal aansluitingen. Hiermee gaat de vergelijking voor de gelijktijdigheidsfactor over in de vergelijking van Rusck: | The simultaneity factor for an infinite number of connections describes the behavior for a specific load type, independent of the number of connections. Thus, the equation for the simultaneity factor transforms into the Rusck equation: | ] By dividing equation 3.10 by n·P max,1 the expression for the simultaneity factor follows: [ 3.11 ] For an infinite number of connections, the following applies: [ 3.12 ]
[ | [ | infinite number of connections describes the behavior for a specific load type, independent of the number of connections. Thus, the equation for the simultaneity factor transforms into the Rusck equation:
3.13 | 3.13 | number of connections describes the behavior for a specific load type, independent of the number of connections. Thus, the equation for the simultaneity factor transforms into the Rusck equation: [
] | ] | of connections describes the behavior for a specific load type, independent of the number of connections. Thus, the equation for the simultaneity factor transforms into the Rusck equation: [ 3.13
Hierdoor kan de formule voor de maximale belasting ook geschreven worden als: | As a result, the formula for the maximum load can also be written as: | connections describes the behavior for a specific load type, independent of the number of connections. Thus, the equation for the simultaneity factor transforms into the Rusck equation: [ 3.13 ]
[ | [ | connections. Thus, the equation for the simultaneity factor transforms into the Rusck equation: [ 3.13 ] As a result, the formula for the maximum load can also be written as:
3.14 | 3.14 | Thus, the equation for the simultaneity factor transforms into the Rusck equation: [ 3.13 ] As a result, the formula for the maximum load can also be written as: [
] | ] | the equation for the simultaneity factor transforms into the Rusck equation: [ 3.13 ] As a result, the formula for the maximum load can also be written as: [ 3.14
Voor één aansluiting is | For one connection, it is | equation for the simultaneity factor transforms into the Rusck equation: [ 3.13 ] As a result, the formula for the maximum load can also be written as: [ 3.14 ]
n=1 | n=1 | transforms into the Rusck equation: [ 3.13 ] As a result, the formula for the maximum load can also be written as: [ 3.14 ] For one connection, it is
en is de gelijktijdigheidsfactor | and is the simultaneity factor | into the Rusck equation: [ 3.13 ] As a result, the formula for the maximum load can also be written as: [ 3.14 ] For one connection, it is n=1
g | g | 3.13 ] As a result, the formula for the maximum load can also be written as: [ 3.14 ] For one connection, it is n=1 and is the simultaneity factor
1 | 1 | ] As a result, the formula for the maximum load can also be written as: [ 3.14 ] For one connection, it is n=1 and is the simultaneity factor g
As a result, the formula for the maximum load can also be written as: [ 3.14 ] For one connection, it is n=1 and is the simultaneity factor g 1
. Voor een oneindig aantal aansluitingen geldt n | . For an infinite number of connections, n applies | a result, the formula for the maximum load can also be written as: [ 3.14 ] For one connection, it is n=1 and is the simultaneity factor g 1 =1
→∞ | →∞ | also be written as: [ 3.14 ] For one connection, it is n=1 and is the simultaneity factor g 1 =1 . For an infinite number of connections, n applies
en is | and is | be written as: [ 3.14 ] For one connection, it is n=1 and is the simultaneity factor g 1 =1 . For an infinite number of connections, n applies →∞
g | g | as: [ 3.14 ] For one connection, it is n=1 and is the simultaneity factor g 1 =1 . For an infinite number of connections, n applies →∞ and is
n | n | [ 3.14 ] For one connection, it is n=1 and is the simultaneity factor g 1 =1 . For an infinite number of connections, n applies →∞ and is g
3.14 ] For one connection, it is n=1 and is the simultaneity factor g 1 =1 . For an infinite number of connections, n applies →∞ and is g n
∞ | ∞ | ] For one connection, it is n=1 and is the simultaneity factor g 1 =1 . For an infinite number of connections, n applies →∞ and is g n =g
. In praktijk blijkt | . In practice, it appears | For one connection, it is n=1 and is the simultaneity factor g 1 =1 . For an infinite number of connections, n applies →∞ and is g n =g ∞
g | g | n=1 and is the simultaneity factor g 1 =1 . For an infinite number of connections, n applies →∞ and is g n =g ∞ . In practice, it appears
∞ | ∞ | and is the simultaneity factor g 1 =1 . For an infinite number of connections, n applies →∞ and is g n =g ∞ . In practice, it appears g
voor de meeste gevallen ongeveer gelijk te zijn aan | to be approximately equal for most cases to | is the simultaneity factor g 1 =1 . For an infinite number of connections, n applies →∞ and is g n =g ∞ . In practice, it appears g ∞
0,2 | 0.2 | For an infinite number of connections, n applies →∞ and is g n =g ∞ . In practice, it appears g ∞ to be approximately equal for most cases to
. In dat geval is de gelijk­tijdig­heidsfactor | . In that case, the simultaneity factor | an infinite number of connections, n applies →∞ and is g n =g ∞ . In practice, it appears g ∞ to be approximately equal for most cases to 0.2
g | g | →∞ and is g n =g ∞ . In practice, it appears g ∞ to be approximately equal for most cases to 0.2 . In that case, the simultaneity factor
n | n | and is g n =g ∞ . In practice, it appears g ∞ to be approximately equal for most cases to 0.2 . In that case, the simultaneity factor g
voor 80% evenredig met het omgekeerde van de wortel van het aantal verbruikers. | for 80% proportional to the inverse of the square root of the number of consumers. | is g n =g ∞ . In practice, it appears g ∞ to be approximately equal for most cases to 0.2 . In that case, the simultaneity factor g n
De gelijktijdigheidsfactor hangt sterk af van de homogeniteit van de belasting. Bij een sterk homogene belasting, zoals openbare verlichting, zal de factor ongeveer gelijk aan 1 zijn. Ook de omvang van het beschouwde netgedeelte heeft grote invloed op de waarde. | The simultaneity factor strongly depends on the homogeneity of the load. For a highly homogeneous load, such as public lighting, the factor will be approximately equal to 1. The size of the considered network segment also has a significant impact on the value. | equal for most cases to 0.2 . In that case, the simultaneity factor g n for 80% proportional to the inverse of the square root of the number of consumers.
De locatie van het beschouwde punt is van invloed op de ‘lokale’ diversiteit. In het algemeen zal dichter bij de voeding de lokale gelijktijdigheidsfactor groter zijn dan in een punt dat zich verder weg van de voeding bevindt. Dit komt doordat bij een groot aantal belastingen het willekeurige gedrag wordt ‘uitgemiddeld’. In een verder weg gelegen punt is het aantal aansluitingen kleiner, waardoor het totaal van de belastingen zich grilliger gedraagt. Figuur 3.14 illustreert dit. In knooppunt 1 is de lokale gelijktijdigheidsfactor voor een totaal van | The location of the considered point affects the 'local' diversity. In general, closer to the supply, the local simultaneity factor will be greater than at a point further away from the supply. This is because, with a large number of loads, the random behavior is 'averaged out.' At a point further away, the number of connections is smaller, causing the total loads to behave more erratically. Figure 3.14 illustrates this. In node 1, the local simultaneity factor for a total of | highly homogeneous load, such as public lighting, the factor will be approximately equal to 1. The size of the considered network segment also has a significant impact on the value.
n | n | away, the number of connections is smaller, causing the total loads to behave more erratically. Figure 3.14 illustrates this. In node 1, the local simultaneity factor for a total of
1 | 1 | the number of connections is smaller, causing the total loads to behave more erratically. Figure 3.14 illustrates this. In node 1, the local simultaneity factor for a total of n
aansluitingen gegeven door | connections given by | number of connections is smaller, causing the total loads to behave more erratically. Figure 3.14 illustrates this. In node 1, the local simultaneity factor for a total of n 1
g(n | g(n) | is smaller, causing the total loads to behave more erratically. Figure 3.14 illustrates this. In node 1, the local simultaneity factor for a total of n 1 connections given by
1 | 1 | smaller, causing the total loads to behave more erratically. Figure 3.14 illustrates this. In node 1, the local simultaneity factor for a total of n 1 connections given by g(n)
) | ) | causing the total loads to behave more erratically. Figure 3.14 illustrates this. In node 1, the local simultaneity factor for a total of n 1 connections given by g(n) 1
. Deze waarde is groter dan de lokale gelijktijdigheidsfactor op het verder weg gelegen knooppunt 2 met een totaal van | This value is greater than the local simultaneity factor at the more distant node 2 with a total of | the total loads to behave more erratically. Figure 3.14 illustrates this. In node 1, the local simultaneity factor for a total of n 1 connections given by g(n) 1 )
n | n | a total of n 1 connections given by g(n) 1 ) This value is greater than the local simultaneity factor at the more distant node 2 with a total of
2 | 2 | total of n 1 connections given by g(n) 1 ) This value is greater than the local simultaneity factor at the more distant node 2 with a total of n
aansluitingen. Hetzelfde geldt voor knooppunt 3. De totale gelijktijdigheidsfactor in knooppunt 1 voor alle | connections. The same applies to node 3. The total simultaneity factor in node 1 for all | of n 1 connections given by g(n) 1 ) This value is greater than the local simultaneity factor at the more distant node 2 with a total of n 2
n | n | simultaneity factor at the more distant node 2 with a total of n 2 connections. The same applies to node 3. The total simultaneity factor in node 1 for all
aansluitingen wordt berekend uit het product van alle achterliggende gelijktijdigheidsfactoren: | connections is calculated from the product of all underlying simultaneity factors: | factor at the more distant node 2 with a total of n 2 connections. The same applies to node 3. The total simultaneity factor in node 1 for all n
[ | [ | n 2 connections. The same applies to node 3. The total simultaneity factor in node 1 for all n connections is calculated from the product of all underlying simultaneity factors:
3.15 | 3.15 | 2 connections. The same applies to node 3. The total simultaneity factor in node 1 for all n connections is calculated from the product of all underlying simultaneity factors: [
] | ] | connections. The same applies to node 3. The total simultaneity factor in node 1 for all n connections is calculated from the product of all underlying simultaneity factors: [ 3.15
Figuur 3.14 Gelijktijdigheid op diverse locaties in een distributienet | Figure 3.14 Simultaneity at various locations in a distribution network | The same applies to node 3. The total simultaneity factor in node 1 for all n connections is calculated from the product of all underlying simultaneity factors: [ 3.15 ]
De maximale belasting voor | The maximum load for | in node 1 for all n connections is calculated from the product of all underlying simultaneity factors: [ 3.15 ] Figure 3.14 Simultaneity at various locations in a distribution network
n | n | all n connections is calculated from the product of all underlying simultaneity factors: [ 3.15 ] Figure 3.14 Simultaneity at various locations in a distribution network The maximum load for
gelijke aansluitingen wordt berekend uit de gelijktijdigheidsfactor en de maximale belasting voor één aansluiting: | equal connections is calculated from the simultaneity factor and the maximum load for one connection: | n connections is calculated from the product of all underlying simultaneity factors: [ 3.15 ] Figure 3.14 Simultaneity at various locations in a distribution network The maximum load for n
[ | [ | Figure 3.14 Simultaneity at various locations in a distribution network The maximum load for n equal connections is calculated from the simultaneity factor and the maximum load for one connection:
3.16 | 3.16 | 3.14 Simultaneity at various locations in a distribution network The maximum load for n equal connections is calculated from the simultaneity factor and the maximum load for one connection: [
] | ] | Simultaneity at various locations in a distribution network The maximum load for n equal connections is calculated from the simultaneity factor and the maximum load for one connection: [ 3.16
waarbij: | where: | at various locations in a distribution network The maximum load for n equal connections is calculated from the simultaneity factor and the maximum load for one connection: [ 3.16 ]
n | n | various locations in a distribution network The maximum load for n equal connections is calculated from the simultaneity factor and the maximum load for one connection: [ 3.16 ] where:
het aantal verbruikers | the number of consumers | locations in a distribution network The maximum load for n equal connections is calculated from the simultaneity factor and the maximum load for one connection: [ 3.16 ] where: n
P | P | network The maximum load for n equal connections is calculated from the simultaneity factor and the maximum load for one connection: [ 3.16 ] where: n the number of consumers
max,1 | max,1 | The maximum load for n equal connections is calculated from the simultaneity factor and the maximum load for one connection: [ 3.16 ] where: n the number of consumers P
maximale waarde van de belasting van één aansluiting | maximum value of the load of one connection | maximum load for n equal connections is calculated from the simultaneity factor and the maximum load for one connection: [ 3.16 ] where: n the number of consumers P max,1
g | g | from the simultaneity factor and the maximum load for one connection: [ 3.16 ] where: n the number of consumers P max,1 maximum value of the load of one connection
n | n | the simultaneity factor and the maximum load for one connection: [ 3.16 ] where: n the number of consumers P max,1 maximum value of the load of one connection g
gelijktijdigheidsfactor voor n aansluitingen | simultaneity factor for n connections | simultaneity factor and the maximum load for one connection: [ 3.16 ] where: n the number of consumers P max,1 maximum value of the load of one connection g n
3.5.3 Relatie tussen elektriciteitsverbruik en de maximale belasting | 3.5.3 Relationship between electricity consumption and maximum load | load for one connection: [ 3.16 ] where: n the number of consumers P max,1 maximum value of the load of one connection g n simultaneity factor for n connections
Het verbruik is de hoeveelheid elektrische energie die per tijdseenheid, meestal per jaar, wordt verbruikt. Het verbruik kan betrekking hebben op één aansluiting, of op een netdeel. Het verbruik | Consumption is the amount of electrical energy used per unit of time, usually per year. Consumption can pertain to a single connection or to a network segment. Consumption | n the number of consumers P max,1 maximum value of the load of one connection g n simultaneity factor for n connections 3.5.3 Relationship between electricity consumption and maximum load
V | V | maximum load Consumption is the amount of electrical energy used per unit of time, usually per year. Consumption can pertain to a single connection or to a network segment. Consumption
wordt gerepresenteerd in kWh/jaar. Voor de diverse belastingscategorieën is het verbruik per aansluiting in het algemeen beter bekend dan de maximale belasting per aansluiting. Voor het ontwerpen van een distributienet is een relatie nodig tussen verbruik en maximale belasting. Een van de mogelijkheden hiervoor is de bedrijfstijd van de maximale belasting. Deze is gedefinieerd als het quotiënt van het jaarverbruik en de maximale belasting in dat jaar. Hoe groter de diversiteit is, des te kleiner wordt de bedrijfstijd van het maximum. | is represented in kWh/year. For the various load categories, the consumption per connection is generally better known than the maximum load per connection. For designing a distribution network, a relationship between consumption and maximum load is needed. One of the possibilities for this is the operating time of the maximum load. This is defined as the quotient of the annual consumption and the maximum load in that year. The greater the diversity, the smaller the operating time of the maximum. | load Consumption is the amount of electrical energy used per unit of time, usually per year. Consumption can pertain to a single connection or to a network segment. Consumption V
[ | [ | load. This is defined as the quotient of the annual consumption and the maximum load in that year. The greater the diversity, the smaller the operating time of the maximum.
3.17 | 3.17 | This is defined as the quotient of the annual consumption and the maximum load in that year. The greater the diversity, the smaller the operating time of the maximum. [
] | ] | is defined as the quotient of the annual consumption and the maximum load in that year. The greater the diversity, the smaller the operating time of the maximum. [ 3.17
Om een gefundeerde uitspraak te kunnen doen over de maximale belasting van een belastingscategorie, heeft Velander in 1952 vanuit metingen deze relatie met het verbruik proefondervindelijk vastgesteld. Hierbij ging hij ervan uit dat de belastingen zich op een specifiek moment gedragen als onderling onafhankelijke stochastische variabelen. Deze relatie is later in 1975 gebruikt door Strand en Axelsson voor toepassing in een computersysteem dat het verbruik en de maximale belasting van een distributienet administreert. | To make a well-founded statement about the maximum load of a load category, Velander empirically established this relationship with consumption based on measurements in 1952. He assumed that the loads behave as mutually independent stochastic variables at a specific moment. This relationship was later used in 1975 by Strand and Axelsson for application in a computer system that manages the consumption and maximum load of a distribution network. | defined as the quotient of the annual consumption and the maximum load in that year. The greater the diversity, the smaller the operating time of the maximum. [ 3.17 ]
De relatie van Velander is geschikt voor het berekenen van de maximale belasting van belastingscategorieën. In combinatie met belastingsprognose zijn de modellen van Rusck en Velander de basis voor het ontwerpen van MS en LS-netten. | The Velander relationship is suitable for calculating the maximum load of load categories. In combination with load forecasting, the models of Rusck and Velander form the basis for designing medium voltage (MV) and low voltage (LV) networks. | specific moment. This relationship was later used in 1975 by Strand and Axelsson for application in a computer system that manages the consumption and maximum load of a distribution network.
De formule van Velander luidt (Velander, 1952; Strand-Axelsson, 1975 en EnergieNed, 1996): | The Velander formula is as follows (Velander, 1952; Strand-Axelsson, 1975, and EnergieNed, 1996): | the maximum load of load categories. In combination with load forecasting, the models of Rusck and Velander form the basis for designing medium voltage (MV) and low voltage (LV) networks.
[ | [ | of Rusck and Velander form the basis for designing medium voltage (MV) and low voltage (LV) networks. The Velander formula is as follows (Velander, 1952; Strand-Axelsson, 1975, and EnergieNed, 1996):
3.18 | 3.18 | Rusck and Velander form the basis for designing medium voltage (MV) and low voltage (LV) networks. The Velander formula is as follows (Velander, 1952; Strand-Axelsson, 1975, and EnergieNed, 1996): [
] | ] | and Velander form the basis for designing medium voltage (MV) and low voltage (LV) networks. The Velander formula is as follows (Velander, 1952; Strand-Axelsson, 1975, and EnergieNed, 1996): [ 3.18
waarbij: | where: | Velander form the basis for designing medium voltage (MV) and low voltage (LV) networks. The Velander formula is as follows (Velander, 1952; Strand-Axelsson, 1975, and EnergieNed, 1996): [ 3.18 ]
P | P | form the basis for designing medium voltage (MV) and low voltage (LV) networks. The Velander formula is as follows (Velander, 1952; Strand-Axelsson, 1975, and EnergieNed, 1996): [ 3.18 ] where:
max,n | max,n | the basis for designing medium voltage (MV) and low voltage (LV) networks. The Velander formula is as follows (Velander, 1952; Strand-Axelsson, 1975, and EnergieNed, 1996): [ 3.18 ] where: P
maximale belasting van | maximum load of | basis for designing medium voltage (MV) and low voltage (LV) networks. The Velander formula is as follows (Velander, 1952; Strand-Axelsson, 1975, and EnergieNed, 1996): [ 3.18 ] where: P max,n
n | n | medium voltage (MV) and low voltage (LV) networks. The Velander formula is as follows (Velander, 1952; Strand-Axelsson, 1975, and EnergieNed, 1996): [ 3.18 ] where: P max,n maximum load of
aansluitingen (kW) | connections (kW) | voltage (MV) and low voltage (LV) networks. The Velander formula is as follows (Velander, 1952; Strand-Axelsson, 1975, and EnergieNed, 1996): [ 3.18 ] where: P max,n maximum load of n
V | V | and low voltage (LV) networks. The Velander formula is as follows (Velander, 1952; Strand-Axelsson, 1975, and EnergieNed, 1996): [ 3.18 ] where: P max,n maximum load of n connections (kW)
jaarverbruik van | annual consumption of | low voltage (LV) networks. The Velander formula is as follows (Velander, 1952; Strand-Axelsson, 1975, and EnergieNed, 1996): [ 3.18 ] where: P max,n maximum load of n connections (kW) V
n | n | networks. The Velander formula is as follows (Velander, 1952; Strand-Axelsson, 1975, and EnergieNed, 1996): [ 3.18 ] where: P max,n maximum load of n connections (kW) V annual consumption of
aansluitingen (kWh/jaar) | connections (kWh/year) | The Velander formula is as follows (Velander, 1952; Strand-Axelsson, 1975, and EnergieNed, 1996): [ 3.18 ] where: P max,n maximum load of n connections (kW) V annual consumption of n
α, β | α, β | formula is as follows (Velander, 1952; Strand-Axelsson, 1975, and EnergieNed, 1996): [ 3.18 ] where: P max,n maximum load of n connections (kW) V annual consumption of n connections (kWh/year)
door meting vast te stellen parameters | parameters determined by measurement | as follows (Velander, 1952; Strand-Axelsson, 1975, and EnergieNed, 1996): [ 3.18 ] where: P max,n maximum load of n connections (kW) V annual consumption of n connections (kWh/year) α, β
De parameters | The parameters | Strand-Axelsson, 1975, and EnergieNed, 1996): [ 3.18 ] where: P max,n maximum load of n connections (kW) V annual consumption of n connections (kWh/year) α, β parameters determined by measurement
α, β | α, β | and EnergieNed, 1996): [ 3.18 ] where: P max,n maximum load of n connections (kW) V annual consumption of n connections (kWh/year) α, β parameters determined by measurement The parameters
en | en | 1996): [ 3.18 ] where: P max,n maximum load of n connections (kW) V annual consumption of n connections (kWh/year) α, β parameters determined by measurement The parameters α, β
V | V | [ 3.18 ] where: P max,n maximum load of n connections (kW) V annual consumption of n connections (kWh/year) α, β parameters determined by measurement The parameters α, β en
beschrijven de belastingscategorie. Deze parameters zijn afhankelijk van: | describe the load category. These parameters depend on: | 3.18 ] where: P max,n maximum load of n connections (kW) V annual consumption of n connections (kWh/year) α, β parameters determined by measurement The parameters α, β en V
de aard van het gebied | the nature of the area | n connections (kW) V annual consumption of n connections (kWh/year) α, β parameters determined by measurement The parameters α, β en V describe the load category. These parameters depend on:
het type aansluitingen | the type of connections | consumption of n connections (kWh/year) α, β parameters determined by measurement The parameters α, β en V describe the load category. These parameters depend on: the nature of the area
het aantal aansluitingen | the number of connections | (kWh/year) α, β parameters determined by measurement The parameters α, β en V describe the load category. These parameters depend on: the nature of the area the type of connections
Door de formule van Velander (3.18) te delen door het aantal aansluitingen volgt de equivalente gelijktijdige maximale belasting per aansluiting op een willekeurige plaats in het beschouwde netdeel, waar | By dividing Velander's formula (3.18) by the number of connections, the equivalent simultaneous maximum load per connection at any given location in the considered network section is obtained, where | determined by measurement The parameters α, β en V describe the load category. These parameters depend on: the nature of the area the type of connections the number of connections
n | n | connections By dividing Velander's formula (3.18) by the number of connections, the equivalent simultaneous maximum load per connection at any given location in the considered network section is obtained, where
gelijksoortige aansluitingen aanwezig zijn. | similar connections are present. | By dividing Velander's formula (3.18) by the number of connections, the equivalent simultaneous maximum load per connection at any given location in the considered network section is obtained, where n
[ | [ | (3.18) by the number of connections, the equivalent simultaneous maximum load per connection at any given location in the considered network section is obtained, where n similar connections are present.
3.19 | 3.19 | by the number of connections, the equivalent simultaneous maximum load per connection at any given location in the considered network section is obtained, where n similar connections are present. [
] | ] | the number of connections, the equivalent simultaneous maximum load per connection at any given location in the considered network section is obtained, where n similar connections are present. [ 3.19
Met de equivalente gelijktijdige maximale belasting per aansluiting wordt als het ware de gelijktijdig maximale belasting van een netdeel verdeeld over alle individuele aansluitingen. De waarde van | With the equivalent simultaneous maximum load per connection, the simultaneous maximum load of a network section is essentially distributed over all individual connections. The value of | number of connections, the equivalent simultaneous maximum load per connection at any given location in the considered network section is obtained, where n similar connections are present. [ 3.19 ]
P | P | present. [ 3.19 ] With the equivalent simultaneous maximum load per connection, the simultaneous maximum load of a network section is essentially distributed over all individual connections. The value of
max,eq | max,eq | [ 3.19 ] With the equivalent simultaneous maximum load per connection, the simultaneous maximum load of a network section is essentially distributed over all individual connections. The value of P
neemt af bij een toenemend aantal aansluitingen. Het minder grillige gedrag van het belastingspatroon in de buurt van de voedingspunten van een netdeel ten opzichte van de individuele aansluitingen is merkbaar doordat in het tweede gedeelte van de vergelijking gedeeld wordt door | decreases with an increasing number of connections. The less erratic behavior of the load pattern near the supply points of a network section compared to the individual connections is noticeable because in the second part of the equation, it is divided by | 3.19 ] With the equivalent simultaneous maximum load per connection, the simultaneous maximum load of a network section is essentially distributed over all individual connections. The value of P max,eq
√n | √n | the load pattern near the supply points of a network section compared to the individual connections is noticeable because in the second part of the equation, it is divided by
. Voor een oneindig aantal aansluitingen is de equivalente gelijktijdig maximale belasting per aansluiting gelijk aan | . For an infinite number of connections, the equivalent simultaneous maximum load per connection is equal to | load pattern near the supply points of a network section compared to the individual connections is noticeable because in the second part of the equation, it is divided by √n
α·V | α·V | because in the second part of the equation, it is divided by √n . For an infinite number of connections, the equivalent simultaneous maximum load per connection is equal to
1 | 1 | in the second part of the equation, it is divided by √n . For an infinite number of connections, the equivalent simultaneous maximum load per connection is equal to α·V
. Figuur 3.15 illustreert dit. In de grafiek zijn twee curves afgebeeld voor een verbruik van 4300 kWh/jaar en 2300 kWh/jaar. De gebruikte parameters zijn: | Figure 3.15 illustrates this. The graph shows two curves for a consumption of 4300 kWh/year and 2300 kWh/year. The parameters used are: | the second part of the equation, it is divided by √n . For an infinite number of connections, the equivalent simultaneous maximum load per connection is equal to α·V 1
α = 0,23·10 | α = 0.23·10 | load per connection is equal to α·V 1 Figure 3.15 illustrates this. The graph shows two curves for a consumption of 4300 kWh/year and 2300 kWh/year. The parameters used are:
-3 | -3 | is equal to α·V 1 Figure 3.15 illustrates this. The graph shows two curves for a consumption of 4300 kWh/year and 2300 kWh/year. The parameters used are: α = 0.23·10
β = 0,016 | β = 0.016 | equal to α·V 1 Figure 3.15 illustrates this. The graph shows two curves for a consumption of 4300 kWh/year and 2300 kWh/year. The parameters used are: α = 0.23·10 -3
Figuur 3.15 Equivalente gelijktijdig maximale belasting per aansluiting | Figure 3.15 Equivalent simultaneous maximum load per connection | 1 Figure 3.15 illustrates this. The graph shows two curves for a consumption of 4300 kWh/year and 2300 kWh/year. The parameters used are: α = 0.23·10 -3 β = 0.016
Door uit te gaan van het specifieke verbruik van één aansluiting kan met de parameters α en β de gelijktijdig maximale belasting voor | By considering the specific consumption of one connection, the simultaneous maximum load can be determined using the parameters α and β. | two curves for a consumption of 4300 kWh/year and 2300 kWh/year. The parameters used are: α = 0.23·10 -3 β = 0.016 Figure 3.15 Equivalent simultaneous maximum load per connection
n | n | 0.016 Figure 3.15 Equivalent simultaneous maximum load per connection By considering the specific consumption of one connection, the simultaneous maximum load can be determined using the parameters α and β.
aansluitingen worden berekend. | connections are calculated. | Figure 3.15 Equivalent simultaneous maximum load per connection By considering the specific consumption of one connection, the simultaneous maximum load can be determined using the parameters α and β. n
[ | [ | simultaneous maximum load per connection By considering the specific consumption of one connection, the simultaneous maximum load can be determined using the parameters α and β. n connections are calculated.
3.20 | 3.20 | maximum load per connection By considering the specific consumption of one connection, the simultaneous maximum load can be determined using the parameters α and β. n connections are calculated. [
] | ] | load per connection By considering the specific consumption of one connection, the simultaneous maximum load can be determined using the parameters α and β. n connections are calculated. [ 3.20
Door vergelijking 3.20 te combineren met de formules van Rusck (3.6 tot en met 3.14) volgen onderstaande relaties. | By combining equation 3.20 with Rusck's formulas (3.6 through 3.14), the following relationships are derived. | per connection By considering the specific consumption of one connection, the simultaneous maximum load can be determined using the parameters α and β. n connections are calculated. [ 3.20 ]
[ | [ | be determined using the parameters α and β. n connections are calculated. [ 3.20 ] By combining equation 3.20 with Rusck's formulas (3.6 through 3.14), the following relationships are derived.
3.21 | 3.21 | determined using the parameters α and β. n connections are calculated. [ 3.20 ] By combining equation 3.20 with Rusck's formulas (3.6 through 3.14), the following relationships are derived. [
] | ] | using the parameters α and β. n connections are calculated. [ 3.20 ] By combining equation 3.20 with Rusck's formulas (3.6 through 3.14), the following relationships are derived. [ 3.21
[ | [ | the parameters α and β. n connections are calculated. [ 3.20 ] By combining equation 3.20 with Rusck's formulas (3.6 through 3.14), the following relationships are derived. [ 3.21 ]
3.22 | 3.22 | parameters α and β. n connections are calculated. [ 3.20 ] By combining equation 3.20 with Rusck's formulas (3.6 through 3.14), the following relationships are derived. [ 3.21 ] [
] | ] | α and β. n connections are calculated. [ 3.20 ] By combining equation 3.20 with Rusck's formulas (3.6 through 3.14), the following relationships are derived. [ 3.21 ] [ 3.22
Met deze relaties kunnen de parameters α en β vastgesteld worden indien van de aansluitingscategorie het jaarverbruik en het gemiddelde en maximum vermogen per aansluiting bekend zijn. Hierbij moet worden opgemerkt dat het gemiddelde vermogen | With these relationships, the parameters α and β can be determined if the annual consumption and the average and maximum power per connection of the connection category are known. It should be noted that the average power | and β. n connections are calculated. [ 3.20 ] By combining equation 3.20 with Rusck's formulas (3.6 through 3.14), the following relationships are derived. [ 3.21 ] [ 3.22 ]
P | P | β can be determined if the annual consumption and the average and maximum power per connection of the connection category are known. It should be noted that the average power
gem,1 | avg,1 | can be determined if the annual consumption and the average and maximum power per connection of the connection category are known. It should be noted that the average power P
niet gelijk is aan het jaarverbruik gedeeld door het aantal uren in het jaar. Zoals in de vorige paragraaf opgemerkt, gedraagt de belasting zich over een heel etmaal niet als een normaal verdeelde stochastische variabele. Daarom heeft | is not equal to the annual consumption divided by the number of hours in the year. As noted in the previous paragraph, the load does not behave as a normally distributed stochastic variable over a full day. Therefore, | be determined if the annual consumption and the average and maximum power per connection of the connection category are known. It should be noted that the average power P avg,1
P | P | by the number of hours in the year. As noted in the previous paragraph, the load does not behave as a normally distributed stochastic variable over a full day. Therefore,
gem,1 | average,1 | the number of hours in the year. As noted in the previous paragraph, the load does not behave as a normally distributed stochastic variable over a full day. Therefore, P
de gemiddelde waarde van de stochastische variabele die in het beschouwde tijdvenster wel als normaal verdeeld mag worden verondersteld. Dit is de gemiddelde waarde tijdens de piekbelasting. | the average value of the stochastic variable that can be assumed to be normally distributed within the considered time window. This is the average value during peak load. | number of hours in the year. As noted in the previous paragraph, the load does not behave as a normally distributed stochastic variable over a full day. Therefore, P average,1
Indien van een type gebruiker het jaarverbruik voor één aansluiting | If the annual consumption for one connection of a type of user | P average,1 the average value of the stochastic variable that can be assumed to be normally distributed within the considered time window. This is the average value during peak load.
V | V | assumed to be normally distributed within the considered time window. This is the average value during peak load. If the annual consumption for one connection of a type of user
1 | 1 | to be normally distributed within the considered time window. This is the average value during peak load. If the annual consumption for one connection of a type of user V
, de bedrijfstijd | , the operating time | be normally distributed within the considered time window. This is the average value during peak load. If the annual consumption for one connection of a type of user V 1
T | T | the considered time window. This is the average value during peak load. If the annual consumption for one connection of a type of user V 1 , the operating time
1 | 1 | considered time window. This is the average value during peak load. If the annual consumption for one connection of a type of user V 1 , the operating time T
en de gelijktijdigheidfactor voor een oneindig aantal gebruikers | and the simultaneity factor for an infinite number of users | time window. This is the average value during peak load. If the annual consumption for one connection of a type of user V 1 , the operating time T 1
g | g | If the annual consumption for one connection of a type of user V 1 , the operating time T 1 and the simultaneity factor for an infinite number of users
∞ | ∞ | the annual consumption for one connection of a type of user V 1 , the operating time T 1 and the simultaneity factor for an infinite number of users g
bekend zijn, kunnen de parameters | are known, the parameters can | annual consumption for one connection of a type of user V 1 , the operating time T 1 and the simultaneity factor for an infinite number of users g ∞
α | α | of a type of user V 1 , the operating time T 1 and the simultaneity factor for an infinite number of users g ∞ are known, the parameters can
en | en | a type of user V 1 , the operating time T 1 and the simultaneity factor for an infinite number of users g ∞ are known, the parameters can α
β | beta | type of user V 1 , the operating time T 1 and the simultaneity factor for an infinite number of users g ∞ are known, the parameters can α en
vastgesteld worden. De maximale belasting voor één aansluiting | can be determined. The maximum load for a single connection | of user V 1 , the operating time T 1 and the simultaneity factor for an infinite number of users g ∞ are known, the parameters can α en beta
P | P | and the simultaneity factor for an infinite number of users g ∞ are known, the parameters can α en beta can be determined. The maximum load for a single connection
max,1 | max,1 | the simultaneity factor for an infinite number of users g ∞ are known, the parameters can α en beta can be determined. The maximum load for a single connection P
volgt uit de definitie van de bedrijfstijd en de gemiddelde belasting kan volgens Rusck worden berekend uit de gelijktijdigheidfactor en de gemiddelde belasting: | follows from the definition of operating time and the average load can, according to Rusck, be calculated from the simultaneity factor and the average load: | simultaneity factor for an infinite number of users g ∞ are known, the parameters can α en beta can be determined. The maximum load for a single connection P max,1
[ | [ | a single connection P max,1 follows from the definition of operating time and the average load can, according to Rusck, be calculated from the simultaneity factor and the average load:
3.23 | 3.23 | single connection P max,1 follows from the definition of operating time and the average load can, according to Rusck, be calculated from the simultaneity factor and the average load: [
] | ] | connection P max,1 follows from the definition of operating time and the average load can, according to Rusck, be calculated from the simultaneity factor and the average load: [ 3.23
De waarde van | The value of | P max,1 follows from the definition of operating time and the average load can, according to Rusck, be calculated from the simultaneity factor and the average load: [ 3.23 ]
g | g | from the definition of operating time and the average load can, according to Rusck, be calculated from the simultaneity factor and the average load: [ 3.23 ] The value of
∞ | ∞ | the definition of operating time and the average load can, according to Rusck, be calculated from the simultaneity factor and the average load: [ 3.23 ] The value of g
kan volgens Rusck worden afgeleid uit de gelijktijdigheid van | can, according to Rusck, be derived from the simultaneity of | definition of operating time and the average load can, according to Rusck, be calculated from the simultaneity factor and the average load: [ 3.23 ] The value of g ∞
n | n | to Rusck, be calculated from the simultaneity factor and the average load: [ 3.23 ] The value of g ∞ can, according to Rusck, be derived from the simultaneity of
gebruikers: | users: | Rusck, be calculated from the simultaneity factor and the average load: [ 3.23 ] The value of g ∞ can, according to Rusck, be derived from the simultaneity of n
[ | [ | be calculated from the simultaneity factor and the average load: [ 3.23 ] The value of g ∞ can, according to Rusck, be derived from the simultaneity of n users:
3.24 | 3.24 | calculated from the simultaneity factor and the average load: [ 3.23 ] The value of g ∞ can, according to Rusck, be derived from the simultaneity of n users: [
] | ] | from the simultaneity factor and the average load: [ 3.23 ] The value of g ∞ can, according to Rusck, be derived from the simultaneity of n users: [ 3.24
Door deze vergelijkingen in te vullen in de formules die de relaties tussen Velander en Rusck beschrijven, kunnen de parameters α en β vastgesteld worden. | By substituting these equations into the formulas that describe the relationships between Velander and Rusck, the parameters α and β can be determined. | the simultaneity factor and the average load: [ 3.23 ] The value of g ∞ can, according to Rusck, be derived from the simultaneity of n users: [ 3.24 ]
[ | [ | simultaneity of n users: [ 3.24 ] By substituting these equations into the formulas that describe the relationships between Velander and Rusck, the parameters α and β can be determined.
3.25 | 3.25 | of n users: [ 3.24 ] By substituting these equations into the formulas that describe the relationships between Velander and Rusck, the parameters α and β can be determined. [
] | ] | n users: [ 3.24 ] By substituting these equations into the formulas that describe the relationships between Velander and Rusck, the parameters α and β can be determined. [ 3.25
[ | [ | users: [ 3.24 ] By substituting these equations into the formulas that describe the relationships between Velander and Rusck, the parameters α and β can be determined. [ 3.25 ]
3.26 | 3.26 | [ 3.24 ] By substituting these equations into the formulas that describe the relationships between Velander and Rusck, the parameters α and β can be determined. [ 3.25 ] [
] | ] | 3.24 ] By substituting these equations into the formulas that describe the relationships between Velander and Rusck, the parameters α and β can be determined. [ 3.25 ] [ 3.26
Omgekeerd kunnen de stochastische parameters uit de parameters van Velander worden bepaald. Door de vergelijking van Velander te combineren met de formules van Rusck volgen onderstaande relaties. De gemiddelde waarde van de stochastische belasting volgt uit: | Conversely, the stochastic parameters can be determined from Velander's parameters. By combining Velander's equation with Rusck's formulas, the following relationships are obtained. The average value of the stochastic load is derived from: | ] By substituting these equations into the formulas that describe the relationships between Velander and Rusck, the parameters α and β can be determined. [ 3.25 ] [ 3.26 ]
[ | [ | stochastic parameters can be determined from Velander's parameters. By combining Velander's equation with Rusck's formulas, the following relationships are obtained. The average value of the stochastic load is derived from:
3.27 | 3.27 | parameters can be determined from Velander's parameters. By combining Velander's equation with Rusck's formulas, the following relationships are obtained. The average value of the stochastic load is derived from: [
] | ] | can be determined from Velander's parameters. By combining Velander's equation with Rusck's formulas, the following relationships are obtained. The average value of the stochastic load is derived from: [ 3.27
De spreiding van de stochastische belasting wordt hierna berekend met: | The spread of the stochastic load is subsequently calculated with: | be determined from Velander's parameters. By combining Velander's equation with Rusck's formulas, the following relationships are obtained. The average value of the stochastic load is derived from: [ 3.27 ]
[ | [ | Rusck's formulas, the following relationships are obtained. The average value of the stochastic load is derived from: [ 3.27 ] The spread of the stochastic load is subsequently calculated with:
3.28 | 3.28 | formulas, the following relationships are obtained. The average value of the stochastic load is derived from: [ 3.27 ] The spread of the stochastic load is subsequently calculated with: [
] | ] | the following relationships are obtained. The average value of the stochastic load is derived from: [ 3.27 ] The spread of the stochastic load is subsequently calculated with: [ 3.28
Een aspect als variatie van de belasting kan eenvoudig worden meegenomen in de patronen van de gemiddelden. De spreiding moet wel altijd in de pas blijven met de gemiddelde waarde. Hulpmiddel hiervoor is de constante | An aspect such as load variation can easily be incorporated into the patterns of the averages. However, the spread must always stay in line with the average value. A tool for this is the constant. | following relationships are obtained. The average value of the stochastic load is derived from: [ 3.27 ] The spread of the stochastic load is subsequently calculated with: [ 3.28 ]
C | C | variation can easily be incorporated into the patterns of the averages. However, the spread must always stay in line with the average value. A tool for this is the constant.
. Bij toename van de belasting, zonder dat het aantal aansluitingen toeneemt, moet de spreiding evenredig toenemen. | With an increase in load, without an increase in the number of connections, the spread must increase proportionally. | can easily be incorporated into the patterns of the averages. However, the spread must always stay in line with the average value. A tool for this is the constant. C
Figuur 3.16 Kansverdelingen voor de belasting als stochastische variabele bij C=1, 2 en 3 | Figure 3.16 Probability distributions for the load as a stochastic variable at C=1, 2, and 3 | with the average value. A tool for this is the constant. C With an increase in load, without an increase in the number of connections, the spread must increase proportionally.
De factor C is maatgevend voor de kans dat in het model de stochastische belasting groter is dan de maximale belasting | The factor C is decisive for the probability that in the model the stochastic load is greater than the maximum load. | load, without an increase in the number of connections, the spread must increase proportionally. Figure 3.16 Probability distributions for the load as a stochastic variable at C=1, 2, and 3
P | P | as a stochastic variable at C=1, 2, and 3 The factor C is decisive for the probability that in the model the stochastic load is greater than the maximum load.
max | max | a stochastic variable at C=1, 2, and 3 The factor C is decisive for the probability that in the model the stochastic load is greater than the maximum load. P
. Met een waarde voor de constante | . With a value for the constant | stochastic variable at C=1, 2, and 3 The factor C is decisive for the probability that in the model the stochastic load is greater than the maximum load. P max
C | C | The factor C is decisive for the probability that in the model the stochastic load is greater than the maximum load. P max . With a value for the constant
gelijk aan 1 wordt de maximale waarde van de belasting bepaald door | equal to 1, the maximum value of the load is determined by | factor C is decisive for the probability that in the model the stochastic load is greater than the maximum load. P max . With a value for the constant C
μ+1·σ | μ+1·σ | stochastic load is greater than the maximum load. P max . With a value for the constant C equal to 1, the maximum value of the load is determined by
. Door de eigenschappen van de normale verdeling zal het werkelijke maximum zich met ongeveer 85% zekerheid onder deze | Due to the properties of the normal distribution, the actual maximum will be below this value with approximately 85% certainty. | load is greater than the maximum load. P max . With a value for the constant C equal to 1, the maximum value of the load is determined by μ+1·σ
μ+1·σ | μ+1·σ | the maximum value of the load is determined by μ+1·σ Due to the properties of the normal distribution, the actual maximum will be below this value with approximately 85% certainty.
waarde bevinden. Indien de constante | value. If the constant | maximum value of the load is determined by μ+1·σ Due to the properties of the normal distribution, the actual maximum will be below this value with approximately 85% certainty. μ+1·σ
C | C | load is determined by μ+1·σ Due to the properties of the normal distribution, the actual maximum will be below this value with approximately 85% certainty. μ+1·σ value. If the constant
gelijk genomen wordt aan 2, zal het werkelijke maximum zich met ongeveer 97,5% zekerheid onder deze | is taken to be 2, the actual maximum will be below this value with approximately 97.5% certainty. | is determined by μ+1·σ Due to the properties of the normal distribution, the actual maximum will be below this value with approximately 85% certainty. μ+1·σ value. If the constant C
μ+2·σ | μ+2·σ | below this value with approximately 85% certainty. μ+1·σ value. If the constant C is taken to be 2, the actual maximum will be below this value with approximately 97.5% certainty.
waarde bevinden. De parameter s1 is afhankelijk van de keuze voor C. Hieronder is de kansverdeling weergegeven voor respectievelijk C = 1, 2 en 3. In figuur 3.16 is in de grafieken met een verticale lijn de waarde van | value. The parameter s1 depends on the choice of C. Below, the probability distribution is shown for C = 1, 2, and 3, respectively. In figure 3.16, the value is indicated in the graphs with a vertical line. | this value with approximately 85% certainty. μ+1·σ value. If the constant C is taken to be 2, the actual maximum will be below this value with approximately 97.5% certainty. μ+2·σ
P | P | of C. Below, the probability distribution is shown for C = 1, 2, and 3, respectively. In figure 3.16, the value is indicated in the graphs with a vertical line.
max,1 | max,1 | C. Below, the probability distribution is shown for C = 1, 2, and 3, respectively. In figure 3.16, the value is indicated in the graphs with a vertical line. P
aangegeven. Bij het berekenen van de kansverdelingen is uitgegaan van: | indicated. When calculating the probability distributions, the following assumptions were made: | Below, the probability distribution is shown for C = 1, 2, and 3, respectively. In figure 3.16, the value is indicated in the graphs with a vertical line. P max,1
α = 0,23·10 | α = 0.23·10 | and 3, respectively. In figure 3.16, the value is indicated in the graphs with a vertical line. P max,1 indicated. When calculating the probability distributions, the following assumptions were made:
-3 | -3 | In figure 3.16, the value is indicated in the graphs with a vertical line. P max,1 indicated. When calculating the probability distributions, the following assumptions were made: α = 0.23·10
β = 0,023 | β = 0.023 | figure 3.16, the value is indicated in the graphs with a vertical line. P max,1 indicated. When calculating the probability distributions, the following assumptions were made: α = 0.23·10 -3
V | V | value is indicated in the graphs with a vertical line. P max,1 indicated. When calculating the probability distributions, the following assumptions were made: α = 0.23·10 -3 β = 0.023
1 | 1 | is indicated in the graphs with a vertical line. P max,1 indicated. When calculating the probability distributions, the following assumptions were made: α = 0.23·10 -3 β = 0.023 V
indicated in the graphs with a vertical line. P max,1 indicated. When calculating the probability distributions, the following assumptions were made: α = 0.23·10 -3 β = 0.023 V 1
P | P | graphs with a vertical line. P max,1 indicated. When calculating the probability distributions, the following assumptions were made: α = 0.23·10 -3 β = 0.023 V 1 = 4500 kWh/year
gem,1 | avg,1 | with a vertical line. P max,1 indicated. When calculating the probability distributions, the following assumptions were made: α = 0.23·10 -3 β = 0.023 V 1 = 4500 kWh/year P
a vertical line. P max,1 indicated. When calculating the probability distributions, the following assumptions were made: α = 0.23·10 -3 β = 0.023 V 1 = 4500 kWh/year P avg,1
1 | 1 | line. P max,1 indicated. When calculating the probability distributions, the following assumptions were made: α = 0.23·10 -3 β = 0.023 V 1 = 4500 kWh/year P avg,1 = α·V
P max,1 indicated. When calculating the probability distributions, the following assumptions were made: α = 0.23·10 -3 β = 0.023 V 1 = 4500 kWh/year P avg,1 = α·V 1
P | P | When calculating the probability distributions, the following assumptions were made: α = 0.23·10 -3 β = 0.023 V 1 = 4500 kWh/year P avg,1 = α·V 1 = 1.04 kW
max,1 | max,1 | calculating the probability distributions, the following assumptions were made: α = 0.23·10 -3 β = 0.023 V 1 = 4500 kWh/year P avg,1 = α·V 1 = 1.04 kW P
the probability distributions, the following assumptions were made: α = 0.23·10 -3 β = 0.023 V 1 = 4500 kWh/year P avg,1 = α·V 1 = 1.04 kW P max,1
1 | 1 | distributions, the following assumptions were made: α = 0.23·10 -3 β = 0.023 V 1 = 4500 kWh/year P avg,1 = α·V 1 = 1.04 kW P max,1 = α·V
+ | + | the following assumptions were made: α = 0.23·10 -3 β = 0.023 V 1 = 4500 kWh/year P avg,1 = α·V 1 = 1.04 kW P max,1 = α·V 1
b | b | following assumptions were made: α = 0.23·10 -3 β = 0.023 V 1 = 4500 kWh/year P avg,1 = α·V 1 = 1.04 kW P max,1 = α·V 1 +
·√V | ·√V | assumptions were made: α = 0.23·10 -3 β = 0.023 V 1 = 4500 kWh/year P avg,1 = α·V 1 = 1.04 kW P max,1 = α·V 1 + b
1 | 1 | were made: α = 0.23·10 -3 β = 0.023 V 1 = 4500 kWh/year P avg,1 = α·V 1 = 1.04 kW P max,1 = α·V 1 + b ·√V
made: α = 0.23·10 -3 β = 0.023 V 1 = 4500 kWh/year P avg,1 = α·V 1 = 1.04 kW P max,1 = α·V 1 + b ·√V 1
g | g | 0.23·10 -3 β = 0.023 V 1 = 4500 kWh/year P avg,1 = α·V 1 = 1.04 kW P max,1 = α·V 1 + b ·√V 1 = 2.6 kW
∞ | ∞ | -3 β = 0.023 V 1 = 4500 kWh/year P avg,1 = α·V 1 = 1.04 kW P max,1 = α·V 1 + b ·√V 1 = 2.6 kW g
β = 0.023 V 1 = 4500 kWh/year P avg,1 = α·V 1 = 1.04 kW P max,1 = α·V 1 + b ·√V 1 = 2.6 kW g ∞
gem,1 | avg,1 | 0.023 V 1 = 4500 kWh/year P avg,1 = α·V 1 = 1.04 kW P max,1 = α·V 1 + b ·√V 1 = 2.6 kW g ∞ = P
/P | /P | V 1 = 4500 kWh/year P avg,1 = α·V 1 = 1.04 kW P max,1 = α·V 1 + b ·√V 1 = 2.6 kW g ∞ = P avg,1
max,1 | max,1 | 1 = 4500 kWh/year P avg,1 = α·V 1 = 1.04 kW P max,1 = α·V 1 + b ·√V 1 = 2.6 kW g ∞ = P avg,1 /P
C·σ | C·σ | kWh/year P avg,1 = α·V 1 = 1.04 kW P max,1 = α·V 1 + b ·√V 1 = 2.6 kW g ∞ = P avg,1 /P max,1 = 0.4
1 | 1 | P avg,1 = α·V 1 = 1.04 kW P max,1 = α·V 1 + b ·√V 1 = 2.6 kW g ∞ = P avg,1 /P max,1 = 0.4 C·σ
avg,1 = α·V 1 = 1.04 kW P max,1 = α·V 1 + b ·√V 1 = 2.6 kW g ∞ = P avg,1 /P max,1 = 0.4 C·σ 1
max,1 | max,1
– P | – P | α·V 1 = 1.04 kW P max,1 = α·V 1 + b ·√V 1 = 2.6 kW g ∞ = P avg,1 /P max,1 = 0.4 C·σ 1 =P max,1
gem,1 | avg,1
1.04 kW P max,1 = α·V 1 + b ·√V 1 = 2.6 kW g ∞ = P avg,1 /P max,1 = 0.4 C·σ 1 =P max,1 – P avg,1
C = 3 | C = 3 | P max,1 = α·V 1 + b ·√V 1 = 2.6 kW g ∞ = P avg,1 /P max,1 = 0.4 C·σ 1 =P max,1 – P avg,1 =1.54 kW
σ | sigma | α·V 1 + b ·√V 1 = 2.6 kW g ∞ = P avg,1 /P max,1 = 0.4 C·σ 1 =P max,1 – P avg,1 =1.54 kW C = 3
1 | 1 | 1 + b ·√V 1 = 2.6 kW g ∞ = P avg,1 /P max,1 = 0.4 C·σ 1 =P max,1 – P avg,1 =1.54 kW C = 3 sigma
+ b ·√V 1 = 2.6 kW g ∞ = P avg,1 /P max,1 = 0.4 C·σ 1 =P max,1 – P avg,1 =1.54 kW C = 3 sigma 1
De grafieken in figuur 3.16 illustreren dat de spreiding omgekeerd evenredig is met de constante | The graphs in figure 3.16 illustrate that the dispersion is inversely proportional to the constant. | 1 = 2.6 kW g ∞ = P avg,1 /P max,1 = 0.4 C·σ 1 =P max,1 – P avg,1 =1.54 kW C = 3 sigma 1 = 0.51 kW
C | C
. Zie ook figuur 3.10. Met een kleine waarde van | . See also figure 3.10. With a small value of | max,1 – P avg,1 =1.54 kW C = 3 sigma 1 = 0.51 kW The graphs in figure 3.16 illustrate that the dispersion is inversely proportional to the constant. C
C | C | 1 = 0.51 kW The graphs in figure 3.16 illustrate that the dispersion is inversely proportional to the constant. C . See also figure 3.10. With a small value of
worden de met deze kansverdeling te berekenen extremen groter. Hiermee moet bij de interpretatie van de resultaten rekening worden gehouden. | the extremes calculated with this probability distribution become larger. This must be taken into account when interpreting the results.
Voor het plannen wordt gebruik gemaakt van gemiddelde patronen met een relatief kleine spreiding. Terug­rekenend naar enkelvoudige verbruikers verandert de vorm van het gemiddelde patroon niet, maar wordt de bijbehorende spreiding relatief groter. Deze methode houdt geen rekening met individuele extreme uitschieters. In dat geval zou namelijk de oude methode van rekenen met maximale waarden beter van pas komen. | For planning, average patterns with a relatively small spread are used. When recalculating for individual consumers, the shape of the average pattern does not change, but the associated spread becomes relatively larger. This method does not account for individual extreme outliers. In that case, the old method of calculating with maximum values would be more suitable. | . See also figure 3.10. With a small value of C the extremes calculated with this probability distribution become larger. This must be taken into account when interpreting the results.
3.5.4 Vaststellen van de parameters voor korte termijnvariaties met behulp van metingen | 3.5.4 Determining the parameters for short-term variations using measurements | the associated spread becomes relatively larger. This method does not account for individual extreme outliers. In that case, the old method of calculating with maximum values would be more suitable.
De relatie tussen het verbruik en de maximale belasting van een gelijksoortige groep aansluitingen wordt beschreven met de formule van Velander (vergelijking 3.18). Deze formule maakt gebruik van twee parameters α en β, die aan de hand van metingen worden vastgesteld. In het algemeen geldt hierbij dat de metingen voldoende representatief zijn. Aangezien de metingen gezien kunnen worden als een steekproef, geldt volgens de algemene regels van de statistiek dat het aantal metingen (de populatie) groot genoeg moet zijn. Bij het toevoegen van een nieuwe meting aan een verzameling metingen zullen in het algemeen de te bepalen parameters wijzigen. Bij een groter wordend aantal metingen convergeren de parameters naar een vaste ‘werkelijke’ waarde. Hoe groter de populatie, des te beter de parameters de werkelijke waarde benaderen. | The relationship between consumption and the maximum load of a similar group of connections is described by the Velander formula (equation 3.18). This formula uses two parameters, α and β, which are determined based on measurements. Generally, it is assumed that the measurements are sufficiently representative. Since the measurements can be considered a sample, the general rules of statistics dictate that the number of measurements (the population) must be large enough. When adding a new measurement to a collection of measurements, the parameters to be determined will generally change. As the number of measurements increases, the parameters converge to a fixed 'true' value. The larger the population, the better the parameters approximate the true value. | not account for individual extreme outliers. In that case, the old method of calculating with maximum values would be more suitable. 3.5.4 Determining the parameters for short-term variations using measurements
Het is van belang de metingen uit te voeren bij een aantal gelijksoortige kenmerken: | It is important to conduct the measurements on a number of similar characteristics: | determined will generally change. As the number of measurements increases, the parameters converge to a fixed 'true' value. The larger the population, the better the parameters approximate the true value.
de aard van de gebieden | the nature of the areas | to a fixed 'true' value. The larger the population, the better the parameters approximate the true value. It is important to conduct the measurements on a number of similar characteristics:
het type aansluitingen | the type of connections | The larger the population, the better the parameters approximate the true value. It is important to conduct the measurements on a number of similar characteristics: the nature of the areas
Bij het meetprogramma wordt gestreefd naar een zo representatief mogelijke steekproef. Dat betekent dat metingen gedaan zijn aan zowel individuele aansluitingen als aan de LS-kabels en aan de distributietransformator van het voedingsgebied. Daartoe zijn op de aansluitingen, LS-kabels en distributietransformator kWh/kW-meters geplaatst. In een (niet nader gespecificeerde) steekproef bij een netbedrijf zijn metingen verricht aan 18 individuele aansluitingen met jaarverbruiken van 1,5 tot 14 MWh en aan grotere verzorgingsgebieden met jaarverbruiken van 681 tot 10170 MWh. | In the measurement program, the goal is to achieve a sample that is as representative as possible. This means that measurements have been conducted on both individual connections as well as on the low-voltage cables and the distribution transformer of the supply area. To this end, kWh/kW meters have been placed on the connections, low-voltage cables, and distribution transformer. In an (unspecified) sample at a network company, measurements were taken on 18 individual connections with annual consumptions ranging from 1.5 to 14 MWh and on larger service areas with annual consumptions ranging from 681 to 10,170 MWh. | the better the parameters approximate the true value. It is important to conduct the measurements on a number of similar characteristics: the nature of the areas the type of connections
De parameters van de formule van Velander (vergelijking 3.18) worden gevonden met behulp van de kleinste kwadratenmethode. Deze methode berekent de waarden van de parameters α en β, waarvoor geldt dat de som van de gekwadrateerde verschillen tussen meetwaarden en berekende waarden minimaal is. De methode gaat uit van | The parameters of the Velander formula (equation 3.18) are determined using the least squares method. This method calculates the values of the parameters α and β, for which the sum of the squared differences between measured values and calculated values is minimized. The method is based on | measurements were taken on 18 individual connections with annual consumptions ranging from 1.5 to 14 MWh and on larger service areas with annual consumptions ranging from 681 to 10,170 MWh.
m | m | calculates the values of the parameters α and β, for which the sum of the squared differences between measured values and calculated values is minimized. The method is based on
meetpunten | meetpunten | the values of the parameters α and β, for which the sum of the squared differences between measured values and calculated values is minimized. The method is based on m
(x | (x | values of the parameters α and β, for which the sum of the squared differences between measured values and calculated values is minimized. The method is based on m meetpunten
1 | 1 | of the parameters α and β, for which the sum of the squared differences between measured values and calculated values is minimized. The method is based on m meetpunten (x
, f | , f | the parameters α and β, for which the sum of the squared differences between measured values and calculated values is minimized. The method is based on m meetpunten (x 1
1 | 1 | α and β, for which the sum of the squared differences between measured values and calculated values is minimized. The method is based on m meetpunten (x 1 , f
), (x | ), (x | and β, for which the sum of the squared differences between measured values and calculated values is minimized. The method is based on m meetpunten (x 1 , f 1
2 | 2 | for which the sum of the squared differences between measured values and calculated values is minimized. The method is based on m meetpunten (x 1 , f 1 ), (x
, f | , f | which the sum of the squared differences between measured values and calculated values is minimized. The method is based on m meetpunten (x 1 , f 1 ), (x 2
2 | 2 | sum of the squared differences between measured values and calculated values is minimized. The method is based on m meetpunten (x 1 , f 1 ), (x 2 , f
), ... , (x | ), ... , (x | of the squared differences between measured values and calculated values is minimized. The method is based on m meetpunten (x 1 , f 1 ), (x 2 , f 2
m | m | between measured values and calculated values is minimized. The method is based on m meetpunten (x 1 , f 1 ), (x 2 , f 2 ), ... , (x
, f | , f | measured values and calculated values is minimized. The method is based on m meetpunten (x 1 , f 1 ), (x 2 , f 2 ), ... , (x m
m | m | and calculated values is minimized. The method is based on m meetpunten (x 1 , f 1 ), (x 2 , f 2 ), ... , (x m , f
) | ) | calculated values is minimized. The method is based on m meetpunten (x 1 , f 1 ), (x 2 , f 2 ), ... , (x m , f m
, waarbij x | , where x | values is minimized. The method is based on m meetpunten (x 1 , f 1 ), (x 2 , f 2 ), ... , (x m , f m )
i | i | The method is based on m meetpunten (x 1 , f 1 ), (x 2 , f 2 ), ... , (x m , f m ) , where x
een gemeten jaarverbruik is en | a measured annual consumption is and | method is based on m meetpunten (x 1 , f 1 ), (x 2 , f 2 ), ... , (x m , f m ) , where x i
f | f | (x 1 , f 1 ), (x 2 , f 2 ), ... , (x m , f m ) , where x i a measured annual consumption is and
i | i | 1 , f 1 ), (x 2 , f 2 ), ... , (x m , f m ) , where x i a measured annual consumption is and f
een gemeten maximum. Deze meetpunten worden benaderd met onderstaande polynoom. | a measured maximum. These data points are approximated with the polynomial below. | , f 1 ), (x 2 , f 2 ), ... , (x m , f m ) , where x i a measured annual consumption is and f i
[ | [ | (x m , f m ) , where x i a measured annual consumption is and f i a measured maximum. These data points are approximated with the polynomial below.
3.29 | 3.29 | m , f m ) , where x i a measured annual consumption is and f i a measured maximum. These data points are approximated with the polynomial below. [
] | ] | , f m ) , where x i a measured annual consumption is and f i a measured maximum. These data points are approximated with the polynomial below. [ 3.29
De methode van de kleinste kwadraten leidt tot de normaalvergelijkingen van Gauss. Onder de voorwaarde dat, in relatie tot de formule van Velander, de parameter | The method of least squares leads to the normal equations of Gauss. Under the condition that, in relation to Velander's formula, the parameter | f m ) , where x i a measured annual consumption is and f i a measured maximum. These data points are approximated with the polynomial below. [ 3.29 ]
a | a | with the polynomial below. [ 3.29 ] The method of least squares leads to the normal equations of Gauss. Under the condition that, in relation to Velander's formula, the parameter
0 | 0 | the polynomial below. [ 3.29 ] The method of least squares leads to the normal equations of Gauss. Under the condition that, in relation to Velander's formula, the parameter a
gelijk is aan nul en dat slechts gezocht wordt naar de parameters | is equal to zero and that only the parameters are being sought | polynomial below. [ 3.29 ] The method of least squares leads to the normal equations of Gauss. Under the condition that, in relation to Velander's formula, the parameter a 0
a | a | the normal equations of Gauss. Under the condition that, in relation to Velander's formula, the parameter a 0 is equal to zero and that only the parameters are being sought
1 | 1 | normal equations of Gauss. Under the condition that, in relation to Velander's formula, the parameter a 0 is equal to zero and that only the parameters are being sought a
en a | and a | equations of Gauss. Under the condition that, in relation to Velander's formula, the parameter a 0 is equal to zero and that only the parameters are being sought a 1
2 | 2 | Gauss. Under the condition that, in relation to Velander's formula, the parameter a 0 is equal to zero and that only the parameters are being sought a 1 and a
, leidt dit tot vergelijking 3.30. | , this leads to equation 3.30. | Under the condition that, in relation to Velander's formula, the parameter a 0 is equal to zero and that only the parameters are being sought a 1 and a 2
[ | [ | to Velander's formula, the parameter a 0 is equal to zero and that only the parameters are being sought a 1 and a 2 , this leads to equation 3.30.
3.30 | 3.30 | Velander's formula, the parameter a 0 is equal to zero and that only the parameters are being sought a 1 and a 2 , this leads to equation 3.30. [
] | ] | formula, the parameter a 0 is equal to zero and that only the parameters are being sought a 1 and a 2 , this leads to equation 3.30. [ 3.30
Indien in deze vergelijkingen wordt ingevuld: | If these equations are substituted: | the parameter a 0 is equal to zero and that only the parameters are being sought a 1 and a 2 , this leads to equation 3.30. [ 3.30 ]
a | a | equal to zero and that only the parameters are being sought a 1 and a 2 , this leads to equation 3.30. [ 3.30 ] If these equations are substituted:
1 | 1 | to zero and that only the parameters are being sought a 1 and a 2 , this leads to equation 3.30. [ 3.30 ] If these equations are substituted: a
zero and that only the parameters are being sought a 1 and a 2 , this leads to equation 3.30. [ 3.30 ] If these equations are substituted: a 1
a | a | that only the parameters are being sought a 1 and a 2 , this leads to equation 3.30. [ 3.30 ] If these equations are substituted: a 1 = β
2 | 2 | only the parameters are being sought a 1 and a 2 , this leads to equation 3.30. [ 3.30 ] If these equations are substituted: a 1 = β a
the parameters are being sought a 1 and a 2 , this leads to equation 3.30. [ 3.30 ] If these equations are substituted: a 1 = β a 2
x | x | are being sought a 1 and a 2 , this leads to equation 3.30. [ 3.30 ] If these equations are substituted: a 1 = β a 2 = α
1 | 1 | being sought a 1 and a 2 , this leads to equation 3.30. [ 3.30 ] If these equations are substituted: a 1 = β a 2 = α x
sought a 1 and a 2 , this leads to equation 3.30. [ 3.30 ] If these equations are substituted: a 1 = β a 2 = α x 1
i | i | 1 and a 2 , this leads to equation 3.30. [ 3.30 ] If these equations are substituted: a 1 = β a 2 = α x 1 = √V
f | f | and a 2 , this leads to equation 3.30. [ 3.30 ] If these equations are substituted: a 1 = β a 2 = α x 1 = √V i
i | i | a 2 , this leads to equation 3.30. [ 3.30 ] If these equations are substituted: a 1 = β a 2 = α x 1 = √V i f
2 , this leads to equation 3.30. [ 3.30 ] If these equations are substituted: a 1 = β a 2 = α x 1 = √V i f i
i | i | this leads to equation 3.30. [ 3.30 ] If these equations are substituted: a 1 = β a 2 = α x 1 = √V i f i = P
gaan de normaalvergelijkingen over in: | the normal equations transform into: | leads to equation 3.30. [ 3.30 ] If these equations are substituted: a 1 = β a 2 = α x 1 = √V i f i = P i
[ | [ | 3.30 ] If these equations are substituted: a 1 = β a 2 = α x 1 = √V i f i = P i the normal equations transform into:
3.31 | 3.31 | ] If these equations are substituted: a 1 = β a 2 = α x 1 = √V i f i = P i the normal equations transform into: [
] | ] | If these equations are substituted: a 1 = β a 2 = α x 1 = √V i f i = P i the normal equations transform into: [ 3.31
Deze vergelijkingen kunnen ook geschreven worden als: | These equations can also be written as: | these equations are substituted: a 1 = β a 2 = α x 1 = √V i f i = P i the normal equations transform into: [ 3.31 ]
[ | [ | β a 2 = α x 1 = √V i f i = P i the normal equations transform into: [ 3.31 ] These equations can also be written as:
3.32 | 3.32 | a 2 = α x 1 = √V i f i = P i the normal equations transform into: [ 3.31 ] These equations can also be written as: [
] | ] | 2 = α x 1 = √V i f i = P i the normal equations transform into: [ 3.31 ] These equations can also be written as: [ 3.32
Waarin: | Where:
[ | [ | α x 1 = √V i f i = P i the normal equations transform into: [ 3.31 ] These equations can also be written as: [ 3.32 ] Where:
3.33 | 3.33 | x 1 = √V i f i = P i the normal equations transform into: [ 3.31 ] These equations can also be written as: [ 3.32 ] Where: [
] | ] | 1 = √V i f i = P i the normal equations transform into: [ 3.31 ] These equations can also be written as: [ 3.32 ] Where: [ 3.33
Dit zijn twee vergelijkingen met twee onbekenden | These are two equations with two unknowns
α | alpha | i the normal equations transform into: [ 3.31 ] These equations can also be written as: [ 3.32 ] Where: [ 3.33 ] These are two equations with two unknowns
en | en | the normal equations transform into: [ 3.31 ] These equations can also be written as: [ 3.32 ] Where: [ 3.33 ] These are two equations with two unknowns alpha
β | beta | normal equations transform into: [ 3.31 ] These equations can also be written as: [ 3.32 ] Where: [ 3.33 ] These are two equations with two unknowns alpha en
die eenvoudig worden opgelost. Na uitwerken van de sommaties voor alle meetwaarden volgt uiteindelijk voor de parameters | which are easily solved. After working out the summations for all the measurements, the parameters ultimately follow | equations transform into: [ 3.31 ] These equations can also be written as: [ 3.32 ] Where: [ 3.33 ] These are two equations with two unknowns alpha en beta
α | alpha | [ 3.33 ] These are two equations with two unknowns alpha en beta which are easily solved. After working out the summations for all the measurements, the parameters ultimately follow
en | en | 3.33 ] These are two equations with two unknowns alpha en beta which are easily solved. After working out the summations for all the measurements, the parameters ultimately follow alpha
β | beta | ] These are two equations with two unknowns alpha en beta which are easily solved. After working out the summations for all the measurements, the parameters ultimately follow alpha en
: | : | These are two equations with two unknowns alpha en beta which are easily solved. After working out the summations for all the measurements, the parameters ultimately follow alpha en beta
[ | [ | are two equations with two unknowns alpha en beta which are easily solved. After working out the summations for all the measurements, the parameters ultimately follow alpha en beta :
3.34 | 3.34 | two equations with two unknowns alpha en beta which are easily solved. After working out the summations for all the measurements, the parameters ultimately follow alpha en beta : [
] | ] | equations with two unknowns alpha en beta which are easily solved. After working out the summations for all the measurements, the parameters ultimately follow alpha en beta : [ 3.34
Met bovenstaande methode wordt uit de metingen van de steekproef berekend: | Using the above method, the sample measurements are calculated as follows: | with two unknowns alpha en beta which are easily solved. After working out the summations for all the measurements, the parameters ultimately follow alpha en beta : [ 3.34 ]
a = 0,25·10 | a = 0.25·10 | working out the summations for all the measurements, the parameters ultimately follow alpha en beta : [ 3.34 ] Using the above method, the sample measurements are calculated as follows:
-3 | -3 | summations for all the measurements, the parameters ultimately follow alpha en beta : [ 3.34 ] Using the above method, the sample measurements are calculated as follows: a = 0.25·10
en | en | for all the measurements, the parameters ultimately follow alpha en beta : [ 3.34 ] Using the above method, the sample measurements are calculated as follows: a = 0.25·10 -3
b = 0,04 | b = 0.04 | all the measurements, the parameters ultimately follow alpha en beta : [ 3.34 ] Using the above method, the sample measurements are calculated as follows: a = 0.25·10 -3 en
. Figuur 3.17 geeft de metingen en de curve in één grafiek weer. De diversiteit van de metingen is groot. De methode schat de parameters op basis van de kleinste som van de afwijkingen in het kwadraat. Dat heeft tot gevolg dat de meetpunten met grote maximum belasting zwaarder wegen dan meetpunten met kleine maximum belasting. Deze methode verdient de voorkeur vanwege de wet van de grote aantallen in de statistiek. Echter, het model moet ook representatief zijn voor de kleine aantallen. Afbeelden van de gegevens in een grafiek met dubbel-logaritmische schaal geeft meer inzicht in de afwijkingen van de metingen ten opzichte van de curve. | Figure 3.17 shows the measurements and the curve in a single graph. The diversity of the measurements is significant. The method estimates the parameters based on the smallest sum of squared deviations. This results in measurement points with high maximum loads weighing more heavily than those with low maximum loads. This method is preferred due to the law of large numbers in statistics. However, the model must also be representative of small numbers. Plotting the data in a graph with a double logarithmic scale provides more insight into the deviations of the measurements relative to the curve. | the parameters ultimately follow alpha en beta : [ 3.34 ] Using the above method, the sample measurements are calculated as follows: a = 0.25·10 -3 en b = 0.04
Figuur 3.17 Meetpunten en berekende curve, afgebeeld op lineaire schaalverdeling | Figure 3.17 Measurement points and calculated curve, depicted on a linear scale | also be representative of small numbers. Plotting the data in a graph with a double logarithmic scale provides more insight into the deviations of the measurements relative to the curve.
Figuur 3.18 Meetpunten en berekende curve, afgebeeld op dubbel-logaritmische schaalverdeling | Figure 3.18 Measurement points and calculated curve, depicted on a double logarithmic scale | with a double logarithmic scale provides more insight into the deviations of the measurements relative to the curve. Figure 3.17 Measurement points and calculated curve, depicted on a linear scale
De diversiteit in de metingen is goed zichtbaar in de grafiek. Zichtbaar zijn een groep metingen aan kleinverbruikers, een aantal metingen aan kleine distributietransformatoren en twee metingen aan grote distributietransformatoren. Bestudering van de grafieken van figuur 3.17 en figuur 3.18 leert dat de curve een goede representatie is van de metingen aan grotere belastingen. Voor de metingen in de groep van kleinverbruikers is de curve niet representatief. | The diversity in the measurements is clearly visible in the graph. Visible are a group of measurements for small consumers, several measurements for small distribution transformers, and two measurements for large distribution transformers. A study of the graphs in Figure 3.17 and Figure 3.18 shows that the curve is a good representation of the measurements for larger loads. For the measurements in the small consumers group, the curve is not representative. | measurements relative to the curve. Figure 3.17 Measurement points and calculated curve, depicted on a linear scale Figure 3.18 Measurement points and calculated curve, depicted on a double logarithmic scale
Indien in de formule van Velander het jaarverbruik van | If in Velander's formula the annual consumption of | and Figure 3.18 shows that the curve is a good representation of the measurements for larger loads. For the measurements in the small consumers group, the curve is not representative.
n | n | a good representation of the measurements for larger loads. For the measurements in the small consumers group, the curve is not representative. If in Velander's formula the annual consumption of
aansluitingen geschreven wordt als het product van het gemiddelde jaarverbruik van één aansluiting en het aantal aansluitingen, gaat deze over in: | connections is written as the product of the average annual consumption of one connection and the number of connections, it becomes: | good representation of the measurements for larger loads. For the measurements in the small consumers group, the curve is not representative. If in Velander's formula the annual consumption of n
[ | [ | If in Velander's formula the annual consumption of n connections is written as the product of the average annual consumption of one connection and the number of connections, it becomes:
3.35 | 3.35 | in Velander's formula the annual consumption of n connections is written as the product of the average annual consumption of one connection and the number of connections, it becomes: [
] | ] | Velander's formula the annual consumption of n connections is written as the product of the average annual consumption of one connection and the number of connections, it becomes: [ 3.35
Hierin is goed te zien dat de parameter | Here it is clearly visible that the parameter | formula the annual consumption of n connections is written as the product of the average annual consumption of one connection and the number of connections, it becomes: [ 3.35 ]
α | alpha | written as the product of the average annual consumption of one connection and the number of connections, it becomes: [ 3.35 ] Here it is clearly visible that the parameter
gelijke invloed heeft voor zowel kleine aantallen als grote aantallen aansluitingen. De parameter | has the same influence for both small and large numbers of connections. The parameter | as the product of the average annual consumption of one connection and the number of connections, it becomes: [ 3.35 ] Here it is clearly visible that the parameter alpha
β | beta | of connections, it becomes: [ 3.35 ] Here it is clearly visible that the parameter alpha has the same influence for both small and large numbers of connections. The parameter
heeft door het wortelteken van | has through the square root of | connections, it becomes: [ 3.35 ] Here it is clearly visible that the parameter alpha has the same influence for both small and large numbers of connections. The parameter beta
n | n | Here it is clearly visible that the parameter alpha has the same influence for both small and large numbers of connections. The parameter beta has through the square root of
verhoudingsgewijs meer invloed voor kleine aantallen aansluitingen. | relatively more influence for small numbers of connections. | it is clearly visible that the parameter alpha has the same influence for both small and large numbers of connections. The parameter beta has through the square root of n
De grafieken in figuur 3.19 illustreren de invloed van variatie van de parameter α op de ligging van de curve ten opzichte van de meetpunten. De eerste afbeelding toont de grafiek in lineaire schaal en de tweede afbeelding in dubbel-logaritmische schaal. De afbeeldingen illustreren dat variatie van parameter α een gewone lineaire invloed heeft op de curves. Voor het oplossen van de afwijkingen ten opzichte van metingen van weinig verbruik en lage belasting levert variatie van α geen juiste correctie. | The graphs in figure 3.19 illustrate the influence of variation of the parameter α on the position of the curve relative to the data points. The first image shows the graph on a linear scale, and the second image on a double logarithmic scale. The images illustrate that variation of parameter α has a simple linear influence on the curves. For resolving discrepancies relative to measurements of low consumption and low load, variation of α does not provide the correct adjustment. | has the same influence for both small and large numbers of connections. The parameter beta has through the square root of n relatively more influence for small numbers of connections.
Figuur 3.19 Variatie van parameter α, afgebeeld met lineaire en dubbel-logaritmische schaalverdeling | Figure 3.19 Variation of parameter α, depicted with linear and double-logarithmic scales | α has a simple linear influence on the curves. For resolving discrepancies relative to measurements of low consumption and low load, variation of α does not provide the correct adjustment.
De grafieken in figuur 3.20 illustreren de invloed van variatie van de parameter β op de ligging van de curve ten opzichte van de meetpunten. De eerste afbeelding toont de grafiek in lineaire schaal en de tweede afbeelding in dubbel-logaritmische schaal. De afbeeldingen illustreren dat variatie van parameter β juist in de lagere vermogens een relatief grote invloed heeft. | The graphs in figure 3.20 illustrate the influence of variation of the parameter β on the position of the curve relative to the data points. The first image shows the graph on a linear scale, and the second image on a double-logarithmic scale. The images illustrate that variation of parameter β has a relatively large influence, particularly at lower power levels. | relative to measurements of low consumption and low load, variation of α does not provide the correct adjustment. Figure 3.19 Variation of parameter α, depicted with linear and double-logarithmic scales
Figuur 3.20 Variatie van parameter β, afgebeeld met lineaire en dubbel-logaritmische schaalverdeling | Figure 3.20 Variation of parameter β, depicted with linear and double-logarithmic scales | on a linear scale, and the second image on a double-logarithmic scale. The images illustrate that variation of parameter β has a relatively large influence, particularly at lower power levels.
In de beschreven methode wegen de grote vermogens zwaarder in de parameterbepaling. Indien gekeken wordt naar de relatieve afwijkingen ten opzichte van de berekende waarde, krijgen de metingen van weinig verbruik en lage belasting meer gewicht in de parameterbepaling. Deze methode maakt gebruik van vergelijking 3.36. | In the described method, higher power levels carry more weight in the parameter determination. When considering the relative deviations from the calculated value, measurements of low consumption and low load are given more weight in the parameter determination. This method uses equation 3.36. | The images illustrate that variation of parameter β has a relatively large influence, particularly at lower power levels. Figure 3.20 Variation of parameter β, depicted with linear and double-logarithmic scales
Uit de formule van Velander volgt: | From Velander's formula follows: | determination. When considering the relative deviations from the calculated value, measurements of low consumption and low load are given more weight in the parameter determination. This method uses equation 3.36.
[ | [ | relative deviations from the calculated value, measurements of low consumption and low load are given more weight in the parameter determination. This method uses equation 3.36. From Velander's formula follows:
3.36 | 3.36 | deviations from the calculated value, measurements of low consumption and low load are given more weight in the parameter determination. This method uses equation 3.36. From Velander's formula follows: [
] | ] | from the calculated value, measurements of low consumption and low load are given more weight in the parameter determination. This method uses equation 3.36. From Velander's formula follows: [ 3.36
waarbij: | where: | the calculated value, measurements of low consumption and low load are given more weight in the parameter determination. This method uses equation 3.36. From Velander's formula follows: [ 3.36 ]
P | P | calculated value, measurements of low consumption and low load are given more weight in the parameter determination. This method uses equation 3.36. From Velander's formula follows: [ 3.36 ] where:
i | i | value, measurements of low consumption and low load are given more weight in the parameter determination. This method uses equation 3.36. From Velander's formula follows: [ 3.36 ] where: P
gemeten maximale belasting (kW) | measured maximum load (kW) | measurements of low consumption and low load are given more weight in the parameter determination. This method uses equation 3.36. From Velander's formula follows: [ 3.36 ] where: P i
V | V | and low load are given more weight in the parameter determination. This method uses equation 3.36. From Velander's formula follows: [ 3.36 ] where: P i measured maximum load (kW)
i | i | low load are given more weight in the parameter determination. This method uses equation 3.36. From Velander's formula follows: [ 3.36 ] where: P i measured maximum load (kW) V
gemeten jaarverbruik (kWh) | measured annual consumption (kWh) | load are given more weight in the parameter determination. This method uses equation 3.36. From Velander's formula follows: [ 3.36 ] where: P i measured maximum load (kW) V i
α, β | α, β | weight in the parameter determination. This method uses equation 3.36. From Velander's formula follows: [ 3.36 ] where: P i measured maximum load (kW) V i measured annual consumption (kWh)
vast te stellen parameters | to determine parameters | the parameter determination. This method uses equation 3.36. From Velander's formula follows: [ 3.36 ] where: P i measured maximum load (kW) V i measured annual consumption (kWh) α, β
r | r | This method uses equation 3.36. From Velander's formula follows: [ 3.36 ] where: P i measured maximum load (kW) V i measured annual consumption (kWh) α, β to determine parameters
i | i | method uses equation 3.36. From Velander's formula follows: [ 3.36 ] where: P i measured maximum load (kW) V i measured annual consumption (kWh) α, β to determine parameters r
residu van meting | residual of measurement | uses equation 3.36. From Velander's formula follows: [ 3.36 ] where: P i measured maximum load (kW) V i measured annual consumption (kWh) α, β to determine parameters r i
i | i | From Velander's formula follows: [ 3.36 ] where: P i measured maximum load (kW) V i measured annual consumption (kWh) α, β to determine parameters r i residual of measurement
Van deze formule zijn niet eenvoudig de residuvergelijkingen op te stellen, waardoor de methode van oplossen met behulp van de normaalvergelijkingen van Gauss (vergelijkingen 3.29 tot en met 3.34) niet kan worden toegepast. Wel is het eenvoudig mogelijk met behulp van variatie van de parameters α en β in een computerprogramma de kleinste som van de kwadraten van de residuen | It is not easy to establish the residual equations from this formula, which means that the method of solving using Gauss's normal equations (equations 3.29 through 3.34) cannot be applied. However, it is possible to use a computer program to vary the parameters α and β to find the smallest sum of the squares of the residuals. | Velander's formula follows: [ 3.36 ] where: P i measured maximum load (kW) V i measured annual consumption (kWh) α, β to determine parameters r i residual of measurement i
r | r | cannot be applied. However, it is possible to use a computer program to vary the parameters α and β to find the smallest sum of the squares of the residuals.
i | i | be applied. However, it is possible to use a computer program to vary the parameters α and β to find the smallest sum of the squares of the residuals. r
vast te stellen. Met behulp van deze ‘experimentele methode’ wordt voor de meetgegevens uit een steekproef: | determined. Using this 'experimental method,' the measurement data from a sample is: | applied. However, it is possible to use a computer program to vary the parameters α and β to find the smallest sum of the squares of the residuals. r i
α = 0,20·10 | α = 0.20·10 | the parameters α and β to find the smallest sum of the squares of the residuals. r i determined. Using this 'experimental method,' the measurement data from a sample is:
-3 | -3 | and β to find the smallest sum of the squares of the residuals. r i determined. Using this 'experimental method,' the measurement data from a sample is: α = 0.20·10
en | en | β to find the smallest sum of the squares of the residuals. r i determined. Using this 'experimental method,' the measurement data from a sample is: α = 0.20·10 -3
β = 0,09 | β = 0.09 | to find the smallest sum of the squares of the residuals. r i determined. Using this 'experimental method,' the measurement data from a sample is: α = 0.20·10 -3 en
. Toepassen van deze waarden leidt tot een te lage ligging van de curve voor de hoge vermogens. De kleinste kwadratenmethode leidt immers tot een curve, waarbij de meetpunten afwijkingen naar boven en naar beneden hebben. Het experimentele karakter van deze methode laat vrij om de parameters zodanig te beïnvloeden dat de curve voor zowel de grote vermogens als de lage vermogens niet teveel onder de waarden van de metingen ligt. Een betere afstemming wordt gevonden na aanpassen van de parameters: | Applying these values results in the curve being too low for high power levels. The least squares method, after all, leads to a curve where the data points have deviations both above and below. The experimental nature of this method allows for the parameters to be adjusted so that the curve does not fall too far below the measurement values for both high and low power levels. A better fit is found after adjusting the parameters: | smallest sum of the squares of the residuals. r i determined. Using this 'experimental method,' the measurement data from a sample is: α = 0.20·10 -3 en β = 0.09
α = 0,22·10 | α = 0.22·10 | adjusted so that the curve does not fall too far below the measurement values for both high and low power levels. A better fit is found after adjusting the parameters:
-3 | -3 | the curve does not fall too far below the measurement values for both high and low power levels. A better fit is found after adjusting the parameters: α = 0.22·10
en | en | curve does not fall too far below the measurement values for both high and low power levels. A better fit is found after adjusting the parameters: α = 0.22·10 -3
β = 0,10 | β = 0.10 | does not fall too far below the measurement values for both high and low power levels. A better fit is found after adjusting the parameters: α = 0.22·10 -3 en
. | . | too far below the measurement values for both high and low power levels. A better fit is found after adjusting the parameters: α = 0.22·10 -3 en β = 0.10
De afbeeldingen in figuur 3.21 tonen in één grafiek de meetpunten, de curve volgens de parameterbepaling (die voorkeur geeft aan de grote vermogens) en de curve volgens de experimenteel geschatte parameters. | The images in figure 3.21 show in a single graph the measurement points, the curve according to the parameter determination (which favors the high power levels), and the curve according to the experimentally estimated parameters. | far below the measurement values for both high and low power levels. A better fit is found after adjusting the parameters: α = 0.22·10 -3 en β = 0.10 .
Figuur 3.21 Variatie van parameters α en β, afgebeeld met lineaire en dubbel-logaritmische schaalverdeling | Figure 3.21 Variation of parameters α and β, depicted with linear and double-logarithmic scales | show in a single graph the measurement points, the curve according to the parameter determination (which favors the high power levels), and the curve according to the experimentally estimated parameters.
3.6 Nieuwe ontwikkelingen | 3.6 New Developments | determination (which favors the high power levels), and the curve according to the experimentally estimated parameters. Figure 3.21 Variation of parameters α and β, depicted with linear and double-logarithmic scales
In het kader van het verduurzamen van de maatschappij en de daarbij in gang gezette energietransitie wordt gezocht naar alternatieven voor het gebruik van energie. Voorbeelden zijn te vinden in het gebruik van elektrische energie als alternatief voor andere energiedragers, zoals de elektrische auto en ruimteverwarming met behulp van warmtepompen en elektrische bijverwarming. Een ander voorbeeld is de alternatieve manier van opwekken van elektrische energie met behulp van windturbines, micro-WKK’s en zonne-energiesystemen (PV). | In the context of making society more sustainable and the ongoing energy transition, alternatives for energy use are being sought. Examples can be found in the use of electrical energy as an alternative to other energy carriers, such as electric cars and space heating using heat pumps and electric auxiliary heating. Another example is the alternative way of generating electrical energy using wind turbines, micro-CHP systems, and solar energy systems (PV). | the high power levels), and the curve according to the experimentally estimated parameters. Figure 3.21 Variation of parameters α and β, depicted with linear and double-logarithmic scales 3.6 New Developments
Een nadeel van deze ontwikkelingen is dat zij verantwoordelijk zijn voor een forse toename van het elektriciteitstransport over het distributienet en dat dit met een zeer grote waarde voor de gelijktijdigheid gepaard gaat. In netten waar deze nieuwe ontwikkelingen worden toegepast kan daarom niet meer alleen met het gedeelte van de belasting worden gerekend dat zich ongelijktijdig gedraagt maar moet ook rekening gehouden worden met een nieuwe component van de belasting die zich met een grote gelijktijdigheid gedraagt. Zo zullen nagenoeg alle elektrische auto’s worden opgeladen bij thuiskomst aan het einde van een werkdag en zullen warmtepompen met eventueel bijverwarming op koude dagen alle gelijktijdig in bedrijf zijn. Als gevolg hiervan zal in het ontwerp van het net (zowel bestaand als nieuw) in toenemende mate rekening moeten worden gehouden met de som van de individuele maximale belastingen. | A disadvantage of these developments is that they are responsible for a significant increase in electricity transport over the distribution network, accompanied by a very high simultaneity value. In networks where these new developments are applied, it is no longer sufficient to account only for the portion of the load that behaves asynchronously; consideration must also be given to a new component of the load that behaves with high simultaneity. For instance, nearly all electric cars will be charged upon returning home at the end of a workday, and heat pumps with possible auxiliary heating will all be in operation simultaneously on cold days. As a result, the design of the network (both existing and new) will increasingly need to take into account the sum of the individual maximum loads. | and space heating using heat pumps and electric auxiliary heating. Another example is the alternative way of generating electrical energy using wind turbines, micro-CHP systems, and solar energy systems (PV).
3.6.1 Warmtepompen | 3.6.1 Heat Pumps | simultaneously on cold days. As a result, the design of the network (both existing and new) will increasingly need to take into account the sum of the individual maximum loads.
In een groeiend aantal nieuwbouwprojecten worden woningen uitgerust met warmtepompsystemen voor verwarming en koeling. In de huidige nieuwbouw wordt in 6% van de woningen een warmtepomp toegepast, wat overeenkomt met de implementatie van 3500 warmtepompen per jaar. Vooralsnog zijn dit voornamelijk elektrische warmtepompen. Het werkingsprincipe is vergelijkbaar met dat van een koelkast of airconditioner. Voor het verwarmen van een ruimte wordt warmte onttrokken aan een medium. Dit medium kan de buitenlucht zijn of grondwater. Het voordeel van deze systemen is dat ze twee kanten op kunnen werken. Dat betekent dat een ruimte ook gekoeld kan worden door warmte af te geven aan het zelfde medium. Bij gebruik van grondwater als medium kan in de zomer warmte worden opgeslagen in de bodem, die er in de winter voor verwarmingsdoeleinden weer aan onttrokken wordt. Deze warmtepompsystemen zijn weliswaar energiezuiniger dan traditionele verwarmingsketels, maar verbruiken desalniettemin een forse hoeveelheid elektrische energie. De elektrische vermogens variëren van 2 tot 5 kW. Daarnaast is de warmtepomp veelal uitgerust met een bijverwarming met een vermogen van circa 6 kW, die in kan komen bij lage buitentemperatuur en na een langdurige storing van het elektriciteitsnet. Lage buitentemperatuur en een storing treffen alle woningen tegelijkertijd. Daarom moet bij grootschalige toepassing van warmtepompen in woningen terdege rekening gehouden worden met het feit dat deze apparaten een grote gelijktijdigheid vertonen in de elektriciteitsvraag. Hierbij geldt dat deze voornamelijk wordt bepaald door de warmtevraag in de winter of vraag naar koeling in de zomer. Met name in de winterperiode stijgt de behoefte naar ruimteverwarming aan het einde van de middag en in de avond gelijktijdig voor alle woningen. Ook op het warmst van een zomerdag zal de behoefte aan ruimtekoeling gelijktijdig stijgen. Het werkelijke gedrag is afhankelijk van de isolatiegraad van de woning. Bij goed geïsoleerde huizen zal het elektriciteitsprofiel van de warmtepomp vrijwel vlak gaan lopen. | In a growing number of new construction projects, homes are being equipped with heat pump systems for heating and cooling. Currently, 6% of new homes are being fitted with a heat pump, which corresponds to the installation of 3,500 heat pumps per year. For now, these are mainly electric heat pumps. The operating principle is similar to that of a refrigerator or air conditioner. To heat a space, heat is extracted from a medium. This medium can be the outside air or groundwater. The advantage of these systems is that they can work both ways. This means that a space can also be cooled by releasing heat to the same medium. When using groundwater as the medium, heat can be stored in the ground during the summer, which can then be extracted for heating purposes in the winter. Although these heat pump systems are more energy-efficient than traditional heating boilers, they still consume a significant amount of electrical energy. The electrical capacities range from 2 to 5 kW. Additionally, the heat pump is often equipped with an auxiliary heater with a capacity of approximately 6 kW, which can activate during low outside temperatures and after a prolonged power outage. Low outside temperatures and outages affect all homes simultaneously. Therefore, when heat pumps are widely used in homes, it must be taken into account that these devices exhibit a high degree of simultaneity in electricity demand. This demand is mainly determined by the need for heating in the winter or cooling in the summer. Particularly in the winter, the need for space heating increases simultaneously for all homes in the late afternoon and evening. Similarly, on the hottest days of summer, the need for space cooling will rise simultaneously. The actual behavior depends on the insulation level of the home. In well-insulated houses, the electricity profile of the heat pump will be almost flat. | days. As a result, the design of the network (both existing and new) will increasingly need to take into account the sum of the individual maximum loads. 3.6.1 Heat Pumps
Er zijn voorbeelden dat door een wijziging van het milieubeleid tijdens een nieuwbouwproject de woningen niet met conventionele verwarming maar met warmtepompen worden uitgevoerd. Als gevolg van de toegenomen elektriciteitsvraag bleek het distributienet niet meer voldoende. Het is dus van groot belang met de mogelijkheid van deze vorm van verwarming rekening te houden. | There are examples where, due to a change in environmental policy during a new construction project, the homes are equipped with heat pumps instead of conventional heating. As a result of the increased electricity demand, the distribution network proved to be insufficient. It is therefore crucial to take the possibility of this form of heating into account. | space cooling will rise simultaneously. The actual behavior depends on the insulation level of the home. In well-insulated houses, the electricity profile of the heat pump will be almost flat.
In projecten waar deze systemen worden toegepast zal de methode van Velander niet zonder meer gebruikt kunnen worden maar zal rekening gehouden moeten worden met gelijktijdige inschakeling van bijna alle warmtepompen. Dit veelal inclusief de bijverwarming en naast de gebruikelijke kleinschalige belasting. Dit houdt in dat de totale belasting wordt gesplitst in een deel met grote gelijktijdigheid en een deel met kleine gelijktijdigheid. Figuur 3.22 toont een gedeelte van een laagspanningsnet met 4 secties met elk 10 vrijstaande woningen, zonder warmtepompen (boven), met warmtepompen (midden) en met warmtepompen en ingeschakelde bijverwarming (onder). Bij de berekening van de LS-voedingskabels is uitgegaan van een vermogen van 3 kW per warmtepomp en 6 kW per bijverwarming. In het geval zonder warmtepompen kan de LS-hoofdkabel met aluminium geleiders verjongd worden van 95 naar 50 mm | In projects where these systems are applied, the Velander method cannot be used without adjustments, and consideration must be given to the simultaneous activation of almost all heat pumps. This often includes the auxiliary heating in addition to the usual small-scale load. This means that the total load is divided into a part with high simultaneity and a part with low simultaneity. Figure 3.22 shows a section of a low-voltage network with 4 sections, each with 10 detached houses, without heat pumps (top), with heat pumps (middle), and with heat pumps and activated auxiliary heating (bottom). In the calculation of the LV supply cables, a power of 3 kW per heat pump and 6 kW per auxiliary heating was assumed. In the case without heat pumps, the LV main cable with aluminum conductors can be reduced from 95 to 50 mm. | As a result of the increased electricity demand, the distribution network proved to be insufficient. It is therefore crucial to take the possibility of this form of heating into account.
2 | 2 | pump and 6 kW per auxiliary heating was assumed. In the case without heat pumps, the LV main cable with aluminum conductors can be reduced from 95 to 50 mm.
geleiderdoorsnede. In het geval met alleen warmtepompen zijn in de eerste twee secties kabels met 150 mm | conductor cross-section. In the case with only heat pumps, cables with a 150 mm cross-section are used in the first two sections. | and 6 kW per auxiliary heating was assumed. In the case without heat pumps, the LV main cable with aluminum conductors can be reduced from 95 to 50 mm. 2
2 | 2 | be reduced from 95 to 50 mm. 2 conductor cross-section. In the case with only heat pumps, cables with a 150 mm cross-section are used in the first two sections.
geleiderdoorsnede toegepast en dan nog is de eerste sectie overbelast. In het geval met warmtepompen en ingeschakelde bijverwarming is het net met toepassing van 150 mm | conductor cross-section applied and even then the first section is overloaded. In the case with heat pumps and activated auxiliary heating, the network with the application of 150 mm | reduced from 95 to 50 mm. 2 conductor cross-section. In the case with only heat pumps, cables with a 150 mm cross-section are used in the first two sections. 2
2 | 2 | 2 conductor cross-section applied and even then the first section is overloaded. In the case with heat pumps and activated auxiliary heating, the network with the application of 150 mm
Al-kabels zwaar overbelast en is de spanning aan het einde van de streng te laag. Een oplossing voor dit vraagstuk kan worden gevonden door minder aansluitingen op een streng toe te laten of te werken met parallelle kabels, ervan uitgaande dat er geen kabels worden toegepast met een grotere geleiderdoorsnede. | Aluminum cables are heavily overloaded and the voltage at the end of the line is too low. A solution to this problem can be found by allowing fewer connections on a line or by working with parallel cables, assuming that no cables with a larger conductor cross-section are used. | conductor cross-section applied and even then the first section is overloaded. In the case with heat pumps and activated auxiliary heating, the network with the application of 150 mm 2
Indien de warmtepomp en de bijverwarming driefasig zijn aangesloten, levert dat een extra belasting per aansluiting van 9000 kVA / 3 / 235 V = 12,8 A per fase. Bij een gelijktijdigheid van 1 kan dit voor 10 aansluitingen gewoon met 10 vermenigvuldigd worden, resulterend in een extra belastingstroom van 128 A. Deze stroom wordt opgeteld bij de standaard belasting van 10 vrijstaande woningen van maximaal 24 A, resulterend in een totale belastingstroom van 128 + 24 = 152 A, zichtbaar in de laatste kabelsectie van figuur 3.22. Hieruit blijkt dat de impact van warmtepompsystemen (128 A) zo groot is dat de invloed van het stochastische gedrag van de overige belasting (24 A) nagenoeg verwaarloosd kan worden. | If the heat pump and auxiliary heating are connected in three phases, this results in an additional load per connection of 9000 kVA / 3 / 235 V = 12.8 A per phase. With a simultaneity factor of 1, this can simply be multiplied by 10 for 10 connections, resulting in an additional load current of 128 A. This current is added to the standard load of 10 detached houses, which is a maximum of 24 A, resulting in a total load current of 128 + 24 = 152 A, as seen in the last cable section of figure 3.22. This shows that the impact of heat pump systems (128 A) is so significant that the influence of the stochastic behavior of the remaining load (24 A) can be practically neglected. | to this problem can be found by allowing fewer connections on a line or by working with parallel cables, assuming that no cables with a larger conductor cross-section are used.
Figuur 3.22 LS-hoofdkabel zonder en met warmtepompsystemen | Figure 3.22 LV main cable without and with heat pump systems | shows that the impact of heat pump systems (128 A) is so significant that the influence of the stochastic behavior of the remaining load (24 A) can be practically neglected.
3.6.2 Elektrische auto | 3.6.2 Electric car | so significant that the influence of the stochastic behavior of the remaining load (24 A) can be practically neglected. Figure 3.22 LV main cable without and with heat pump systems
De elektrische auto is anno 2010 aan een langzame opmars begonnen. Bij een doorbraak wordt gevreesd dat de piekbelasting sprongsgewijs toeneemt. De prognoses van het aantal elektrische auto’s in Nederland in het jaar 2020 lopen sterk uiteen, van 200 000 tot meer dan 1 miljoen. Een kwart miljoen is al ambitieus, maar in principe haalbaar. Het effect hiervan zal het meest merkbaar zijn in de laagspanningsnetten, direct gevolgd door de middenspanningsnetten. In dit kader staat de netbeheerder voor een aantal onzekerheden. Onder andere: hoe kan bij de bestaande transportcapaciteit deze nieuwe ontwikkeling goed worden ingepast en hoe moeten nieuw te ontwerpen netten hierop voorbereid worden? Om deze vragen te kunnen beantwoorden moet eerst naar het te verwachten elektrische gedrag van de elektrische auto gekeken worden. | The electric car began a slow rise in 2010. In the event of a breakthrough, there are concerns that peak load will increase abruptly. The forecasts for the number of electric cars in the Netherlands in the year 2020 vary widely, from 200,000 to more than 1 million. A quarter of a million is already ambitious but theoretically achievable. The effect of this will be most noticeable in the low-voltage networks, immediately followed by the medium-voltage networks. In this context, the grid operator faces several uncertainties. Among others: how can this new development be properly integrated with the existing transport capacity, and how should newly designed networks be prepared for this? To answer these questions, the expected electrical behavior of the electric car must first be examined. | the influence of the stochastic behavior of the remaining load (24 A) can be practically neglected. Figure 3.22 LV main cable without and with heat pump systems 3.6.2 Electric car
In 2007 reed een personenauto gemiddeld 13877 km in het jaar (CBS Statline). Aangenomen wordt dat het verbruik van de elektrische auto 5-7 km/kWh (gemiddeld 1 kWh op 6 km) is. Dit is gebaseerd op specificaties van leveranciers en op praktijkcijfers, die uiteenlopen van 1 op 4 tot 1 op 7, afhankelijk van rijstijl en type auto. Dat houdt in dat het jaarverbruik van een elektrische auto gelijk is aan 13877/6 = 2312 kWh/jr. Op basis van dit jaarverbruik komt dit neer op een verbruik van circa 6,3 kWh per dag. Ter vergelijking, het gemiddelde jaarverbruik van een woning in 2007 is 3512 kWh (9,6 kWh per dag). | In 2007, a passenger car drove an average of 13,877 km per year (CBS Statline). It is assumed that the consumption of the electric car is 5-7 km/kWh (an average of 1 kWh per 6 km). This is based on specifications from suppliers and on practical figures, which range from 1 per 4 to 1 per 7, depending on driving style and type of car. This means that the annual consumption of an electric car is equal to 13,877/6 = 2,312 kWh/year. Based on this annual consumption, this amounts to a consumption of approximately 6.3 kWh per day. For comparison, the average annual consumption of a household in 2007 is 3,512 kWh (9.6 kWh per day). | the existing transport capacity, and how should newly designed networks be prepared for this? To answer these questions, the expected electrical behavior of the electric car must first be examined.
De piekbelasting van een elektrische auto wordt bepaald door de hoeveelheid bij te laden energie en de tijdsduur van het laden. Voor het berekenen van de piekbelasting in de thuissituatie kan worden aangenomen dat een lege accu in een nacht opgeladen moet kunnen worden. Indien uitgegaan wordt van een duur van 8 uur (van 23:00 uur tot 7:00 uur) en een accucapaciteit in de auto van 16 tot 36 kWh (anno 2009), dan is het benodigde laadvermogen van een auto: | The peak load of an electric car is determined by the amount of energy to be recharged and the duration of the charging. For calculating the peak load in a home situation, it can be assumed that an empty battery should be able to be charged overnight. Assuming a duration of 8 hours (from 11:00 PM to 7:00 AM) and a battery capacity in the car of 16 to 36 kWh (as of 2009), the required charging power of a car is: | consumption, this amounts to a consumption of approximately 6.3 kWh per day. For comparison, the average annual consumption of a household in 2007 is 3,512 kWh (9.6 kWh per day).
Voor een kleine accu: 16 / 8 = 2 kW | For a small battery: 16 / 8 = 2 kW | hours (from 11:00 PM to 7:00 AM) and a battery capacity in the car of 16 to 36 kWh (as of 2009), the required charging power of a car is:
Voor een grote accu: 36 / 8 = 4,5 kW | For a large battery: 36 / 8 = 4.5 kW | capacity in the car of 16 to 36 kWh (as of 2009), the required charging power of a car is: For a small battery: 16 / 8 = 2 kW
Er zijn elektrische auto’s waarvan het piek-laadvermogen is afgestemd op een reguliere installatie van 10 A en 230 V, waardoor het piek-laadvermogen beperkt is tot 2 kW. Er zijn ook elektrische auto’s die zijn uitgerust met een krachtstroomstekker, die geschikt is voor 3 x 16 A en 400 V. Hiermee kan bij gebruik van een fase geladen worden met 3,5 kW en bij gebruik van drie fasen met 10 kW. De Europese standaardstekker is geschikt voor 3 x 63 A en 400 V. Dit zou overeenkomen met een piek-laadvermogen van 40 kW. Dit vermogen wordt nog niet geheel benut. De ontwikkelingen van de laders zijn in 2010 nog niet zover. Er zijn fabrikanten die nadenken over een lader van 20 kW. Als dit soort laders in grote hoeveelheden worden toegepast en als zij tegelijkertijd laden, zullen zij een probleem vormen ten aanzien van de piekbelasting van het distributienet. | There are electric cars whose peak charging power is adjusted to a regular installation of 10 A and 230 V, limiting the peak charging power to 2 kW. There are also electric cars equipped with a three-phase plug, suitable for 3 x 16 A and 400 V. With this, charging with one phase can be done at 3.5 kW and with three phases at 10 kW. The European standard plug is suitable for 3 x 63 A and 400 V. This would correspond to a peak charging power of 40 kW. This capacity is not yet fully utilized. As of 2010, the development of chargers has not progressed that far. Some manufacturers are considering a 20 kW charger. If such chargers are used in large quantities and charged simultaneously, they will pose a problem regarding the peak load on the distribution network. | of 2009), the required charging power of a car is: For a small battery: 16 / 8 = 2 kW For a large battery: 36 / 8 = 4.5 kW
Een vermogen van 4,5 kW voor het in 8 uren opladen van een grote accu kan al niet meer door een normaal stopcontact met een zekering van 16 A worden geleverd. In dat geval moet gebruik worden gemaakt van een driefasenaansluiting of moet genoegen worden genomen met een langere tijdsduur. Een tijdsduur van 10 uren betekent een laadvermogen van 3,6 kW en dit komt bij een spanning van 230 V overeen met een stroom van 15,7 A. Een voorwaarde is dat de oplaadcyclus voor elke elektrische auto, onafhankelijk van de laadtoestand van de accu, gespreid wordt over de maximale tijdsduur van 8 tot 10 uren. In aanmerking moet worden genomen dat in veel huishoudelijke situaties de oplaadtijd ook 12 uur zou mogen bedragen, hetgeen de piekbelasting zou kunnen reduceren. Figuur 3.23 illustreert de elektriciteitsvraag in geval van een niet gestuurde oplaadcyclus, waar de stroom in de avonduren gedurende korte tijd zeer groot is. Figuur 3.24 toont een situatie van een geoptimaliseerde oplaadcyclus, waarbij de tijdsduur door de klant is ingesteld. Het voorbeeld gaat uit van een wijk met 40 eengezinswoningen waarvan bij 25% van de woningen een elektrische auto opgeladen moet worden. Er zijn dus in dit voorbeeldnet 10 elektrische auto’s aanwezig, waarvan de energiebehoefte gemiddeld 6,3 kWh per dag is. | A power of 4.5 kW for charging a large battery in 8 hours can no longer be supplied by a regular outlet with a 16 A fuse. In that case, a three-phase connection must be used, or a longer charging time must be accepted. A duration of 10 hours means a charging power of 3.6 kW, which corresponds to a current of 15.7 A at a voltage of 230 V. A condition is that the charging cycle for each electric car, regardless of the battery's state of charge, is spread over the maximum duration of 8 to 10 hours. It should be considered that in many household situations, the charging time could also be 12 hours, which could reduce the peak load. Figure 3.23 illustrates the electricity demand in the case of an uncontrolled charging cycle, where the current is very high for a short period in the evening. Figure 3.24 shows a situation of an optimized charging cycle, where the duration is set by the customer. The example assumes a neighborhood with 40 single-family homes, of which 25% need to charge an electric car. Thus, in this example network, there are 10 electric cars, with an average energy requirement of 6.3 kWh per day. | are considering a 20 kW charger. If such chargers are used in large quantities and charged simultaneously, they will pose a problem regarding the peak load on the distribution network.
Bij een ongecontroleerde oplaadcyclus kan een gemiddelde energie van 6,3 kWh per auto in 2 uren geleverd worden bij een stroomsterkte van 13,7 A en een enkelfasige spanning van 230 V. In het voorbeeld is ervan uitgegaan dat de helft van de auto’s vanaf 19:00 uur wordt opgeladen en de andere helft vanaf 20:00 uur. Dit veroorzaakt in het eerste uur een extra stroomsterkte van 23 A per fase en in het tweede uur een extra stroomsterkte van 46 A per fase. Als dit in de avonduren tijdens de maximale belasting plaatsvindt, kan het net hierdoor overbelast raken. | With an uncontrolled charging cycle, an average energy of 6.3 kWh per car can be delivered in 2 hours at a current of 13.7 A and a single-phase voltage of 230 V. In the example, it is assumed that half of the cars start charging at 7:00 PM and the other half at 8:00 PM. This causes an additional current of 23 A per phase in the first hour and an additional current of 46 A per phase in the second hour. If this occurs during the evening hours at peak load times, the grid can become overloaded. | homes, of which 25% need to charge an electric car. Thus, in this example network, there are 10 electric cars, with an average energy requirement of 6.3 kWh per day.
Voorbeeld ongecontroleerd opladen: | Example of uncontrolled charging: | hour and an additional current of 46 A per phase in the second hour. If this occurs during the evening hours at peak load times, the grid can become overloaded.
Aantal woningen: 40 | Number of homes: 40 | current of 46 A per phase in the second hour. If this occurs during the evening hours at peak load times, the grid can become overloaded. Example of uncontrolled charging:
Aantal elektrische auto’s: 10 | Number of electric cars: 10 | per phase in the second hour. If this occurs during the evening hours at peak load times, the grid can become overloaded. Example of uncontrolled charging: Number of homes: 40
Energiebehoefte: 6,3 kWh per auto gemiddeld | Energy requirement: 6.3 kWh per car on average | hour. If this occurs during the evening hours at peak load times, the grid can become overloaded. Example of uncontrolled charging: Number of homes: 40 Number of electric cars: 10
Totale energiebehoefte: 63 kWh | Total energy requirement: 63 kWh | at peak load times, the grid can become overloaded. Example of uncontrolled charging: Number of homes: 40 Number of electric cars: 10 Energy requirement: 6.3 kWh per car on average
Aantal uren benodigd voor opladen: 2 | Number of hours required for charging: 2 | grid can become overloaded. Example of uncontrolled charging: Number of homes: 40 Number of electric cars: 10 Energy requirement: 6.3 kWh per car on average Total energy requirement: 63 kWh
Piekvermogen: 63 kWh / 2 h = 31,5 kW | Peak power: 63 kWh / 2 h = 31.5 kW | charging: Number of homes: 40 Number of electric cars: 10 Energy requirement: 6.3 kWh per car on average Total energy requirement: 63 kWh Number of hours required for charging: 2
Maximale stroom driefasensysteem: (31500/3) / 230 = 46 A/fase | Maximum current three-phase system: (31500/3) / 230 = 46 A/phase | Energy requirement: 6.3 kWh per car on average Total energy requirement: 63 kWh Number of hours required for charging: 2 Peak power: 63 kWh / 2 h = 31.5 kW
Figuur 3.23 Ongecontroleerde oplaadcyclus van 10 elektrische auto’s | Figure 3.23 Uncontrolled charging cycle of 10 electric cars | requirement: 63 kWh Number of hours required for charging: 2 Peak power: 63 kWh / 2 h = 31.5 kW Maximum current three-phase system: (31500/3) / 230 = 46 A/phase
Bij een gecontroleerde en geoptimaliseerde oplaadcyclus kan de gemiddelde energie van 6,3 kWh per auto in 8 uren gespreid geleverd worden bij een stroomsterkte van 3,4 A en een enkelfasige spanning van 230 V. In het voorbeeld is ervan uitgegaan dat alle auto’s vanaf 22:00 uur worden opgeladen. Dit veroorzaakt in het net een extra stroomvraag van 11,4 A per fase. | With a controlled and optimized charging cycle, the average energy of 6.3 kWh per car can be delivered over 8 hours at a current of 3.4 A and a single-phase voltage of 230 V. In the example, it is assumed that all cars start charging from 10:00 PM. This causes an additional current demand of 11.4 A per phase on the grid. | 2 Peak power: 63 kWh / 2 h = 31.5 kW Maximum current three-phase system: (31500/3) / 230 = 46 A/phase Figure 3.23 Uncontrolled charging cycle of 10 electric cars
Voorbeeld gecontroleerd en geoptimaliseerd opladen: | Example of controlled and optimized charging: | 230 V. In the example, it is assumed that all cars start charging from 10:00 PM. This causes an additional current demand of 11.4 A per phase on the grid.
Aantal woningen: 40 | Number of homes: 40 | is assumed that all cars start charging from 10:00 PM. This causes an additional current demand of 11.4 A per phase on the grid. Example of controlled and optimized charging:
Aantal elektrische auto’s: 10 | Number of electric cars: 10 | cars start charging from 10:00 PM. This causes an additional current demand of 11.4 A per phase on the grid. Example of controlled and optimized charging: Number of homes: 40
Energiebehoefte: 6,3 kWh per auto gemiddeld | Energy requirement: 6.3 kWh per car on average | PM. This causes an additional current demand of 11.4 A per phase on the grid. Example of controlled and optimized charging: Number of homes: 40 Number of electric cars: 10
Totale energiebehoefte: 63 kWh | Total energy requirement: 63 kWh | 11.4 A per phase on the grid. Example of controlled and optimized charging: Number of homes: 40 Number of electric cars: 10 Energy requirement: 6.3 kWh per car on average
Aantal uren benodigd voor opladen: 8 | Number of hours required for charging: 8 | the grid. Example of controlled and optimized charging: Number of homes: 40 Number of electric cars: 10 Energy requirement: 6.3 kWh per car on average Total energy requirement: 63 kWh
Piekvermogen: 63 kWh / 8 h = 7,9 kW | Peak power: 63 kWh / 8 h = 7.9 kW | charging: Number of homes: 40 Number of electric cars: 10 Energy requirement: 6.3 kWh per car on average Total energy requirement: 63 kWh Number of hours required for charging: 8
Maximale stroom driefasensysteem: (7900/3) / 230 = 11,4 A/fase | Maximum current three-phase system: (7900/3) / 230 = 11.4 A/phase | Energy requirement: 6.3 kWh per car on average Total energy requirement: 63 kWh Number of hours required for charging: 8 Peak power: 63 kWh / 8 h = 7.9 kW
Figuur 3.24 Geoptimaliseerde oplaadcyclus van 10 elektrische auto’s | Figure 3.24 Optimized charging cycle of 10 electric cars | requirement: 63 kWh Number of hours required for charging: 8 Peak power: 63 kWh / 8 h = 7.9 kW Maximum current three-phase system: (7900/3) / 230 = 11.4 A/phase
Bovenstaand voorbeeld illustreert het belang van de spreiding van de oplaadperiode van de elektrische auto’s. Ook belastingsturing voorkomt dat het opladen voor of tijdens de piek in de avonduren start. | The above example illustrates the importance of spreading out the charging period of electric cars. Load management also prevents charging from starting before or during the peak evening hours. | 8 Peak power: 63 kWh / 8 h = 7.9 kW Maximum current three-phase system: (7900/3) / 230 = 11.4 A/phase Figure 3.24 Optimized charging cycle of 10 electric cars
Door de accu’s gestuurd op te laden (slim laden) wordt de vraag afgestemd op de netcapaciteit en eventueel op het aanbod van duurzame energie. De stromen waarbij accu’s geladen worden als ze aan het net gekoppeld zijn, mogen variëren gedurende de laadsessie. Hierbij worden de accu’s vanuit het net alleen opgeladen. De accu’s kunnen in principe ook gebruikt worden als buffer voor het net, waarbij zij elektriciteit terugleveren aan het net. Hierdoor zal het aantal op- en ontlaadcycli toenemen Een nadeel dat hierbij optreedt is dat dit tot snellere slijtage van de accu’s kan leiden. Daarom zal dit maar met mate worden toegepast. | By charging the batteries in a controlled manner (smart charging), the demand is adjusted to the grid capacity and potentially to the supply of sustainable energy. The currents at which batteries are charged when connected to the grid may vary during the charging session. In this process, the batteries are only charged from the grid. The batteries can, in principle, also be used as a buffer for the grid, where they supply electricity back to the grid. This will increase the number of charge and discharge cycles. A disadvantage of this is that it can lead to faster wear and tear on the batteries. Therefore, this will only be applied in moderation. | cars The above example illustrates the importance of spreading out the charging period of electric cars. Load management also prevents charging from starting before or during the peak evening hours.
Er wordt geëxperimenteerd met snelladen binnen 20 tot 40 minuten. Snelladen betekent in de praktijk het opladen van de accu van 20% lading naar 80% lading, dus niet van 0 naar 100%. Wel treedt hier, door de grote vermogens veel warmteverlies op. Daarom is het laadvermogen al snel 10% of meer groter dan het vermogen dat in de accu komt. Voor het 60% opladen binnen een half uur is dan het benodigde laadvermogen, inclusief de warmteverliezen, per auto: | Experiments are being conducted with fast charging within 20 to 40 minutes. In practice, fast charging means charging the battery from 20% to 80% capacity, not from 0 to 100%. However, due to the high power involved, significant heat loss occurs. Therefore, the charging power quickly becomes 10% or more greater than the power that actually goes into the battery. For charging 60% within half an hour, the required charging power per car, including heat losses, is: | of charge and discharge cycles. A disadvantage of this is that it can lead to faster wear and tear on the batteries. Therefore, this will only be applied in moderation.
Voor een kleine accu: 0,6 · ( 16 / 0,5 ) · 1,1 = 21 kW | For a small battery: 0.6 · (16 / 0.5) · 1.1 = 21 kW | 10% or more greater than the power that actually goes into the battery. For charging 60% within half an hour, the required charging power per car, including heat losses, is:
Voor een grote accu: 0,6 · ( 36 / 0,5 ) · 1,1 = 48 kW | For a large battery: 0.6 · (36 / 0.5) · 1.1 = 48 kW | charging 60% within half an hour, the required charging power per car, including heat losses, is: For a small battery: 0.6 · (16 / 0.5) · 1.1 = 21 kW
Deze vermogens corresponderen in een LS-driefasensysteem met een stroomsterkte van respectievelijk 30 en 70 A, uitgaande van een arbeidsfactor van 1. Aanleg van een faciliteit om meerdere auto’s te kunnen snelladen vergt een specifieke investering in de infrastructuur. Vanwege de hierbij optredende hoge stroomvraag kan dit eventueel leiden tot een eigen MS-aansluiting of een distributiestation. | These power levels correspond in an LV three-phase system with a current of 30 and 70 A, respectively, assuming a power factor of 1. Establishing a facility to fast-charge multiple cars requires a specific investment in the infrastructure. Due to the high current demand that occurs in this scenario, this may potentially lead to the need for a dedicated MV connection or a distribution station. | losses, is: For a small battery: 0.6 · (16 / 0.5) · 1.1 = 21 kW For a large battery: 0.6 · (36 / 0.5) · 1.1 = 48 kW
Voor het berekenen van de gelijktijdigheid voor het laden van veel auto’s in de woonsituatie kan worden uitgegaan van het gemiddelde elektriciteitsverbruik van een auto van 6,3 kWh/dag. De gelijktijdige belasting van het net door ’s nachts gedurende 8 uren te laden wordt dan 6,3 kWh gedeeld door 8 = 0,79 kW per elektrische auto (gebaseerd op gegevens van een elektrische auto in 2010). Het probleem met de gelijktijdigheid is dat er nog helemaal geen ervaring is opgedaan met het grootschalig opladen van elektrische auto’s. In het ergste geval is de gelijktijdigheidsfactor 1, waardoor alle piek-laadvermogens gelijktijdig zijn aangesloten. Dit betekent dat de extra piekbelasting kan liggen tussen 0,79 kW per auto en 10 kW per auto, bij de stand van de toegepaste techniek in 2010. | For calculating the simultaneity of charging many cars in a residential situation, one can assume an average electricity consumption of 6.3 kWh/day per car. The simultaneous load on the grid by charging at night for 8 hours would then be 6.3 kWh divided by 8 = 0.79 kW per electric car (based on data from an electric car in 2010). The problem with simultaneity is that there is no experience yet with large-scale charging of electric cars. In the worst case, the simultaneity factor is 1, meaning all peak charging capacities are connected simultaneously. This means that the additional peak load can range between 0.79 kW per car and 10 kW per car, based on the technology applied in 2010. | in the infrastructure. Due to the high current demand that occurs in this scenario, this may potentially lead to the need for a dedicated MV connection or a distribution station.
Het rekenen met gelijktijdigheid gaat altijd uit van grote aantallen. Het aantal elektrische auto’s is vooralsnog gering. Bovendien blijkt de diversiteit van de behoefte om op te laden groot. Ook kan rekening gehouden worden met de mogelijkheid om ook overdag, in parkeergelegenheden bij winkelcentra of op het werk, de accu’s van de auto’s op te laden. Met name het grote aantal elektrische auto’s kan leiden tot een grote, tot op heden niet voorziene, toename van de belasting lokaal in het netwerk. | Calculating with simultaneity always assumes large numbers. The number of electric cars is still small. Moreover, the diversity of charging needs is significant. Additionally, consideration can be given to the possibility of charging car batteries during the day, in parking lots at shopping centers or at work. Specifically, the large number of electric cars can lead to a significant, previously unforeseen increase in the local load on the network. | capacities are connected simultaneously. This means that the additional peak load can range between 0.79 kW per car and 10 kW per car, based on the technology applied in 2010.
3.7 Decentrale opwekking | 3.7 Decentralized generation | parking lots at shopping centers or at work. Specifically, the large number of electric cars can lead to a significant, previously unforeseen increase in the local load on the network.
Decentrale opwekking is allang niet meer een marginaal verschijnsel in de distributienetten. De toegepaste systemen variëren van micro-WKK’s en PV-systemen in laagspanningsnetten tot aan grote WKK- en windenergiesystemen die op het middenspannings- en hoogspanningsnet worden aangesloten. Windturbines met elk een vermogen van 3 tot 5 MW, verzameld in windparken, voeden in op transportnetten op middenspannings- of hoogspanningsniveau. In warmtekrachtcentrales worden grote generatoren toegepast die, afhankelijk van hun vermogen, op het distributie- dan wel het transportnet zijn aangesloten. Maar ook grote hoeveelheden kleine generatoren, zoals in micro-WKK installaties, worden in toenemende mate in de LS-netten toegepast. Deze zijn meestal via converters aangesloten. | Decentralized generation is no longer a marginal phenomenon in distribution networks. The systems used range from micro-CHP units and PV systems in low-voltage networks to large CHP and wind energy systems connected to medium-voltage and high-voltage grids. Wind turbines with capacities of 3 to 5 MW each, grouped in wind farms, feed into transmission networks at medium-voltage or high-voltage levels. In combined heat and power plants, large generators are used, which, depending on their capacity, are connected to either the distribution or transmission network. Additionally, large numbers of small generators, such as those in micro-CHP installations, are increasingly being used in low-voltage networks. These are usually connected via converters. | shopping centers or at work. Specifically, the large number of electric cars can lead to a significant, previously unforeseen increase in the local load on the network. 3.7 Decentralized generation
Er worden in de literatuur uiteenlopende definities voor decentrale opwekking gehanteerd. De meeste definities zijn gebaseerd op het type technologie dat toegepast wordt, de impact op het milieu van de installatie, de grootte van het opgesteld vermogen van de installatie en het spanningsniveau waaraan de installatie is gekoppeld. Een definitie op basis van type technologie is lastig vanwege de grote diversiteit aan technologische ontwikkelingen, zoals WKK-systemen, PV-systemen en windmolens. Een definitie op basis van het spanningsniveau of op basis van de grootte van het opgesteld vermogen wordt ook wel gebruikt. De NMa hanteert geen specifieke definitie van decentrale opwekking, maar spreekt over (NMa 2009_2): | Various definitions for decentralized generation are used in the literature. Most definitions are based on the type of technology applied, the environmental impact of the installation, the size of the installed capacity of the installation, and the voltage level to which the installation is connected. A definition based on the type of technology is challenging due to the wide variety of technological developments, such as CHP systems, PV systems, and wind turbines. A definition based on the voltage level or the size of the installed capacity is also used. The NMa does not use a specific definition of decentralized generation but refers to (NMa 2009_2): | the distribution or transmission network. Additionally, large numbers of small generators, such as those in micro-CHP installations, are increasingly being used in low-voltage networks. These are usually connected via converters.
productiemiddel: een (deel van een) installatie bestemd voor het opwekken van elektriciteit, bestaande uit één of meer productie-eenheden | production facility: a (part of an) installation intended for generating electricity, consisting of one or more production units | on the voltage level or the size of the installed capacity is also used. The NMa does not use a specific definition of decentralized generation but refers to (NMa 2009_2):
productie-eenheid: een (deel van een) productiemiddel, dat zelfstandig (ofwel onafhankelijk van de andere delen van het desbetreffende productiemiddel) kan worden ingezet voor het opwekken van elektriciteit. Van een productie-eenheid kunnen één of meer generatoren deel uitmaken. | production unit: a (part of a) production facility that can independently (or independently of the other parts of the respective production facility) be used for generating electricity. A production unit can consist of one or more generators. | use a specific definition of decentralized generation but refers to (NMa 2009_2): production facility: a (part of an) installation intended for generating electricity, consisting of one or more production units
Daarnaast hanteert de NMa de term ‘duurzame elektriciteit’, die wordt opgewekt met hernieuwbare energiebronnen, zoals wind, zonne-energie, aardwarmte, golfenergie, getijdenenergie, waterkracht, biomassa, stortgas, rioolwaterzuiveringsgas en biogas (Elektriciteitswet 1998). Een groot gedeelte van de decentrale opwekking valt onder de noemer van duurzame elektriciteit. De productie van duurzame elektriciteit is gestegen van 6,0 procent van het binnenlands elektriciteitsverbruik in 2007 tot 7,5 procent in 2008. Dit komt door een toename van de elektriciteitsproductie uit windenergie en biomassa. | Additionally, the NMa uses the term 'sustainable electricity,' which is generated from renewable energy sources such as wind, solar energy, geothermal energy, wave energy, tidal energy, hydropower, biomass, landfill gas, sewage treatment gas, and biogas (Electricity Act 1998). A large portion of decentralized generation falls under the category of sustainable electricity. The production of sustainable electricity increased from 6.0 percent of domestic electricity consumption in 2007 to 7.5 percent in 2008. This increase is due to a rise in electricity production from wind energy and biomass. | facility that can independently (or independently of the other parts of the respective production facility) be used for generating electricity. A production unit can consist of one or more generators.
Figuur 3.25 Ontwikkeling van duurzame elektriciteit in Nederland (bron: CBS) | Figure 3.25 Development of sustainable electricity in the Netherlands (source: CBS) | increased from 6.0 percent of domestic electricity consumption in 2007 to 7.5 percent in 2008. This increase is due to a rise in electricity production from wind energy and biomass.
De elektriciteitsproductie uit windenergie was in 2008 een kwart hoger dan in 2007. Dit komt vooral doordat er veel nieuwe windmolens in gebruik zijn genomen. Windenergie is daarmee verantwoordelijk voor ongeveer de helft van de duurzame elektriciteitsproductie. Eind 2008 was de windmolencapaciteit 2216 megawatt, ongeveer 470 MW meer dan een jaar eerder (CBS, 2009). | Electricity production from wind energy was a quarter higher in 2008 than in 2007. This is mainly due to the commissioning of many new wind turbines. Wind energy is thus responsible for approximately half of the sustainable electricity production. At the end of 2008, wind turbine capacity was 2,216 megawatts, about 470 MW more than a year earlier (CBS, 2009). | 7.5 percent in 2008. This increase is due to a rise in electricity production from wind energy and biomass. Figure 3.25 Development of sustainable electricity in the Netherlands (source: CBS)
De generatoren van decentrale opwekkers zijn meestal uitgevoerd als synchrone machine en soms als asynchrone machine. Een synchrone generator heeft een rotor die zodanig bekrachtigd is dat deze zich gedraagt als een roterende magneet. De rotor draait in het elektromagnetische veld dat wordt opgewekt door de statorwikkelingen die op het elektriciteitsnet zijn aangesloten. Hierdoor is de synchrone machine gedwongen synchroon met het door het net bepaalde roterende veld mee te draaien. De frequentie van de spanning die door de synchrone generator wordt opgewekt moet 50 Hz bedragen. Een asynchrone generator heeft daarentegen een kortgesloten rotorwikkeling, waarin een stroom loopt waarvan de grootte en frequentie afhangen van het verschil in omwentelingsnelheid van de rotor ten opzichte van het ronddraaiende elektromagnetische veld van de statorwikkelingen. De asynchrone generator kan alleen vermogen opwekken indien hij sneller (dus asynchroon) dan het door het net bepaalde roterende veld draait. | The generators of decentralized producers are usually designed as synchronous machines and sometimes as asynchronous machines. A synchronous generator has a rotor that is energized in such a way that it behaves like a rotating magnet. The rotor rotates in the electromagnetic field generated by the stator windings that are connected to the power grid. As a result, the synchronous machine is forced to rotate in sync with the rotating field determined by the grid. The frequency of the voltage generated by the synchronous generator must be 50 Hz. An asynchronous generator, on the other hand, has a short-circuited rotor winding, in which a current flows whose magnitude and frequency depend on the difference in rotational speed of the rotor relative to the rotating electromagnetic field of the stator windings. The asynchronous generator can only generate power if it rotates faster (thus asynchronously) than the rotating field determined by the grid. | responsible for approximately half of the sustainable electricity production. At the end of 2008, wind turbine capacity was 2,216 megawatts, about 470 MW more than a year earlier (CBS, 2009).
Figuur 3.26 Synchrone generator voor groot vermogen | Figure 3.26 Synchronous generator for high power | to the rotating electromagnetic field of the stator windings. The asynchronous generator can only generate power if it rotates faster (thus asynchronously) than the rotating field determined by the grid.
Decentrale opwekking heeft invloed op het gedrag van stromen en spanningen in het distributienet. In het algemeen veroorzaakt een generator een stijging van de spanning en een toename van het kortsluitvermogen. Soms kan dit wenselijk zijn, maar soms niet. Een loadflow- en kortsluitberekening geeft hier meer inzicht in. Hierop wordt in de hoofdstukken 9 en 10 verder ingegaan. De maximale kortsluitstroom van via converters aangesloten generatoren is door de elektronica beperkt tot ongeveer de nominale stroom. Onderstaande systemen worden in de distributienetten en MS-transportnetten het meest toegepast. | Decentralized generation affects the behavior of currents and voltages in the distribution network. In general, a generator causes an increase in voltage and an increase in short-circuit power. Sometimes this can be desirable, but sometimes not. A load flow and short-circuit calculation provides more insight into this. This is further discussed in chapters 9 and 10. The maximum short-circuit current of generators connected via converters is limited by the electronics to approximately the nominal current. The following systems are most commonly used in distribution networks and medium-voltage transport networks. | stator windings. The asynchronous generator can only generate power if it rotates faster (thus asynchronously) than the rotating field determined by the grid. Figure 3.26 Synchronous generator for high power
Micro-WKK-systemen: 1 .. 5 kW per aansluiting | Micro-CHP systems: 1 .. 5 kW per connection | current of generators connected via converters is limited by the electronics to approximately the nominal current. The following systems are most commonly used in distribution networks and medium-voltage transport networks.
PV-systemen: 0,5 .. 2 kW per aansluiting | PV systems: 0.5 .. 2 kW per connection | by the electronics to approximately the nominal current. The following systems are most commonly used in distribution networks and medium-voltage transport networks. Micro-CHP systems: 1 .. 5 kW per connection
Windturbines: 1 .. 5 MW per aansluiting | Wind turbines: 1 .. 5 MW per connection | The following systems are most commonly used in distribution networks and medium-voltage transport networks. Micro-CHP systems: 1 .. 5 kW per connection PV systems: 0.5 .. 2 kW per connection
WKK-systemen bij tuinders: 100 .. 630 kW per aansluiting | CHP systems for horticulturists: 100 .. 630 kW per connection | distribution networks and medium-voltage transport networks. Micro-CHP systems: 1 .. 5 kW per connection PV systems: 0.5 .. 2 kW per connection Wind turbines: 1 .. 5 MW per connection
Grote WKK-systemen: 1 .. 20 MW per aansluiting | Large CHP systems: 1 .. 20 MW per connection | 5 kW per connection PV systems: 0.5 .. 2 kW per connection Wind turbines: 1 .. 5 MW per connection CHP systems for horticulturists: 100 .. 630 kW per connection
Grotere windturbines met een vermogen van 5 MW of meer en grote WKK-installaties kunnen niet zonder meer in het net worden opgenomen. Een nadere studie en een berekening van de effecten die gepaard gaan met het al dan niet leveren van elektrische energie aan het net en de gevolgen van kortsluiting in het net, moeten hierbij vooraf zijn uitgevoerd. | Larger wind turbines with a capacity of 5 MW or more and large CHP systems cannot be integrated into the grid without further consideration. A detailed study and calculation of the effects associated with supplying or not supplying electrical energy to the grid, as well as the consequences of a short circuit in the grid, must be conducted in advance. | kW per connection Wind turbines: 1 .. 5 MW per connection CHP systems for horticulturists: 100 .. 630 kW per connection Large CHP systems: 1 .. 20 MW per connection
3.7.1 Micro-WKK-systemen | 3.7.1 Micro-CHP Systems | the effects associated with supplying or not supplying electrical energy to the grid, as well as the consequences of a short circuit in the grid, must be conducted in advance.
In een groeiende hoeveelheid nieuwbouwprojecten worden woningen uitgerust met micro-WKK systemen. Deze systemen kunnen een relatief klein vermogen van 1 tot 5 kW per aansluiting leveren. De gelijktijdigheid van deze systemen is vrij groot. De elektriciteitsproductie volgt immers de warmtevraag. Die hangt af van het bewonerspatroon. Bij een relatief grote groep gelijksoortige woningen kan verwacht worden dat de warmtevraag gemiddeld genomen ook gelijksoortig is. Zo zullen bijvoorbeeld de meeste werkenden omstreeks 18:00 uur thuiskomen en zal tijdens koude dagen op dat moment de warmtevraag in woningen toenemen. Bij niet-werkenden zal de warmtevraag over de hele dag genomen minder sterk variëren. Het voordeel van deze vorm van decentrale opwekking is dat de meeste productie van elektriciteit grotendeels samenvalt met de vraag. Met name in de wintermaanden is de normale belasting van woonwijken in de avonduren vrij groot, zoals geïllustreerd in figuur 3.4. Als gevolg zal de netto belasting van een distributienet door de micro-WKK systemen afnemen. Het gedrag van de aangeslotenen is echter onzeker, zodat voor het verlagen van de piek uitgegaan mag worden van een schatting van de minimum opbrengst van de micro-WKK systemen. | In a growing number of new construction projects, homes are being equipped with micro-CHP systems. These systems can deliver a relatively small power output of 1 to 5 kW per connection. The simultaneity of these systems is quite high. After all, electricity production follows the heat demand, which depends on the residents' patterns. In a relatively large group of similar homes, it can be expected that the heat demand will also be similar on average. For example, most working people will come home around 6:00 PM, and during cold days, the heat demand in homes will increase at that time. For non-working people, the heat demand will vary less throughout the day. The advantage of this form of decentralized generation is that most electricity production largely coincides with the demand. Especially in the winter months, the normal load of residential areas in the evening hours is quite high, as illustrated in figure 3.4. As a result, the net load on a distribution network will decrease due to the micro-CHP systems. However, the behavior of the connected users is uncertain, so for reducing the peak, an estimate of the minimum output of the micro-CHP systems can be used. | with supplying or not supplying electrical energy to the grid, as well as the consequences of a short circuit in the grid, must be conducted in advance. 3.7.1 Micro-CHP Systems
In de laagspanningsnetten worden éénfase micro-WKK’s toegepast. Dit zijn voor netberekeningen redelijk eenvoudige componenten, die een specifiek gedrag vertonen in geval van starten en bij kortsluiting. Omdat de verwachting is dat deze opwekkers in de toekomst veelvuldig zullen worden toegepast, is het belangrijk om juist aan dit soort componenten specifiek aandacht te besteden. Met name het collectieve gedrag tijdens kortsluitingen en het gelijktijdig starten na herstel van de elektriciteitsvoorziening is onderwerp van studie in (toekomstige) projecten. | In the low-voltage networks, single-phase micro-CHP systems are used. These are relatively simple components for network calculations, exhibiting specific behavior during startup and in case of short circuits. Since it is expected that these generators will be widely used in the future, it is important to pay specific attention to these types of components. In particular, the collective behavior during short circuits and the simultaneous startup after the restoration of the power supply is a subject of study in (future) projects. | the micro-CHP systems. However, the behavior of the connected users is uncertain, so for reducing the peak, an estimate of the minimum output of the micro-CHP systems can be used.
Veel micro-WKK’s zijn uitgerust met een Stirlingmotor. Bij een Stirling machine vindt de verbranding van de brandstof buiten de motor plaats. Het arbeidsmedium, bijvoorbeeld lucht of helium, dat zich in de machine bevindt, verlaat deze nooit. De motor bestaat uit een koud deel en een warm deel. Deze zijn in figuur 3.27 aangegeven met blauw en rood. Een warmtebron, bijvoorbeeld de vlam van een gasbrander, of hete gassen van een verwarmingsketel, verwarmt voortdurend het warme deel van de motor terwijl het koude deel continu gekoeld wordt door bijvoorbeeld het retourcircuit van de verwarming. Beide delen, warm en koud, staan voortdurend met elkaar in verbinding. Het arbeidsmedium wordt door een verplaatser (bijna) zonder arbeid heen en weer geschoven tussen de hete en de koude ruimte, waarbij het medium in de hete ruimte onder het opnemen van warmte expandeert en arbeid verricht door een zuiger te bewegen. Vervolgens wordt de lucht door de verplaatser weer naar de koude ruimte bewogen, koelt daar af en neemt in volume af. Het arbeidsmedium, opgesloten in de motor, circuleert dus voortdurend van het warme naar het koude deel en omgekeerd en beweegt hierbij de zuiger heen en weer. De zuiger kan een lineaire generator aandrijven of via een overbrenging een meer conventionele roterende generator. | Many micro-CHP units are equipped with a Stirling engine. In a Stirling machine, the combustion of the fuel takes place outside the engine. The working medium, such as air or helium, that is inside the machine never leaves it. The engine consists of a cold part and a hot part. These are indicated in figure 3.27 with blue and red. A heat source, such as the flame of a gas burner or hot gases from a heating boiler, continuously heats the hot part of the engine while the cold part is continuously cooled by, for example, the return circuit of the heating system. Both parts, hot and cold, are constantly connected to each other. The working medium is moved back and forth between the hot and cold spaces by a displacer (almost) without work, where the medium in the hot space expands by absorbing heat and performs work by moving a piston. The air is then moved by the displacer back to the cold space, cools down there, and decreases in volume. The working medium, confined within the engine, thus continuously circulates from the hot part to the cold part and vice versa, moving the piston back and forth. The piston can drive a linear generator or, via a transmission, a more conventional rotary generator. | types of components. In particular, the collective behavior during short circuits and the simultaneous startup after the restoration of the power supply is a subject of study in (future) projects.
Figuur 3.27 Voorbeeld van een opengewerkte Stirlingmachine en het werkingsprincipe | Figure 3.27 Example of a cutaway Stirling engine and its operating principle | part to the cold part and vice versa, moving the piston back and forth. The piston can drive a linear generator or, via a transmission, a more conventional rotary generator.
Er zijn twee varianten voor de elektriciteitsopwekking in de micro-WKK’s. | There are two variants for electricity generation in micro-CHP systems. | and forth. The piston can drive a linear generator or, via a transmission, a more conventional rotary generator. Figure 3.27 Example of a cutaway Stirling engine and its operating principle
Het type Microgen is voorzien van een lineaire synchrone generator. | The Microgen type is equipped with a linear synchronous generator. | via a transmission, a more conventional rotary generator. Figure 3.27 Example of a cutaway Stirling engine and its operating principle There are two variants for electricity generation in micro-CHP systems.
Het type WhisperGen is voorzien van een gemodificeerde kortsluitanker­generator. | The WhisperGen type is equipped with a modified short-circuit armature generator. | Example of a cutaway Stirling engine and its operating principle There are two variants for electricity generation in micro-CHP systems. The Microgen type is equipped with a linear synchronous generator.
Microgen | Microgen | are two variants for electricity generation in micro-CHP systems. The Microgen type is equipped with a linear synchronous generator. The WhisperGen type is equipped with a modified short-circuit armature generator.
Deze generator is geen roterende machine. Het elektrische vermogen wordt opgewekt door een lineair trillende magneet, die via de zuiger van de Stirlingmachine wordt aangedreven. De generator is via een converter aan het net gekoppeld. | This generator is not a rotating machine. The electrical power is generated by a linearly oscillating magnet, which is driven by the piston of the Stirling engine. The generator is connected to the grid via a converter. | two variants for electricity generation in micro-CHP systems. The Microgen type is equipped with a linear synchronous generator. The WhisperGen type is equipped with a modified short-circuit armature generator. Microgen
WhisperGen | WhisperGen | The electrical power is generated by a linearly oscillating magnet, which is driven by the piston of the Stirling engine. The generator is connected to the grid via a converter.
De WhisperGen-WKK maakt gebruik van een gemodificeerde asynchrone generator die, via een overbrenging, door vier zuigers van de Stirlingmachine wordt aangedreven. De stator van de kleine asynchrone motor is gewikkeld als een 4-polige tweefasengenerator. De stroom in de hulpwikkeling is met behulp van een condensator 90 graden verschoven om een draaiveld te genereren. Figuur 3.28 illustreert dit aan de hand van het wikkelschema voor de stator. De hoofdwikkeling is met blauw aangegeven en de hulpwikkeling met rood. | The WhisperGen-CHP uses a modified asynchronous generator that is driven by four pistons of the Stirling engine via a transmission. The stator of the small asynchronous motor is wound as a 4-pole two-phase generator. The current in the auxiliary winding is shifted by 90 degrees using a capacitor to generate a rotating magnetic field. Figure 3.28 illustrates this with the winding diagram for the stator. The main winding is indicated in blue and the auxiliary winding in red. | electrical power is generated by a linearly oscillating magnet, which is driven by the piston of the Stirling engine. The generator is connected to the grid via a converter. WhisperGen
Figuur 3.28 Rotor en stator van gemodificeerde asynchrone generator | Figure 3.28 Rotor and stator of modified asynchronous generator | to generate a rotating magnetic field. Figure 3.28 illustrates this with the winding diagram for the stator. The main winding is indicated in blue and the auxiliary winding in red.
3.7.2 PV-systemen | 3.7.2 PV Systems | this with the winding diagram for the stator. The main winding is indicated in blue and the auxiliary winding in red. Figure 3.28 Rotor and stator of modified asynchronous generator
Zonlicht wordt met fotovoltaïsche cellen in zonnepanelen omgezet in gelijkspanning. Via een converter worden de zonnepanelen voor de vermogensoverdracht aan het net gekoppeld. Zonnepanelen hebben met de stand van de techniek in 2010 een vermogen van 100 tot 120 W per m | Sunlight is converted into direct current by photovoltaic cells in solar panels. Through a converter, the solar panels are connected to the grid for power transfer. As of 2010, solar panels have a power output of 100 to 120 W per m² with the current state of technology. | winding diagram for the stator. The main winding is indicated in blue and the auxiliary winding in red. Figure 3.28 Rotor and stator of modified asynchronous generator 3.7.2 PV Systems
2 | 2 | are connected to the grid for power transfer. As of 2010, solar panels have a power output of 100 to 120 W per m² with the current state of technology.
. In praktische situaties leidt dit tot vermogens van 0,5 tot 2 kW per aansluiting. Figuur 3.29 toont een PV systeem met 112 panelen. Deze zijn tezamen goed voor ruim 10 kW. Bij grootschalige toepassing kunnen deze PV-systemen op zomerse dagen zoveel elektriciteit produceren dat tijdens momenten van lage belasting de energievraag wijzigt in een energieoverschot, waardoor de energierichting in een LS-net omkeert. | In practical situations, this leads to power outputs of 0.5 to 2 kW per connection. Figure 3.29 shows a PV system with 112 panels. Together, these are good for over 10 kW. With large-scale application, these PV systems can produce so much electricity on summer days that during periods of low demand, the energy demand turns into an energy surplus, causing the energy flow direction in an LV network to reverse. | connected to the grid for power transfer. As of 2010, solar panels have a power output of 100 to 120 W per m² with the current state of technology. 2
De gelijktijdigheid van de elektriciteitsopbrengst van PV-systemen in een LS-distributienet is groot, vanwege de verhouding van het gebied dat de effecten van bewolking ondervindt tot de grootte van het gebied dat een distributiestation verzorgt. Een gelijktijdigheidsfactor van 1 kan gerust gebruikt worden voor het plannen van LS-distributienetten. Het verzorgingsgebied van een voedingsstation bestrijkt een vele malen groter gebied, waardoor de gelijktijdigheid van alle PV-systemen in geval van bewolking afneemt. Echter, tijdens een onbewolkte dag zullen alle PV-systemen maximaal produceren, zodat ook op de schaal van een MS-distributienet gerekend kan worden met een gelijktijdigheidsfactor van 1. De studies naar de invloeden van PV-systemen zullen zich voornamelijk afspelen op het vlak van de lokale LS-distributienetten. Hierbij zal met name gekeken worden naar de combinatie van maximale opbrengst en minimale belasting. | The simultaneity of electricity yield from PV systems in an LV distribution network is high, due to the ratio of the area affected by cloud cover to the size of the area served by a distribution station. A simultaneity factor of 1 can safely be used for planning LV distribution networks. The service area of a feeder station covers a much larger area, reducing the simultaneity of all PV systems in case of cloud cover. However, on a clear day, all PV systems will produce at maximum capacity, so a simultaneity factor of 1 can also be used on the scale of an MV distribution network. Studies on the impacts of PV systems will mainly focus on local LV distribution networks. These studies will particularly look at the combination of maximum yield and minimum load. | much electricity on summer days that during periods of low demand, the energy demand turns into an energy surplus, causing the energy flow direction in an LV network to reverse.
Figuur 3.29 10 kW PV-systeem op een boerderij | Figure 3.29 10 kW PV system on a farm | network. Studies on the impacts of PV systems will mainly focus on local LV distribution networks. These studies will particularly look at the combination of maximum yield and minimum load.
Figuur 3.30 Converters voor 20 kW PV-systeem | Figure 3.30 Converters for 20 kW PV system | mainly focus on local LV distribution networks. These studies will particularly look at the combination of maximum yield and minimum load. Figure 3.29 10 kW PV system on a farm
De PV-systemen zijn altijd aangesloten via een omvormer. Figuur 3.30 toont een systeem met drie converters voor een totaal vermogen van 20 kW. De PV-panelen leveren een gelijkspanning van ongeveer 40 tot 50 V, die moet worden geconverteerd. Hierdoor is het kortsluitvermogen altijd beperkt tot maximaal de nominale stroom van de omvormers. Een PV-systeem levert alleen vermogen wanneer het systeem aangesloten is op het 230 V distributienet. Ingeval van een storing stopt de converter met de productie. Dit is een veiligheidseis. | The PV systems are always connected via an inverter. Figure 3.30 shows a system with three converters for a total power of 20 kW. The PV panels provide a direct current voltage of approximately 40 to 50 V, which needs to be converted. As a result, the short-circuit power is always limited to the maximum nominal current of the inverters. A PV system only delivers power when the system is connected to the 230 V distribution network. In case of a malfunction, the converter stops production. This is a safety requirement. | studies will particularly look at the combination of maximum yield and minimum load. Figure 3.29 10 kW PV system on a farm Figure 3.30 Converters for 20 kW PV system
3.7.3 Windturbines | 3.7.3 Wind Turbines | PV system only delivers power when the system is connected to the 230 V distribution network. In case of a malfunction, the converter stops production. This is a safety requirement.
Windturbines hebben een nominaal vermogen van 1 tot 5 MW per windmolen. Meestal worden ze in windparken geclusterd in kleine tot vrij grote groepen. In het verleden werden deze windparken alleen op land geplaatst, maar steeds vaker worden grote windparken op zee aangelegd. Het potentieel voor de opbrengst van windenergie op zee wordt geschat op twee maal het totale Nederlandse energieverbruik. | Wind turbines have a nominal capacity of 1 to 5 MW per turbine. They are usually clustered in wind farms, ranging from small to fairly large groups. In the past, these wind farms were only placed on land, but increasingly, large wind farms are being built offshore. The potential yield of offshore wind energy is estimated to be twice the total Dutch energy consumption. | delivers power when the system is connected to the 230 V distribution network. In case of a malfunction, the converter stops production. This is a safety requirement. 3.7.3 Wind Turbines
Het vermogen van een enkele windturbine is te groot om op een laagspanningsnet te worden aangesloten. Een vermogen van 1 MW leidt in een LS-net al tot een stroom van 1,4 kA. Om deze reden worden windturbines op MS-niveau aangesloten. Grote windparken worden op HS-niveau aangesloten. | The power of a single wind turbine is too large to be connected to a low-voltage grid. A power of 1 MW already results in a current of 1.4 kA in an LV grid. For this reason, wind turbines are connected at the MV level. Large wind farms are connected at the HV level. | only placed on land, but increasingly, large wind farms are being built offshore. The potential yield of offshore wind energy is estimated to be twice the total Dutch energy consumption.
Er bestaan windturbines voor constant en voor variabel toerental. Bij windturbines met een vast toerental is de generator (een asynchrone machine) direct gekoppeld aan het net. Bij deze windturbines is elke fluctuatie in de windsnelheid direct merkbaar in het actieve vermogen. Windturbines met een variabel toerental worden geregeld met behulp van vermogenselektronica, waardoor fluctuaties in windsnelheid voor een groot deel kunnen worden opgeslagen in rotatie-energie van de rotor. Dit laatste zorgt ervoor dat bij windturbines met variabel toerental de geleverde energie weinig fluctuaties vertoont. | There are wind turbines for constant and variable rotational speeds. In wind turbines with a fixed rotational speed, the generator (an asynchronous machine) is directly connected to the grid. In these wind turbines, any fluctuation in wind speed is directly noticeable in the active power. Wind turbines with a variable rotational speed are controlled using power electronics, allowing fluctuations in wind speed to be largely stored in the rotational energy of the rotor. This ensures that wind turbines with variable rotational speed exhibit minimal fluctuations in the delivered energy. | in a current of 1.4 kA in an LV grid. For this reason, wind turbines are connected at the MV level. Large wind farms are connected at the HV level.
De nieuwe grote generatoren zijn meestal van het type DFIG (Doubly Fed Induction Generator), waarvan de statorwikkeling direct op het net is aangesloten en de rotorwikkeling via een converter. Door de frequentie van de stroom door de rotorwikkeling te variëren kan deze synchrone generator bij variabel toerental functioneren. Dit type windturbine en zijn gedrag is goed beschreven in de literatuur (Slootweg, 2003). Deze generatoren worden ingezet in windturbines voor vermogens tussen 1 en 5 MW. | The new large generators are usually of the DFIG (Doubly Fed Induction Generator) type, with the stator winding directly connected to the grid and the rotor winding connected via a converter. By varying the frequency of the current through the rotor winding, this synchronous generator can operate at variable rotational speeds. This type of wind turbine and its behavior is well described in the literature (Slootweg, 2003). These generators are used in wind turbines with capacities between 1 and 5 MW. | in wind speed to be largely stored in the rotational energy of the rotor. This ensures that wind turbines with variable rotational speed exhibit minimal fluctuations in the delivered energy.
Figuur 3.31 Opengewerkte windturbinegondel | Figure 3.31 Cutaway view of a wind turbine nacelle | This type of wind turbine and its behavior is well described in the literature (Slootweg, 2003). These generators are used in wind turbines with capacities between 1 and 5 MW.
Voor het vaststellen van de te verwachten elektriciteitsproductie is inzicht in de vermogenskarakteristiek van belang. De vermogenskarakteristiek van elke windturbine is zodanig dat beneden de cut-in windsnelheid het vermogen nul is. Boven deze windsnelheid is het elektrisch vermogen afhankelijk van de derde macht van de windsnelheid. Boven de nominale windsnelheid is het vermogen constant en gelijk aan het nominale vermogen. Boven de cut-out windsnelheid wordt de windturbine buiten bedrijf genomen om beschadigingen te voorkomen. | To determine the expected electricity production, understanding the power characteristic is important. The power characteristic of each wind turbine is such that below the cut-in wind speed, the power is zero. Above this wind speed, the electrical power depends on the cube of the wind speed. Above the nominal wind speed, the power is constant and equal to the nominal power. Above the cut-out wind speed, the wind turbine is taken out of operation to prevent damage. | well described in the literature (Slootweg, 2003). These generators are used in wind turbines with capacities between 1 and 5 MW. Figure 3.31 Cutaway view of a wind turbine nacelle
Figuur 3.32 Vermogenskarakteristiek van een windturbine | Figure 3.32 Power characteristic of a wind turbine | the nominal wind speed, the power is constant and equal to the nominal power. Above the cut-out wind speed, the wind turbine is taken out of operation to prevent damage.
3.7.4 Grote WKK-systemen | 3.7.4 Large CHP Systems | and equal to the nominal power. Above the cut-out wind speed, the wind turbine is taken out of operation to prevent damage. Figure 3.32 Power characteristic of a wind turbine
Een WKK-systeem wordt geplaatst om warmte, meestal met een hoge temperatuur te produceren. Deze warmte wordt gebruikt in de industrie, voor ruimteverwarming, in de tuinbouw of voor stadsverwarming. De WKK produceert hiervoor stoom of heet water en de restwarmte wordt gebruikt voor het opwekken van elektriciteit, die eventueel teruggeleverd wordt in het net. Door de gecombineerde opwekking in het WKK-systeem kan een hoog energetisch rendement worden behaald. | A CHP system is installed to produce heat, usually at a high temperature. This heat is used in industry, for space heating, in horticulture, or for district heating. The CHP produces steam or hot water for this purpose, and the residual heat is used to generate electricity, which can potentially be fed back into the grid. The combined generation in the CHP system can achieve a high energy efficiency. | nominal power. Above the cut-out wind speed, the wind turbine is taken out of operation to prevent damage. Figure 3.32 Power characteristic of a wind turbine 3.7.4 Large CHP Systems
Sinds 2006 is vooral in de glastuinbouw de elektriciteitsproductie sterk gestegen. Veel glastuinbouwbedrijven gebruiken een gasmotor voor de opwekking van elektriciteit en warmte. Hiermee verlichten en verwarmen ze hun kassen. Vanwege de hoogte van de energieprijzen is de verkoop van elektriciteit een aantrekkelijke extra inkomstenbron voor deze tuinders. Er zijn dan ook veel nieuwe gasmotoren geïnstalleerd, waardoor het elektrisch vermogen in deze sector in twee jaar tijd is verdubbeld. Aan het begin van 2008 bestond ruim 10 procent van het totale elektrische vermogen in Nederland uit productie-eenheden in de glastuinbouw (CBS, 2009). Inmiddels daalt dit percentage weer door de toename van conventionele centrales en WKK-centrales. | Since 2006, electricity production in greenhouse horticulture has increased significantly. Many greenhouse horticulture companies use a gas engine to generate electricity and heat. They use this to light and heat their greenhouses. Due to the high energy prices, selling electricity has become an attractive additional source of income for these growers. As a result, many new gas engines have been installed, doubling the electrical capacity in this sector within two years. At the beginning of 2008, more than 10 percent of the total electrical capacity in the Netherlands consisted of production units in greenhouse horticulture (CBS, 2009). This percentage has since decreased due to the increase in conventional power plants and CHP plants. | the residual heat is used to generate electricity, which can potentially be fed back into the grid. The combined generation in the CHP system can achieve a high energy efficiency.
Door de toename van de hoeveelheid decentrale opwekking met grote WKK-installaties kan de belasting van het MS-distributienet aanzienlijk veranderen. De gevolgen zijn sterk afhankelijk van de specifieke locatie in het net. Het is mogelijk dat het distributienet niet berekend is op veel decentrale invoeding. De richting van de vermogensstroom, traditioneel van een hoog naar een laag spanningsniveau, kan omkeren. Dit kan leiden tot minder of juist extra netkosten. Netverliezen kunnen toenemen, doordat de afstand van de opwekinstallatie tot de afnemer toe kan nemen, bijvoorbeeld als veel opwekkers in een perifere regio worden opgesteld. Aan de andere kant kunnen netverliezen afnemen doordat het elektrische vermogen dichter bij de verbruiker wordt opgewekt. | Due to the increase in the amount of decentralized generation with large CHP installations, the load on the medium voltage distribution network can change significantly. The consequences are highly dependent on the specific location in the network. It is possible that the distribution network is not designed for a lot of decentralized input. The direction of the power flow, traditionally from a high to a low voltage level, can reverse. This can lead to either reduced or increased network costs. Network losses can increase because the distance from the generation installation to the consumer can increase, for example, if many generators are set up in a peripheral region. On the other hand, network losses can decrease because the electrical power is generated closer to the consumer. | electrical capacity in the Netherlands consisted of production units in greenhouse horticulture (CBS, 2009). This percentage has since decreased due to the increase in conventional power plants and CHP plants.
De elektrische vermogens van WKK-installaties liggen in de ordegrootte van 0,1 tot 20 MW per aansluiting. Grotere vermogens komen ook voor. Een 10 kV-kabel met een aluminium geleider van 240 mm | The electrical capacities of CHP installations range from 0.1 to 20 MW per connection. Larger capacities also exist. A 10 kV cable with an aluminum conductor of 240 mm | for example, if many generators are set up in a peripheral region. On the other hand, network losses can decrease because the electrical power is generated closer to the consumer.
2 | 2 | consumer. The electrical capacities of CHP installations range from 0.1 to 20 MW per connection. Larger capacities also exist. A 10 kV cable with an aluminum conductor of 240 mm
mag belast worden met 5 MVA. Een vermogen van 20 MW is dan ook teveel om op het MS-distributienet aan te sluiten. Figuur 3.6 en figuur 3.7 illustreren metingen van voedingsstromen van 20 kV-strengen in kassengebieden. De patronen vertonen dagelijkse belastingschommelingen tot 17 MW tussen maximale vraag en aanbod. Deze schommelingen worden veroorzaakt door de som van de patronen van de belasting en van de opwekking. Met name in de glastuinbouw worden WKK-eenheden met vermogens van 3 tot 4 MW geclusterd. In tuindersgebieden komen clusters voor met vermogens tot 100 MW, die aangesloten zijn op het HS-net. De grootte van een complete installatie wordt dan mede bepaald door de omvang van het betreffende kassengebied. | may be loaded with 5 MVA. A capacity of 20 MW is therefore too much to connect to the medium-voltage distribution network. Figures 3.6 and 3.7 illustrate measurements of power flows of 20 kV lines in greenhouse areas. The patterns show daily load fluctuations up to 17 MW between maximum demand and supply. These fluctuations are caused by the sum of the patterns of the load and the generation. Particularly in greenhouse horticulture, CHP units with capacities of 3 to 4 MW are clustered. In horticultural areas, clusters with capacities up to 100 MW are connected to the high-voltage network. The size of a complete installation is then partly determined by the size of the respective greenhouse area. | The electrical capacities of CHP installations range from 0.1 to 20 MW per connection. Larger capacities also exist. A 10 kV cable with an aluminum conductor of 240 mm 2
Tuinders produceren niet alleen elektriciteit naar de eigen warmte- en elektriciteitsbehoefte maar ook volgens de marktvraag naar elektrische energie. Bij een hoge kWh-prijs kunnen zij extra elektriciteit produceren en bij een lage kWh-prijs kunnen zij zelfs elektriciteit inkopen. Het is niet zozeer een energietechnische maar een economische afweging. De maximale elektriciteitsproductie hoeft dus niet samen te vallen met de maximale lokale elektriciteitsvaag. Voor het aansluiten van dergelijke grote installaties moet daarom altijd een gedegen studie worden uitgevoerd, waarbij uitgegaan wordt van de extreme situaties van maximale opwekking tegelijk met minimale belasting en minimale opwekking tegelijk met maximale belasting. De capaciteit van het MS-net is beperkt, zodat voor het aansluiten van een groot cluster in veel gevallen een netverzwaring nodig is. In extreme gevallen is zelfs verzwaring van het HS-net nodig. | Growers not only produce electricity to meet their own heat and electricity needs but also according to market demand for electrical energy. When the kWh price is high, they can produce extra electricity, and when the kWh price is low, they can even purchase electricity. It is more of an economic consideration than an energy-technical one. Therefore, the maximum electricity production does not necessarily coincide with the maximum local electricity demand. For connecting such large installations, a thorough study must always be conducted, considering extreme situations of maximum generation coinciding with minimum load and minimum generation coinciding with maximum load. The capacity of the medium-voltage network is limited, so in many cases, a network upgrade is necessary to connect a large cluster. In extreme cases, even an upgrade of the high-voltage network is required. | with capacities up to 100 MW are connected to the high-voltage network. The size of a complete installation is then partly determined by the size of the respective greenhouse area.
3.8 Motoren | 3.8 Motors | medium-voltage network is limited, so in many cases, a network upgrade is necessary to connect a large cluster. In extreme cases, even an upgrade of the high-voltage network is required.
Motoren worden veelvuldig toegepast in de industrie en vormen daar het grootste deel van de belasting. Bij het dimensioneren van industriële netten moet terdege rekening gehouden worden met het gedrag van de motoren. Met name bij het starten van de motor en bij het optreden van een kortsluiting in het net is de invloed van de motor merkbaar. Het starten van een motor vraagt kortstondig een grote stroom van 4 tot 8 maal de nominale stroom, hetgeen leidt tot een spanningsdip. Deze aanloopstroom kan worden beperkt door het toepassen van een sterdriehoek schakeling, een softstarter of een frequentieomvormer. Indien een motor wordt bestuurd met behulp van vermogenselektronica, kan dit leiden tot toename van de harmonische vervorming van de wisselspanning. Indien een kortsluiting in het net optreedt, zullen de motoren bijdragen aan de kortsluitstroom waardoor deze op de kortsluitplaats vergroot wordt. De invloed van motoren is in de meeste distributienetten gering. In een situatie dat in een industriële omgeving vele en grote motoren zijn toegepast, kan het echter nodig zijn hun invloed op het net nader te bestuderen. | Motors are frequently used in industry and constitute the majority of the load. When designing industrial networks, the behavior of the motors must be carefully considered. The influence of the motor is particularly noticeable when starting the motor and when a short circuit occurs in the network. Starting a motor briefly requires a large current, 4 to 8 times the nominal current, which leads to a voltage dip. This inrush current can be limited by using a star-delta connection, a soft starter, or a frequency converter. If a motor is controlled using power electronics, this can lead to an increase in the harmonic distortion of the alternating voltage. If a short circuit occurs in the network, the motors will contribute to the short-circuit current, thereby increasing it at the short-circuit location. The influence of motors is minimal in most distribution networks. However, in an industrial environment where many large motors are used, it may be necessary to further study their impact on the network. | is limited, so in many cases, a network upgrade is necessary to connect a large cluster. In extreme cases, even an upgrade of the high-voltage network is required. 3.8 Motors
Wisselstroommotoren bestaan in de uitvoeringsvormen van de synchrone en de asynchrone machine. De synchrone motor heeft dezelfde constructie als de synchrone generator. Grote synchrone motoren worden bijna uitsluitend in de industrie toegepast. De asynchrone motor heeft een kortgesloten rotorwikkeling. Deze motoren worden ook wel inductiemotor of kortsluitankermotor genoemd. Bij nullast draait de asynchrone motor iets langzamer dan het synchrone toerental. Indien de motor wordt belast, zal hij nog iets langzamer gaan lopen. Dit gedrag is vastgelegd in de koppel-toerenkromme van de motor. Bij toename van de belasting zal de motor een punt bereiken waarbij de motor het gevraagde koppel niet meer kan leveren. De motor zal dan tot stilstand komen. Het punt waarop dit gebeurt, wordt aangeduid met het kippkoppel. Bij stilstand zal de motor een stroom trekken die gelijk is aan de aanloopstroom. | Alternating current motors exist in the forms of synchronous and asynchronous machines. The synchronous motor has the same construction as the synchronous generator. Large synchronous motors are almost exclusively used in industry. The asynchronous motor has a squirrel-cage rotor winding. These motors are also known as induction motors or squirrel-cage motors. At no load, the asynchronous motor runs slightly slower than the synchronous speed. If the motor is loaded, it will run even slower. This behavior is depicted in the torque-speed curve of the motor. As the load increases, the motor will reach a point where it can no longer deliver the required torque. The motor will then come to a stop. The point at which this occurs is referred to as the pull-out torque. When stopped, the motor will draw a current equal to the starting current. | motors is minimal in most distribution networks. However, in an industrial environment where many large motors are used, it may be necessary to further study their impact on the network.
Figuur 3.33 Asynchrone machine | Figure 3.33 Asynchronous machine | come to a stop. The point at which this occurs is referred to as the pull-out torque. When stopped, the motor will draw a current equal to the starting current.
Motoren kunnen direct op het net (DOL, Direct On Line) zijn aangesloten. In dat geval moet rekening gehouden worden met de grootste aanloopstroom. Om de aanloopstroom te beperken kunnen de wikkelingen bij sommige uitvoeringen tijdelijk van driehoek naar ster worden geschakeld. Hierbij krijgen de wikkelingen tijdens het aanlopen een spanning die een factor √3 lager is dan normaal. Motoren kunnen ook met behulp van een softstarter aanlopen. Hiermee wordt de aanloopstroom beperkt tot ongeveer de nominale stroom. Motoren waarvan het toerental geregeld wordt, zijn via een frequentieomvormer op het net aangesloten. Deze converters beperken de aanloopstroom tot ongeveer de nominale stroom. | Motors can be connected directly to the grid (DOL, Direct On Line). In that case, the highest starting current must be taken into account. To limit the starting current, the windings in some designs can be temporarily switched from delta to star. In this configuration, the windings receive a voltage during startup that is a factor of √3 lower than normal. Motors can also start using a soft starter. This limits the starting current to approximately the nominal current. Motors with adjustable speed are connected to the grid via a frequency converter. These converters limit the starting current to approximately the nominal current. | The point at which this occurs is referred to as the pull-out torque. When stopped, the motor will draw a current equal to the starting current. Figure 3.33 Asynchronous machine
Asynchrone motoren leveren in geval van kortsluiting in het net een kortstondige bijdrage aan de kortsluitstroom, die ongeveer gelijk is aan de aanloopstroom. Motoren die via een frequentieomvormer zijn aangesloten leveren in de regel geen bijdrage aan de kortsluitstroom. In het geval dat de frequentieomvormer teruglevering mogelijk maakt is de kortsluitstroombijdrage beperkt tot ongeveer de nominale stroom. | Asynchronous motors provide a brief contribution to the short-circuit current in the event of a short circuit in the grid, which is approximately equal to the starting current. Motors connected via a frequency converter generally do not contribute to the short-circuit current. If the frequency converter allows for feedback, the short-circuit current contribution is limited to approximately the nominal current. | current to approximately the nominal current. Motors with adjustable speed are connected to the grid via a frequency converter. These converters limit the starting current to approximately the nominal current.
Motorbesturing | Motorbesturing | via a frequency converter generally do not contribute to the short-circuit current. If the frequency converter allows for feedback, the short-circuit current contribution is limited to approximately the nominal current.
Aanloopstroom | Aanloopstroom | a frequency converter generally do not contribute to the short-circuit current. If the frequency converter allows for feedback, the short-circuit current contribution is limited to approximately the nominal current. Motorbesturing
Kortsluitstroombijdrage | Kortsluitstroombijdrage | frequency converter generally do not contribute to the short-circuit current. If the frequency converter allows for feedback, the short-circuit current contribution is limited to approximately the nominal current. Motorbesturing Aanloopstroom
Direct op het net | Directly on the grid | converter generally do not contribute to the short-circuit current. If the frequency converter allows for feedback, the short-circuit current contribution is limited to approximately the nominal current. Motorbesturing Aanloopstroom Kortsluitstroombijdrage
6 .. 8 x nominale stroom | 6 .. 8 x nominal current | contribute to the short-circuit current. If the frequency converter allows for feedback, the short-circuit current contribution is limited to approximately the nominal current. Motorbesturing Aanloopstroom Kortsluitstroombijdrage Directly on the grid
6 .. 8 x nominale stroom | 6 .. 8 x nominal current | the frequency converter allows for feedback, the short-circuit current contribution is limited to approximately the nominal current. Motorbesturing Aanloopstroom Kortsluitstroombijdrage Directly on the grid 6 .. 8 x nominal current
Softstarter | Softstarter | the short-circuit current contribution is limited to approximately the nominal current. Motorbesturing Aanloopstroom Kortsluitstroombijdrage Directly on the grid 6 .. 8 x nominal current 6 .. 8 x nominal current
ongeveer nominale stroom | approximately nominal current | short-circuit current contribution is limited to approximately the nominal current. Motorbesturing Aanloopstroom Kortsluitstroombijdrage Directly on the grid 6 .. 8 x nominal current 6 .. 8 x nominal current Softstarter
6 .. 8 x nominale stroom | 6 .. 8 x nominal current | is limited to approximately the nominal current. Motorbesturing Aanloopstroom Kortsluitstroombijdrage Directly on the grid 6 .. 8 x nominal current 6 .. 8 x nominal current Softstarter approximately nominal current
Converter | Converter | current. Motorbesturing Aanloopstroom Kortsluitstroombijdrage Directly on the grid 6 .. 8 x nominal current 6 .. 8 x nominal current Softstarter approximately nominal current 6 .. 8 x nominal current
ongeveer nominale stroom | approximately nominal current | Motorbesturing Aanloopstroom Kortsluitstroombijdrage Directly on the grid 6 .. 8 x nominal current 6 .. 8 x nominal current Softstarter approximately nominal current 6 .. 8 x nominal current Converter
geen bijdrage of ongeveer nominale stroom | no contribution or approximately nominal current | Directly on the grid 6 .. 8 x nominal current 6 .. 8 x nominal current Softstarter approximately nominal current 6 .. 8 x nominal current Converter approximately nominal current
3.9 Onderscheid problematiek op MS- en LS-niveau | 3.9 Distinguishing Issues at MV and LV Levels | 8 x nominal current 6 .. 8 x nominal current Softstarter approximately nominal current 6 .. 8 x nominal current Converter approximately nominal current no contribution or approximately nominal current
Op laagspanningsniveau worden de netten meestal gekarakteriseerd door grote aantallen kleine afnemers. Het is meestal gerechtvaardigd om over afnemers te spreken omdat zij voornamelijk elektriciteit verbruiken. De voorzieningsgebieden op LS-niveau zijn meestal van dien aard dat de afnemers een voorspelbaar en gelijksoortig karakter hebben. Het is daarom gebruikelijk om te werken met specifieke belastingstypen en gebruik te maken van de gelijktijdigheid van de afnemers. Ook indien de gebruikers zelf elektriciteit opwekken met behulp van bijvoorbeeld PV-systemen, is het nog gerechtvaardigd om op deze manier te werken. | At the low voltage level, the networks are usually characterized by large numbers of small consumers. It is generally justified to refer to them as consumers because they primarily consume electricity. The supply areas at the LV level are typically such that the consumers have a predictable and similar character. Therefore, it is common to work with specific load types and to utilize the simultaneity of the consumers. Even if the users generate electricity themselves using, for example, PV systems, it is still justified to work in this manner. | nominal current Softstarter approximately nominal current 6 .. 8 x nominal current Converter approximately nominal current no contribution or approximately nominal current 3.9 Distinguishing Issues at MV and LV Levels
Bij introductie van grote elektriciteitsverbruikers, zoals de elektrische auto en ruimteverwarming met behulp van warmtepompen en elektrische bijverwarming, volstaat het niet meer om rekening te houden met de ongelijktijdigheid van de elektriciteitsvraag van alle afnemers en moet rekening gehouden worden met het feit dat grote elektriciteitsverbruikers gelijktijdig in bedrijf zijn. Ten aanzien van de toekomstige ontwikkelingen zijn de onzekerheden het grootst in de laagspanningsnetten. Als gevolg hiervan zal bij nieuwbouw van netten steeds meer ontworpen worden op basis van de som van de individuele maximale belastingen. Hierom ontstaat de trend dat de netontwerper zich steeds meer gaat indekken voor deze toekomstige onzekerheden en zal hij het laagspanningsnet zo zwaar mogelijk gaan ontwerpen: met maximale kabeldoorsneden, van bijvoorbeeld 150 mm | With the introduction of large electricity consumers, such as electric cars and space heating using heat pumps and electric auxiliary heating, it is no longer sufficient to consider the non-simultaneity of the electricity demand of all consumers. Instead, it is necessary to account for the fact that large electricity consumers are operating simultaneously. Regarding future developments, the uncertainties are greatest in low-voltage networks. As a result, new network constructions will increasingly be designed based on the sum of individual maximum loads. Consequently, there is a trend that network designers will increasingly hedge against these future uncertainties by designing the low-voltage network as robustly as possible: with maximum cable cross-sections, for example, 150 mm. | types and to utilize the simultaneity of the consumers. Even if the users generate electricity themselves using, for example, PV systems, it is still justified to work in this manner.
2 | 2 | is a trend that network designers will increasingly hedge against these future uncertainties by designing the low-voltage network as robustly as possible: with maximum cable cross-sections, for example, 150 mm.
aluminium geleider, en een zo groot mogelijke distributietransformator, van bijvoorbeeld 630 kVA. Ook zal de netontwerper bij nieuwbouw extra ruimte claimen om in de toekomst, mocht het nodig blijken, extra netruimten te kunnen plaatsen en zo toekomstige kosten zoveel mogelijk te vermijden. | aluminum conductor, and the largest possible distribution transformer, for example, 630 kVA. Additionally, the network designer will claim extra space in new constructions to potentially place additional network spaces in the future if necessary, thereby avoiding future costs as much as possible. | a trend that network designers will increasingly hedge against these future uncertainties by designing the low-voltage network as robustly as possible: with maximum cable cross-sections, for example, 150 mm. 2
Op MS-niveau moet goed worden gerealiseerd of het net aansluitingen bedient die een afwijkend gedrag vertonen. Naast de distributiestations, die grote groepen laagspanningsklanten bedienen, komen namelijk ook kleine hoeveelheden aansluitingen van grote vermogens voor, die als functie van de tijd een afwijkend belastingspatroon vertonen. Met name de decentrale opwekking op MS-niveau vertoont een gedrag dat niet eenvoudig met gelijktijdigheidsfactoren te modelleren is. Indien het gedrag van de belasting op opwekking van een grote klant goed bekend is, kan met belastingspatronen worden gewerkt. Er wordt dan meer specifiek gekeken naar de belasting en opwekking in de loop van een bepaalde periode. Het net moet dan voor alle situaties geschikt zijn voor de te distribueren vermogens. Indien het gedrag onbekend is en niet betrouwbaar vastgesteld kan worden, kan alleen worden volstaan door rekening te houden met extreme situaties in opwekking en belasting. In dat geval moet bij het analyseren van het MS-net ten aanzien van deze klanten worden uitgegaan van maximale belasting en minimale productie en minimale belasting en maximale productie, uiteraard in combinatie met de overige belastingen in het net. | At the medium voltage (MV) level, it must be carefully considered whether the network serves connections that exhibit abnormal behavior. In addition to the distribution stations that serve large groups of low-voltage customers, there are also small numbers of high-capacity connections that show varying load patterns over time. Specifically, decentralized generation at the MV level exhibits behavior that cannot be easily modeled with coincidence factors. If the load behavior of a large customer's generation is well known, load patterns can be used. In such cases, the focus is more specifically on the load and generation over a certain period. The network must then be suitable for distributing power in all situations. If the behavior is unknown and cannot be reliably determined, it is only possible to account for extreme situations in generation and load. In that case, when analyzing the MV network concerning these customers, one must assume maximum load and minimum production, and minimum load and maximum production, of course in combination with the other loads in the network. | Additionally, the network designer will claim extra space in new constructions to potentially place additional network spaces in the future if necessary, thereby avoiding future costs as much as possible.