## Sheet1
Original Text | Translated Text | Previous Context
Intelligente netten | Smart grids
Hoofdstuk 15 geeft een beschrijving van de ontwikkelingen rond de intelligente netten en de mogelijke gevolgen voor het ontwerp en de bedrijfsvoering van de netten. De ontwikkelingen gaan snel, waardoor de in dit hoofdstuk besproken zaken snel verouderen. | Chapter 15 provides a description of the developments surrounding smart grids and the potential implications for the design and operation of the grids. The developments are progressing rapidly, causing the topics discussed in this chapter to quickly become outdated. | Smart grids
15 Intelligente netten | 15 Smart Grids | smart grids and the potential implications for the design and operation of the grids. The developments are progressing rapidly, causing the topics discussed in this chapter to quickly become outdated.
15.1 Wat is een intelligent net? | 15.1 What is a smart grid? | the potential implications for the design and operation of the grids. The developments are progressing rapidly, causing the topics discussed in this chapter to quickly become outdated. 15 Smart Grids
15.2 Waarom intelligente netten? | 15.2 Why smart grids? | and operation of the grids. The developments are progressing rapidly, causing the topics discussed in this chapter to quickly become outdated. 15 Smart Grids 15.1 What is a smart grid?
15.3 Hoe zit een intelligent net in elkaar? | 15.3 How is a smart grid structured? | grids. The developments are progressing rapidly, causing the topics discussed in this chapter to quickly become outdated. 15 Smart Grids 15.1 What is a smart grid? 15.2 Why smart grids?
15.3.1 Intelligent MS-distributienet met gecombineerde netstructuur | 15.3.1 Intelligent MV distribution network with combined network structure | the topics discussed in this chapter to quickly become outdated. 15 Smart Grids 15.1 What is a smart grid? 15.2 Why smart grids? 15.3 How is a smart grid structured?
15.3.2 MS-distributienet met intelligent knooppunt in de open ring | 15.3.2 MV distribution network with intelligent node in the open ring | outdated. 15 Smart Grids 15.1 What is a smart grid? 15.2 Why smart grids? 15.3 How is a smart grid structured? 15.3.1 Intelligent MV distribution network with combined network structure
15.3.3 Eerste stap naar een MS-distributienet met automatisering in de onderstations | 15.3.3 First step towards an MV distribution network with automation in the substations | Why smart grids? 15.3 How is a smart grid structured? 15.3.1 Intelligent MV distribution network with combined network structure 15.3.2 MV distribution network with intelligent node in the open ring
15.3.4 LS-distributienet | 15.3.4 LV distribution network | distribution network with combined network structure 15.3.2 MV distribution network with intelligent node in the open ring 15.3.3 First step towards an MV distribution network with automation in the substations
15.4 Technieken | 15.4 Techniques | network structure 15.3.2 MV distribution network with intelligent node in the open ring 15.3.3 First step towards an MV distribution network with automation in the substations 15.3.4 LV distribution network
15.4.1 Afstemmen van belasting op opwekking | 15.4.1 Balancing load with generation | 15.3.2 MV distribution network with intelligent node in the open ring 15.3.3 First step towards an MV distribution network with automation in the substations 15.3.4 LV distribution network 15.4 Techniques
15.4.2 Regelen in een laagspanningsnet | 15.4.2 Control in a low-voltage network | intelligent node in the open ring 15.3.3 First step towards an MV distribution network with automation in the substations 15.3.4 LV distribution network 15.4 Techniques 15.4.1 Balancing load with generation
15.4.3 Opslagsystemen | 15.4.3 Storage Systems | 15.3.3 First step towards an MV distribution network with automation in the substations 15.3.4 LV distribution network 15.4 Techniques 15.4.1 Balancing load with generation 15.4.2 Control in a low-voltage network
15.5 Toepassingen | 15.5 Applications | towards an MV distribution network with automation in the substations 15.3.4 LV distribution network 15.4 Techniques 15.4.1 Balancing load with generation 15.4.2 Control in a low-voltage network 15.4.3 Storage Systems
15.5.1 Het Mobile Smart Grid concept | 15.5.1 The Mobile Smart Grid concept | MV distribution network with automation in the substations 15.3.4 LV distribution network 15.4 Techniques 15.4.1 Balancing load with generation 15.4.2 Control in a low-voltage network 15.4.3 Storage Systems 15.5 Applications
15.5.2 Opslag van elektrische energie | 15.5.2 Storage of electrical energy | the substations 15.3.4 LV distribution network 15.4 Techniques 15.4.1 Balancing load with generation 15.4.2 Control in a low-voltage network 15.4.3 Storage Systems 15.5 Applications 15.5.1 The Mobile Smart Grid concept
15.5.3 Intelligent distributiestation | 15.5.3 Intelligent Distribution Station | network 15.4 Techniques 15.4.1 Balancing load with generation 15.4.2 Control in a low-voltage network 15.4.3 Storage Systems 15.5 Applications 15.5.1 The Mobile Smart Grid concept 15.5.2 Storage of electrical energy
15 Intelligente netten | 15 Intelligent Grids | Balancing load with generation 15.4.2 Control in a low-voltage network 15.4.3 Storage Systems 15.5 Applications 15.5.1 The Mobile Smart Grid concept 15.5.2 Storage of electrical energy 15.5.3 Intelligent Distribution Station
De wereldwijd ingezette energietransitie probeert de overgang te bewerkstelligen van een op fossiele brandstoffen gebaseerde energievoorziening naar een volledig duurzame energievoorziening. Hierbij ontstaat een verschuiving van het gebruik van gas voor cv-ketels naar de inzet van elektrische warmtepompen voor ruimteverwarming en van het gebruik van benzine voor auto's naar biogas of elektrisch rijden. Grootschalige introductie van elektrisch rijden kan resulteren in een verdubbeling van het huidige huishoudelijke elektriciteitsverbruik. Toepassing van warmtepompen voor ruimteverwarming kan in bestaande situaties eveneens tot een verdubbeling leiden. Om de energievoorziening bij dit soort ontwikkelingen te blijven waarborgen zouden de bestaande distributienetten verzwaard moeten worden. Vanwege de omvang en de kosten hiervan is dit niet altijd een geaccepteerde oplossing. | The global energy transition aims to shift from a fossil fuel-based energy supply to a fully sustainable energy supply. This involves a transition from using gas for central heating boilers to using electric heat pumps for space heating, and from using gasoline for cars to using biogas or electric vehicles. Large-scale introduction of electric vehicles can result in a doubling of current household electricity consumption. The use of heat pumps for space heating can also lead to a doubling in existing situations. To ensure the energy supply for these kinds of developments, the existing distribution networks would need to be reinforced. Due to the scale and costs involved, this is not always an acceptable solution. | generation 15.4.2 Control in a low-voltage network 15.4.3 Storage Systems 15.5 Applications 15.5.1 The Mobile Smart Grid concept 15.5.2 Storage of electrical energy 15.5.3 Intelligent Distribution Station 15 Intelligent Grids
Ontwikkelingen in het kader van de energietransitie leiden ook tot een toename van duurzame decentrale opwekking. Helaas laat duurzaam opgewekte elektriciteit zich niet altijd sturen zodat gezocht moet worden naar mogelijkheden om de vraag af te stemmen op het beschikbare duurzame aanbod uit zon en wind. Een natuurkundig probleem hierbij is dat aanbod en vraag van elektrische energie op elk moment in evenwicht moeten zijn, terwijl dit bij het toepassen van duurzame bronnen zonder buffersystemen niet zondermeer mogelijk is. In de loop van tijd zal de behoefte ontstaan aan een meer aanbodvolgend systeem in plaats van een puur vraagvolgend systeem. Het bestaande conventionele distributienet is een vraagvolgend systeem en is niet voor deze ontwikkelingen ontworpen. Het is daarom belangrijk om inzicht te krijgen in de ontwikkelingen van en de maatschappelijke behoefte aan deze nieuwe energiebehoeften, waardoor inzicht kan worden ontwikkeld in de bijbehorende energiestromen. Het gedrag van klanten die beschikken over een elektrische auto, warmtepompsysteem, zonnepanelen en micro-WKK's is nog niet voldoende bekend. Het is de vraag of gerekend kan worden op spreiding van de energievraag over de dag of dat rekening moet worden gehouden met nieuwe pieken in het verbruik, bijvoorbeeld bij ingang van het nachttarief. Toepassing van op afstand uitleesbare elektriciteitsmeters kan daarbij helpen de ontwikkelingen te bewaken. | Developments in the context of the energy transition also lead to an increase in sustainable decentralized generation. Unfortunately, sustainably generated electricity cannot always be controlled, so it is necessary to look for ways to match demand with the available sustainable supply from solar and wind. A physical problem here is that the supply and demand of electrical energy must be balanced at all times, while this is not inherently possible when using sustainable sources without buffer systems. Over time, the need will arise for a more supply-following system instead of a purely demand-following system. The existing conventional distribution network is a demand-following system and is not designed for these developments. Therefore, it is important to gain insight into the developments and societal needs for these new energy demands, thereby developing an understanding of the associated energy flows. The behavior of customers who have an electric car, heat pump system, solar panels, and micro-CHP units is not yet sufficiently known. The question is whether we can count on the distribution of energy demand throughout the day or if new peaks in consumption should be anticipated, for example, at the start of the night rate. The application of remotely readable electricity meters can help monitor these developments. | energy supply for these kinds of developments, the existing distribution networks would need to be reinforced. Due to the scale and costs involved, this is not always an acceptable solution.
Om de continuïteit en de kwaliteit van de levering van elektrische energie in de toekomst te waarborgen en de ontwikkelingen van elektriciteitsproductie met duurzame bronnen te faciliteren, wordt gezocht naar mogelijkheden om het distributienet 'intelligent' te maken. | To ensure the continuity and quality of electricity supply in the future and to facilitate the development of electricity production from sustainable sources, possibilities are being explored to make the distribution network 'intelligent.' | or if new peaks in consumption should be anticipated, for example, at the start of the night rate. The application of remotely readable electricity meters can help monitor these developments.
15.1 Wat is een intelligent net? | 15.1 What is an intelligent grid? | continuity and quality of electricity supply in the future and to facilitate the development of electricity production from sustainable sources, possibilities are being explored to make the distribution network 'intelligent.'
De term 'intelligent net' of 'smart grid' is een overkoepelend concept waar verschillende innovatieve ontwikkelingen rond energie-infrastructuur in passen (Taskforce, 2010). Er zijn vele definities van een intelligent net. Het European Technology Platform hanteert als definitie (ETP, 2010): 'Een intelligent net is een elektriciteitsnet dat op een intelligente wijze omgaat met het gedrag en de acties van alle aangeslotenen (producenten, afnemers en diegenen die beide doen) teneinde te komen tot een economisch efficiënt en duurzaam elektriciteitsvoorzieningsysteem met weinig verliezen, hoge kwaliteit, betrouwbaarheid en veiligheid.' In een intelligent net worden op basis van meetgegevens componenten en systemen aangestuurd en geregeld om zodoende de kwaliteit van de elektriciteitsvoorziening te waarborgen. | The term 'intelligent grid' or 'smart grid' is an overarching concept that encompasses various innovative developments related to energy infrastructure (Taskforce, 2010). There are many definitions of an intelligent grid. The European Technology Platform defines it as follows (ETP, 2010): 'An intelligent grid is an electricity network that intelligently manages the behavior and actions of all connected parties (producers, consumers, and those who do both) in order to achieve an economically efficient and sustainable electricity supply system with minimal losses, high quality, reliability, and safety.' In an intelligent grid, components and systems are controlled and regulated based on measurement data to ensure the quality of the electricity supply. | in the future and to facilitate the development of electricity production from sustainable sources, possibilities are being explored to make the distribution network 'intelligent.' 15.1 What is an intelligent grid?
Volgens hetzelfde European Technology Platform gebruikt een intelligent net innovatieve producten en diensten, in combinatie met intelligente meting, besturing, communicatie en zelfherstellende technieken, om in de toekomst, vergeleken met de huidige situatie: | According to the same European Technology Platform, an intelligent grid uses innovative products and services, in combination with intelligent measurement, control, communication, and self-healing techniques, to ensure that in the future, compared to the current situation: | minimal losses, high quality, reliability, and safety.' In an intelligent grid, components and systems are controlled and regulated based on measurement data to ensure the quality of the electricity supply.
het aansluiten en bedrijfsvoeren van opwekeenheden van elke grootte beter te ondersteunen | to better support the connection and operation of generation units of any size | Platform, an intelligent grid uses innovative products and services, in combination with intelligent measurement, control, communication, and self-healing techniques, to ensure that in the future, compared to the current situation:
het mogelijk te maken dat aangeslotenen een rol spelen bij het optimaliseren van de bedrijfsvoering van het elektriciteitsnet | to enable connected parties to play a role in optimizing the operation of the electricity grid | measurement, control, communication, and self-healing techniques, to ensure that in the future, compared to the current situation: to better support the connection and operation of generation units of any size
klanten van informatie te voorzien, zodanig dat zij meer keuze hebben ten aanzien van de levering van elektrische energie | to provide customers with information so that they have more choices regarding the supply of electrical energy | situation: to better support the connection and operation of generation units of any size to enable connected parties to play a role in optimizing the operation of the electricity grid
de invloed van het totale elektriciteitsvoorzieningsysteem op het milieu significant te reduceren | significantly reduce the impact of the entire electricity supply system on the environment | parties to play a role in optimizing the operation of the electricity grid to provide customers with information so that they have more choices regarding the supply of electrical energy
de betrouwbaarheid van de levering te verbeteren. | to improve the reliability of the supply. | to provide customers with information so that they have more choices regarding the supply of electrical energy significantly reduce the impact of the entire electricity supply system on the environment
Bij het realiseren van een intelligent netwerk concentreert men zich op drie hoofddoelstellingen: verhogen van de betrouwbaarheid (herstel na een storing, afschakelbaarheid van belastingen), handhaven van de betaalbaarheid (voor de netbeheerder en voor de aangeslotenen) en verhogen van de duurzaamheid, onder meer door het actiever betrekken van klanten (duurzame bronnen en energietransitie). Bij het realiseren van deze doelstellingen worden verschillende wegen bewandeld: het netgerichte, het marktgerichte en het integrale concept (Slootweg, 2010). | In the realization of an intelligent network, the focus is on three main objectives: increasing reliability (recovery after a failure, load shedding), maintaining affordability (for the grid operator and the connected users), and enhancing sustainability, including more active customer involvement (sustainable sources and energy transition). Various approaches are taken to achieve these objectives: the grid-oriented, market-oriented, and integrated concepts (Slootweg, 2010). | they have more choices regarding the supply of electrical energy significantly reduce the impact of the entire electricity supply system on the environment to improve the reliability of the supply.
Netgericht concept | Grid-oriented concept | users), and enhancing sustainability, including more active customer involvement (sustainable sources and energy transition). Various approaches are taken to achieve these objectives: the grid-oriented, market-oriented, and integrated concepts (Slootweg, 2010).
Met het netgerichte concept wil de netbeheerder de benutting en de betrouwbaarheid van distributienetten verhogen. Om dit te bereiken worden de netten voorzien van op afstand uitleesbare meters en afstandbesturing. Ook kan decentrale opslag van elektrische energie (zie paragraaf 15.4.3) worden ingevoerd om de pieken en dalen in de productie en afname van elektrisch vermogen op te vangen. In dit concept is geen betrokkenheid van producenten en verbruikers. | With the grid-oriented concept, the grid operator aims to increase the utilization and reliability of distribution networks. To achieve this, the networks are equipped with remotely readable meters and remote control. Additionally, decentralized storage of electrical energy (see paragraph 15.4.3) can be introduced to manage the peaks and troughs in the production and consumption of electrical power. In this concept, there is no involvement of producers and consumers. | enhancing sustainability, including more active customer involvement (sustainable sources and energy transition). Various approaches are taken to achieve these objectives: the grid-oriented, market-oriented, and integrated concepts (Slootweg, 2010). Grid-oriented concept
Marktgericht concept | Market-oriented concept | paragraph 15.4.3) can be introduced to manage the peaks and troughs in the production and consumption of electrical power. In this concept, there is no involvement of producers and consumers.
Met het marktgerichte concept worden aangeslotenen intensiever betrokken bij de elektriciteitsmarkt. Dit wordt enerzijds bereikt door de aangeslotenen met behulp van tarieven te prikkelen tot een bepaald gedrag voor afname of productie van elektriciteit en anderzijds door specifieke processen van de aangeslotenen beïnvloedbaar te maken voor flexibilisering van de elektriciteitsvraag. In dit concept zijn commerciële energiemarktpartijen, leveranciers en verbruikers betrokken en speelt de netbeheerder geen rol (zie | With the market-oriented concept, participants are more intensively involved in the electricity market. This is achieved on one hand by incentivizing participants through tariffs to adopt certain behaviors for the consumption or production of electricity, and on the other hand by making specific processes of the participants adaptable for the flexibilization of electricity demand. In this concept, commercial energy market parties, suppliers, and consumers are involved, and the grid operator does not play a role. | can be introduced to manage the peaks and troughs in the production and consumption of electrical power. In this concept, there is no involvement of producers and consumers. Market-oriented concept
paragraaf 15.4.1 | paragraph 15.4.1 | the participants adaptable for the flexibilization of electricity demand. In this concept, commercial energy market parties, suppliers, and consumers are involved, and the grid operator does not play a role.
). Het marktgerichte concept leidt niet tot een intelligent elektriciteitsnet. | The market-oriented concept does not lead to an intelligent electricity grid. | adaptable for the flexibilization of electricity demand. In this concept, commercial energy market parties, suppliers, and consumers are involved, and the grid operator does not play a role. paragraph 15.4.1
Integraal concept | Integrated concept | energy market parties, suppliers, and consumers are involved, and the grid operator does not play a role. paragraph 15.4.1 The market-oriented concept does not lead to an intelligent electricity grid.
Door het netgerichte en het marktgerichte concept te combineren, ontstaat het integrale concept, waarbij de tariefstructuren gebaseerd zijn op de energiemarkt en op de lokaal beschikbare netcapaciteit. In dit concept kunnen bepaalde apparaten (bijvoorbeeld voor wassen, koelen en verwarmen) op afstand worden in- en uitgeschakeld, rekening houdend met de prijs van elektriciteit op de markt en met de lokale elektriciteitsproductie en netcapaciteit. | By combining the grid-oriented and market-oriented concepts, the integrated concept is created, where the tariff structures are based on the energy market and the locally available grid capacity. In this concept, certain devices (such as for washing, cooling, and heating) can be remotely switched on and off, taking into account the price of electricity on the market and the local electricity production and grid capacity. | parties, suppliers, and consumers are involved, and the grid operator does not play a role. paragraph 15.4.1 The market-oriented concept does not lead to an intelligent electricity grid. Integrated concept
Er zijn veel initiatieven voor het automatisch afstemmen van de belasting op het aanbod. Deze systemen moeten een balans vinden tussen de belangen van afnemer, producent en netbeheerder zonder dat het elektriciteitsnet overbelast raakt. Doelstelling is dat een consument een zo laag mogelijke prijs betaalt en dat zoveel mogelijk gebruik wordt gemaakt van duurzaam opgewekte energie. Met intelligente systemen, zoals software-agenten, is het mogelijk op basis van actuele meetgegevens (vraag, aanbod, prijs, netcapaciteit) en andere randvoorwaarden snel en rationeel keuzes te maken (Warmer, 2010). | There are many initiatives for automatically aligning demand with supply. These systems must balance the interests of the consumer, producer, and grid operator without overloading the electricity grid. The objective is for the consumer to pay the lowest possible price and to maximize the use of sustainably generated energy. With intelligent systems, such as software agents, it is possible to make quick and rational decisions based on current measurement data (demand, supply, price, grid capacity) and other conditions (Warmer, 2010). | for washing, cooling, and heating) can be remotely switched on and off, taking into account the price of electricity on the market and the local electricity production and grid capacity.
Essentieel voor een intelligent net is dat het tweerichtingsverkeer van het elektrische vermogen in het net toestaat. Door de toevoeging van (intelligente) meetsystemen in het distributienet kunnen de energiestromen beter worden bewaakt, bestuurd en beheerd. Door het toepassen van nieuwe ICT-technologieën en het verder ontwikkelen van de gewenste automatiseringssystemen ontstaat een intelligent distributienet waarbij de 'intelligentie' de gewenste betrouwbaarheid, betaalbaarheid en de verduurzaming van de energievoorziening ondersteunt. | Essential for an intelligent grid is that it allows for the bidirectional flow of electrical power within the network. By adding (intelligent) measurement systems to the distribution network, energy flows can be better monitored, controlled, and managed. The application of new ICT technologies and the further development of the desired automation systems create an intelligent distribution network where the 'intelligence' supports the desired reliability, affordability, and sustainability of the energy supply. | intelligent systems, such as software agents, it is possible to make quick and rational decisions based on current measurement data (demand, supply, price, grid capacity) and other conditions (Warmer, 2010).
Het sleutelwoord bij de ontwikkeling van intelligente netten is flexibiliteit. Een intelligent net signaleert knelpunten. De intelligente systemen in het net spelen daar met zelfstandig ingrijpen op in door automatisch schakelingen te veranderen en belastingen te beïnvloeden. Extra flexibiliteit wordt gerealiseerd door toepassing van nieuwe technologie en concepten, zoals opslag van elektrische energie. | The key word in the development of intelligent grids is flexibility. An intelligent grid detects bottlenecks. The intelligent systems in the grid respond to these by independently intervening, automatically changing circuits, and influencing loads. Additional flexibility is achieved through the application of new technologies and concepts, such as the storage of electrical energy. | ICT technologies and the further development of the desired automation systems create an intelligent distribution network where the 'intelligence' supports the desired reliability, affordability, and sustainability of the energy supply.
Belangrijk is dat het intelligente net lokale productie en opslag van elektrische energie mogelijk maakt. Het toekomstige intelligente net moet zoveel mogelijk zelf herstellend zijn. Storingen en foutplaatsen in het netwerk kunnen met de modernste digitale middelen opgespoord worden. Ook moet de 'kleine' aangeslotene de kans krijgen te participeren in de markt. Het intelligente net moet met telecommunicatie en hoogwaardige IT worden uitgerust, zodat ook consumenten thuis hun elektriciteitszaken kunnen regelen en bezitters van een elektrische auto 's avonds en 's nachts tegen voordelig tarief hun accu's kunnen opladen. | It is important that the intelligent grid enables local production and storage of electrical energy. The future intelligent grid should be as self-healing as possible. Faults and problem areas in the network can be detected using the latest digital tools. Additionally, the 'small' consumer should have the opportunity to participate in the market. The intelligent grid must be equipped with telecommunications and high-quality IT, so that consumers can manage their electricity affairs at home and owners of electric cars can charge their batteries at a favorable rate in the evenings and at night. | to these by independently intervening, automatically changing circuits, and influencing loads. Additional flexibility is achieved through the application of new technologies and concepts, such as the storage of electrical energy.
15.2 Waarom intelligente netten? | 15.2 Why smart grids? | IT, so that consumers can manage their electricity affairs at home and owners of electric cars can charge their batteries at a favorable rate in the evenings and at night.
De overgang naar duurzame energie heeft tot gevolg dat enerzijds meer elektriciteit op MS- en LS-niveau decentraal wordt opgewekt, zoals met zonnepanelen, micro-WKK's en windmolens, en anderzijds, door het geleidelijk afstappen van traditionele energiebronnen, meer elektriciteit wordt gebruikt, zoals voor ruimteverwarming en elektrisch rijden. Deze ontwikkelingen leiden ertoe dat de elektriciteit niet meer alleen traditioneel in een bij het ontwerp bekende richting naar de aangeslotene loopt, maar bi-directioneel wordt. Ten gevolge van toename van de decentrale opwekking en van het elektriciteitsverbruik zullen de variaties van de vermogensstromen in het distributienet fors toenemen. Dit heeft voor het bestaande distributienet onder andere tot gevolg: | The transition to sustainable energy results in more electricity being generated decentrally at MV and LV levels, such as with solar panels, micro-CHPs, and wind turbines. Additionally, as traditional energy sources are gradually phased out, more electricity is being used for applications like space heating and electric driving. These developments mean that electricity no longer flows solely in the traditional, design-predicted direction to the consumer but becomes bidirectional. As a result of the increase in decentralized generation and electricity consumption, the variations in power flows within the distribution network will significantly increase. This has several implications for the existing distribution network, including: | can manage their electricity affairs at home and owners of electric cars can charge their batteries at a favorable rate in the evenings and at night. 15.2 Why smart grids?
de toename van het elektriciteitsverbruik kan leiden tot overbelasting in bestaande netdelen | the increase in electricity consumption can lead to overloading in existing network segments | the increase in decentralized generation and electricity consumption, the variations in power flows within the distribution network will significantly increase. This has several implications for the existing distribution network, including:
het omkeren van de richting van het energietransport heeft gevolgen voor de werking van de beveiliging; de bestaande beveiligingsconcepten zijn hier nog niet op aangepast | Reversing the direction of energy transport has implications for the functioning of the security systems; the existing security concepts have not yet been adapted to this. | within the distribution network will significantly increase. This has several implications for the existing distribution network, including: the increase in electricity consumption can lead to overloading in existing network segments
de fluctuaties in het vermogenstransport leiden tot verslechtering van de kwaliteit van de spanning. | the fluctuations in power transport lead to a deterioration in voltage quality. | in existing network segments Reversing the direction of energy transport has implications for the functioning of the security systems; the existing security concepts have not yet been adapted to this.
Om de geschetste problemen te kunnen oplossen, wordt naarstig gezocht naar mogelijkheden om de bestaande distributienetten bestendig te maken voor de geschetste toekomstige ontwikkelingen. Er moeten hierbij keuzes gemaakt worden. Enerzijds kunnen de netten robuuster gemaakt worden en kan de beveiliging uitgevoerd worden met technieken zoals die in transportnetten worden gebruikt. Anderzijds wordt gekeken of introductie van metingen, besturingen en automatisering in combinatie met inzet van vermogenselektronische apparatuur (voor het regelen en bufferen van energie) een oplossing leveren, waarmee tevens meer flexibiliteit verkregen wordt. Deze technieken zijn ingrediënten voor een 'intelligent net'. Het toekomstbestendige distributienet moet voldoende capaciteit hebben en moet tegelijk stabiel en betrouwbaar zijn. Het net moet hiervoor door inzet van 'intelligente' systemen geschikt worden gemaakt. De systemen hiervoor moeten nog ontwikkeld worden en deze moeten leiden tot een efficiënte, duurzame en betrouwbare elektriciteitsvoorziening tegen acceptabele kosten. | To solve the outlined problems, there is an urgent search for ways to make the existing distribution networks resilient to the described future developments. Choices need to be made in this regard. On one hand, the networks can be made more robust, and security can be implemented using techniques similar to those used in transmission networks. On the other hand, the introduction of measurements, controls, and automation in combination with the use of power electronic equipment (for regulating and buffering energy) is being considered as a solution, which also provides more flexibility. These techniques are ingredients for an 'intelligent grid.' The future-proof distribution network must have sufficient capacity and be both stable and reliable. To achieve this, the network must be made suitable through the use of 'intelligent' systems. These systems still need to be developed and must lead to an efficient, sustainable, and reliable electricity supply at acceptable costs. | for the functioning of the security systems; the existing security concepts have not yet been adapted to this. the fluctuations in power transport lead to a deterioration in voltage quality.
Nationaal en internationaal is veel aandacht voor de intelligente netten. Organisaties als het European Technology Platform en Cigré beschrijven in diverse publicaties de ontwikkelingen voor nu en de nabije toekomst. Volgens het European Technology Platform zijn de belangrijkste uitdagingen voor intelligente netten (ETP, 2010): | Nationally and internationally, there is a lot of attention for smart grids. Organizations such as the European Technology Platform and Cigré describe in various publications the developments for now and the near future. According to the European Technology Platform, the main challenges for smart grids are (ETP, 2010): | be made suitable through the use of 'intelligent' systems. These systems still need to be developed and must lead to an efficient, sustainable, and reliable electricity supply at acceptable costs.
versterken van het elektriciteitsnet: verzekeren dat er voldoende capaciteit is om met name duurzame energiebronnen aan te sluiten | strengthening the electricity grid: ensuring that there is sufficient capacity to connect, in particular, renewable energy sources | Platform and Cigré describe in various publications the developments for now and the near future. According to the European Technology Platform, the main challenges for smart grids are (ETP, 2010):
energieopwekking op zee mogelijk maken: ontwikkelen van efficiënte verbindingen naar windparken op zee en andere opwekeenheden; de invloed op MS-netten is overigens beperkt, want grote windparken zullen meer op HS-niveau worden ingepast | enabling offshore energy generation: developing efficient connections to offshore wind farms and other generation units; the impact on medium voltage (MV) networks is limited, as large wind farms will be integrated more at the high voltage (HV) level | the European Technology Platform, the main challenges for smart grids are (ETP, 2010): strengthening the electricity grid: ensuring that there is sufficient capacity to connect, in particular, renewable energy sources
ontwikkeling van gedecentraliseerde infrastructuur: mogelijk maken dat kleinschalige elektriciteitssystemen goed integreren met het totale elektriciteitsvoorzieningsysteem | development of decentralized infrastructure: enabling small-scale electricity systems to integrate well with the overall electricity supply system | offshore wind farms and other generation units; the impact on medium voltage (MV) networks is limited, as large wind farms will be integrated more at the high voltage (HV) level
communicatie: ontwikkelen van een communicatie-infrastructuur die het mogelijk maakt voor alle aangeslotenen om actief aan de elektriciteitsmarkt deel te nemen; informatie-uitwisseling tussen partijen behoeft bescherming en regelgeving vanwege de privacy | communication: developing a communication infrastructure that enables all connected parties to actively participate in the electricity market; information exchange between parties requires protection and regulation due to privacy concerns | large wind farms will be integrated more at the high voltage (HV) level development of decentralized infrastructure: enabling small-scale electricity systems to integrate well with the overall electricity supply system
actieve rol van aangeslotenen: mogelijk maken dat alle aangeslotenen met of zonder eigen opwekking een actieve rol spelen in de elektriciteitvoorziening | active role of connected parties: enabling all connected parties, with or without their own generation, to play an active role in the electricity supply | system communication: developing a communication infrastructure that enables all connected parties to actively participate in the electricity market; information exchange between parties requires protection and regulation due to privacy concerns
integreren van wisselende opwekking: vinden van de beste oplossingen om sterk wisselende opwekking, zoals huishoudelijke micro-WKK systemen, in te passen; hier is de grootschaligheid waarmee de kleinschalige systemen op het LS-net worden aangesloten van belang | integration of variable generation: finding the best solutions to integrate highly variable generation, such as household micro-CHP systems; here, the scale at which small-scale systems are connected to the LV network is important | and regulation due to privacy concerns active role of connected parties: enabling all connected parties, with or without their own generation, to play an active role in the electricity supply
toevoegen van intelligente systemen bij opwekking, belasting en met name in het netwerk | adding intelligent systems in generation, load, and especially in the network | generation: finding the best solutions to integrate highly variable generation, such as household micro-CHP systems; here, the scale at which small-scale systems are connected to the LV network is important
gebruik maken van de voordelen van decentrale opwekking en opslag van energie | taking advantage of the benefits of decentralized generation and storage of energy | as household micro-CHP systems; here, the scale at which small-scale systems are connected to the LV network is important adding intelligent systems in generation, load, and especially in the network
voorbereiden van alle elektrische voertuigen: met hun inherent mobiele en decentrale karakter en hun grote vermogensbehoefte stellen zij hoge eisen aan de flexibiliteit van het distributienet. | preparing all electric vehicles: with their inherently mobile and decentralized nature and their high power demand, they place high demands on the flexibility of the distribution network. | connected to the LV network is important adding intelligent systems in generation, load, and especially in the network taking advantage of the benefits of decentralized generation and storage of energy
De hierboven genoemde uitdagingen zijn voor het grootste deel gedreven door de ontwikkelingen rond de verduurzaming van de energievoorziening. Uit de uitdagingen zijn door het European Technology Platform zes prioriteiten gedefinieerd: | The aforementioned challenges are largely driven by developments in the sustainability of energy supply. From these challenges, the European Technology Platform has defined six priorities: | storage of energy preparing all electric vehicles: with their inherently mobile and decentralized nature and their high power demand, they place high demands on the flexibility of the distribution network.
optimaliseren van de bedrijfsvoering en de benutting van het elektriciteitsnet | optimizing the operation and utilization of the electricity grid | flexibility of the distribution network. The aforementioned challenges are largely driven by developments in the sustainability of energy supply. From these challenges, the European Technology Platform has defined six priorities:
optimaliseren van de infrastructuur van het elektriciteitsnet | optimizing the infrastructure of the electricity grid | largely driven by developments in the sustainability of energy supply. From these challenges, the European Technology Platform has defined six priorities: optimizing the operation and utilization of the electricity grid
op grote schaal integreren van decentrale opwekking met sterk wisselende vermogens | large-scale integration of decentralized generation with highly variable power outputs | of energy supply. From these challenges, the European Technology Platform has defined six priorities: optimizing the operation and utilization of the electricity grid optimizing the infrastructure of the electricity grid
definitie en implementatie van standaards voor informatie- en communicatietechniek | definition and implementation of standards for information and communication technology | has defined six priorities: optimizing the operation and utilization of the electricity grid optimizing the infrastructure of the electricity grid large-scale integration of decentralized generation with highly variable power outputs
ondersteunen van de transitie naar actieve distributienetwerken | supporting the transition to active distribution networks | the electricity grid optimizing the infrastructure of the electricity grid large-scale integration of decentralized generation with highly variable power outputs definition and implementation of standards for information and communication technology
ondersteunen van de nieuwe marktwerking en energie-efficiëntie. | supporting the new market operations and energy efficiency. | the electricity grid large-scale integration of decentralized generation with highly variable power outputs definition and implementation of standards for information and communication technology supporting the transition to active distribution networks
Van deze prioriteiten hebben de meeste betrekking op het elektriciteitsnet en een op de marktwerking. De meeste uitdagingen komen dus terecht bij de netbeheerder, voor wie het optimaliseren van de bedrijfsvoering en de infrastructuur veel denkwerk en creativiteit vereist. Het integreren van bronnen van sterk wisselende vermogens stelt eisen aan de flexibiliteit van het net. In plaats van de traditionele methodes zullen de planner en de ontwerper zich moeten bedienen van scenario's en risicobeheersing om met de toegenomen beweeglijkheid en onzekerheid van de opwekking van elektriciteit om te gaan. De toepassing van ICT is een voorwaarde voor de werking van intelligente netten, waar het enerzijds gaat om gegevensuitwisseling voor de meting en besturing van het flexibele netwerk en anderzijds om de gegevensuitwisseling tussen de diverse marktpartijen. De ontwikkeling van actieve distributienetwerken markeert de overgang van de huidige netten, die afhankelijk zijn van de geplande acties van de bedrijfsvoering, naar een nieuw type netten, die zich automatisch snel kunnen aanpassen aan sterk wisselende situaties. Volgens Cigré liggen de belangrijkste ontwikkelingen van actieve distributienetten op het gebied van: beveiliging, communicatie, integratie in bestaande systemen en flexibele netwerktopologie (Cigré, 2009-2). Voor wat betreft de toepassingen ziet men mogelijkheden voor: bewaking van de capaciteit van het elektriciteitsnet; verzamelen en beheren van gegevens; spanningshuishouding; bedrijfsvoering van belastingen en decentrale opwekking; snelle wijziging van de configuratie van het netwerk. Als voordelen worden genoemd: verbeterde betrouwbaarheid; toename van de benutting van de bedrijfsmiddelen; verbeterde mogelijkheden voor het aansluiten van decentrale opwekking; bieden van alternatieven voor het verzwaren van de netwerken; verbeterde stabiliteit van het netwerk. | Most of these priorities pertain to the electricity grid, with one relating to market operations. Therefore, most challenges fall upon the grid operator, for whom optimizing operations and infrastructure requires considerable thought and creativity. Integrating sources with highly variable power outputs demands flexibility from the grid. Instead of traditional methods, planners and designers will need to use scenarios and risk management to handle the increased variability and uncertainty in electricity generation. The application of ICT is a prerequisite for the operation of smart grids, involving data exchange for the measurement and control of the flexible network on one hand, and data exchange between various market parties on the other. The development of active distribution networks marks the transition from current grids, which depend on planned operational actions, to a new type of grid that can automatically and quickly adapt to highly variable situations. According to Cigré, the main developments in active distribution networks are in the areas of security, communication, integration into existing systems, and flexible network topology (Cigré, 2009-2). Regarding applications, possibilities include monitoring the capacity of the electricity grid, data collection and management, voltage regulation, load and decentralized generation management, and rapid network configuration changes. The cited benefits include improved reliability, increased utilization of assets, enhanced capabilities for connecting decentralized generation, providing alternatives to network reinforcement, and improved network stability. | with highly variable power outputs definition and implementation of standards for information and communication technology supporting the transition to active distribution networks supporting the new market operations and energy efficiency.
Op nationaal niveau buigt de Taskforce Intelligente Netten zich over de mogelijkheden en de ontwikkelingen van intelligente netten. Tabel 15.1 geeft een overzicht van de mogelijkheden die een traditioneel elektriciteitsnet en een intelligent elektriciteitsnet bieden (Taskforce, 2010). | At the national level, the Smart Grids Taskforce is examining the possibilities and developments of smart grids. Table 15.1 provides an overview of the capabilities offered by a traditional electricity grid and a smart electricity grid (Taskforce, 2010). | and rapid network configuration changes. The cited benefits include improved reliability, increased utilization of assets, enhanced capabilities for connecting decentralized generation, providing alternatives to network reinforcement, and improved network stability.
Tabel 15.1 Mogelijkheden in een traditioneel en een intelligent elektriciteitsnet | Table 15.1 Capabilities in a traditional and a smart electricity grid | is examining the possibilities and developments of smart grids. Table 15.1 provides an overview of the capabilities offered by a traditional electricity grid and a smart electricity grid (Taskforce, 2010).
Aspect | Aspect | provides an overview of the capabilities offered by a traditional electricity grid and a smart electricity grid (Taskforce, 2010). Table 15.1 Capabilities in a traditional and a smart electricity grid
Traditioneel netwerk | Traditional network | an overview of the capabilities offered by a traditional electricity grid and a smart electricity grid (Taskforce, 2010). Table 15.1 Capabilities in a traditional and a smart electricity grid Aspect
Intelligent net | Smart grid | of the capabilities offered by a traditional electricity grid and a smart electricity grid (Taskforce, 2010). Table 15.1 Capabilities in a traditional and a smart electricity grid Aspect Traditional network
Gebruikers | Gebruikers | capabilities offered by a traditional electricity grid and a smart electricity grid (Taskforce, 2010). Table 15.1 Capabilities in a traditional and a smart electricity grid Aspect Traditional network Smart grid
De gebruikers zijn niet geïnformeerd en participeren niet | The users are not informed and do not participate | offered by a traditional electricity grid and a smart electricity grid (Taskforce, 2010). Table 15.1 Capabilities in a traditional and a smart electricity grid Aspect Traditional network Smart grid Gebruikers
De gebruikers zijn geïnformeerd, betrokken en actief; besparing door 'slimheid' (met privacy!) | The users are informed, engaged, and active; savings through 'smartness' (with privacy!) | electricity grid (Taskforce, 2010). Table 15.1 Capabilities in a traditional and a smart electricity grid Aspect Traditional network Smart grid Gebruikers The users are not informed and do not participate
Productie | Productie | smart electricity grid Aspect Traditional network Smart grid Gebruikers The users are not informed and do not participate The users are informed, engaged, and active; savings through 'smartness' (with privacy!)
Vooral centraal opgestelde productiemiddelen | Mainly centrally located production resources | electricity grid Aspect Traditional network Smart grid Gebruikers The users are not informed and do not participate The users are informed, engaged, and active; savings through 'smartness' (with privacy!) Productie
Allerlei decentrale productiemiddelen; verbruik kan gekoppeld worden aan soort productiemiddel | Various decentralized production resources; consumption can be linked to the type of production resource | Smart grid Gebruikers The users are not informed and do not participate The users are informed, engaged, and active; savings through 'smartness' (with privacy!) Productie Mainly centrally located production resources
Duurzame energie | Sustainable energy | are informed, engaged, and active; savings through 'smartness' (with privacy!) Productie Mainly centrally located production resources Various decentralized production resources; consumption can be linked to the type of production resource
Inpassing (decentrale) duurzame energie beperkt mogelijk en soms moeizaam | Integration of (decentralized) sustainable energy is limited and sometimes challenging | engaged, and active; savings through 'smartness' (with privacy!) Productie Mainly centrally located production resources Various decentralized production resources; consumption can be linked to the type of production resource Sustainable energy
Gestandaardiseerde plug-in voor duurzame productie, gestuurd door elektronica en IT | Standardized plug-in for sustainable production, driven by electronics and IT | centrally located production resources Various decentralized production resources; consumption can be linked to the type of production resource Sustainable energy Integration of (decentralized) sustainable energy is limited and sometimes challenging
Emissies | Emissies | be linked to the type of production resource Sustainable energy Integration of (decentralized) sustainable energy is limited and sometimes challenging Standardized plug-in for sustainable production, driven by electronics and IT
Emissies en verliezen (warmte) ingebouwd in het systeem en weinig inzichtelijk | Emissions and losses (heat) built into the system and not very transparent | linked to the type of production resource Sustainable energy Integration of (decentralized) sustainable energy is limited and sometimes challenging Standardized plug-in for sustainable production, driven by electronics and IT Emissies
De gebruikers zijn geïnformeerd en optimaliseren op de 'kleur' van hun energieverbruik (wel/niet duurzaam) | The users are informed and optimize based on the 'color' of their energy consumption (sustainable or not). | sustainable energy is limited and sometimes challenging Standardized plug-in for sustainable production, driven by electronics and IT Emissies Emissions and losses (heat) built into the system and not very transparent
Opslag | Opslag | Emissies Emissions and losses (heat) built into the system and not very transparent The users are informed and optimize based on the 'color' of their energy consumption (sustainable or not).
Nauwelijks of geen opslagmogelijkheden | Hardly any or no storage options | Emissions and losses (heat) built into the system and not very transparent The users are informed and optimize based on the 'color' of their energy consumption (sustainable or not). Opslag
Beschikbaarheid van opslagmiddelen die in de markt participeren | Availability of storage resources participating in the market | the system and not very transparent The users are informed and optimize based on the 'color' of their energy consumption (sustainable or not). Opslag Hardly any or no storage options
Marktwerking | Marktwerking | are informed and optimize based on the 'color' of their energy consumption (sustainable or not). Opslag Hardly any or no storage options Availability of storage resources participating in the market
Vooral producenten en industriële grootverbruikers actief in de markt | Mainly producers and industrial large-scale consumers active in the market | informed and optimize based on the 'color' of their energy consumption (sustainable or not). Opslag Hardly any or no storage options Availability of storage resources participating in the market Marktwerking
Grote (prijsafhankelijke) vraagrespons op basis van nieuwe diensten en innovatieve applicaties | Large (price-dependent) demand response based on new services and innovative applications | consumption (sustainable or not). Opslag Hardly any or no storage options Availability of storage resources participating in the market Marktwerking Mainly producers and industrial large-scale consumers active in the market
Kwaliteit | Kwaliteit | Availability of storage resources participating in the market Marktwerking Mainly producers and industrial large-scale consumers active in the market Large (price-dependent) demand response based on new services and innovative applications
Focus op leveringsonderbrekingen | Focus on supply interruptions | of storage resources participating in the market Marktwerking Mainly producers and industrial large-scale consumers active in the market Large (price-dependent) demand response based on new services and innovative applications Kwaliteit
Dynamische interactie tussen prijs en kwaliteit met snelle respons op kwaliteitsissues | Dynamic interaction between price and quality with a quick response to quality issues | in the market Marktwerking Mainly producers and industrial large-scale consumers active in the market Large (price-dependent) demand response based on new services and innovative applications Kwaliteit Focus on supply interruptions
Systeembeheer | Systeembeheer | market Large (price-dependent) demand response based on new services and innovative applications Kwaliteit Focus on supply interruptions Dynamic interaction between price and quality with a quick response to quality issues
Beperkte integratie van asset management, bedrijfsvoering en operationele data | Limited integration of asset management, operations, and operational data | Large (price-dependent) demand response based on new services and innovative applications Kwaliteit Focus on supply interruptions Dynamic interaction between price and quality with a quick response to quality issues Systeembeheer
Real-time systeeminformatie beschikbaar voor bedrijfsvoering, waarbij preventie centraal staat | Real-time system information available for operations, with a focus on prevention | innovative applications Kwaliteit Focus on supply interruptions Dynamic interaction between price and quality with a quick response to quality issues Systeembeheer Limited integration of asset management, operations, and operational data
Verstoringen | Verstoringen | and quality with a quick response to quality issues Systeembeheer Limited integration of asset management, operations, and operational data Real-time system information available for operations, with a focus on prevention
Systeembeveiliging richt zich op het voorkomen van schade bij componenten | System security focuses on preventing damage to components | quality with a quick response to quality issues Systeembeheer Limited integration of asset management, operations, and operational data Real-time system information available for operations, with a focus on prevention Verstoringen
Systeembeveiliging reageert automatisch zodanig dat de levering gewaarborgd blijft (self-healing) | System security responds automatically to ensure delivery remains guaranteed (self-healing) | Systeembeheer Limited integration of asset management, operations, and operational data Real-time system information available for operations, with a focus on prevention Verstoringen System security focuses on preventing damage to components
Rampen | Rampen | Real-time system information available for operations, with a focus on prevention Verstoringen System security focuses on preventing damage to components System security responds automatically to ensure delivery remains guaranteed (self-healing)
Systeem gevoelig voor (natuur) rampen en terroristische aanvallen | System sensitive to (natural) disasters and terrorist attacks | system information available for operations, with a focus on prevention Verstoringen System security focuses on preventing damage to components System security responds automatically to ensure delivery remains guaranteed (self-healing) Rampen
Systeem is relatief ongevoelig voor rampen ('dispersed' en met efficiënte herstelmechanismen) maar mogelijk gevoelig voor 'cyber attacks' | The system is relatively insensitive to disasters ('dispersed' and with efficient recovery mechanisms) but may be sensitive to cyber attacks. | on prevention Verstoringen System security focuses on preventing damage to components System security responds automatically to ensure delivery remains guaranteed (self-healing) Rampen System sensitive to (natural) disasters and terrorist attacks
15.3 Hoe zit een intelligent net in elkaar? | 15.3 How is an intelligent network structured? | (self-healing) Rampen System sensitive to (natural) disasters and terrorist attacks The system is relatively insensitive to disasters ('dispersed' and with efficient recovery mechanisms) but may be sensitive to cyber attacks.
De elektrische midden- en laagspanningsdistributienetten worden de komende jaren in hoog tempo geïnstrumenteerd en gedigitaliseerd. Er ontstaan drie functionele lagen. De traditionele distributienetten vormen een eerste fysieke laag. Deze laag wordt de komende jaren uitgebreid met een tweede laag die bestaat uit sensoren, data verbindingen, verresturing en -regelingen. Er zijn dan meer mogelijkheden tot informatie-uitwisseling waardoor energiestromen beter kunnen worden gecontroleerd, gestuurd en beheerd. Op deze tweede laag wordt langzamerhand een derde laag aangebracht met specifieke 'intelligente' toepassingen voor bijvoorbeeld foutplaatslokalisering, storingsanalyse, decentrale balanshandhaving met decentrale opwek en actief participerende consumenten. | The medium and low voltage electrical distribution networks will be instrumented and digitized at a rapid pace in the coming years. Three functional layers will emerge. The traditional distribution networks form the first physical layer. This layer will be expanded in the coming years with a second layer consisting of sensors, data connections, remote control, and regulations. This will enable more opportunities for information exchange, allowing energy flows to be better monitored, controlled, and managed. Gradually, a third layer with specific 'intelligent' applications will be added to this second layer, such as fault location, fault analysis, decentralized balance maintenance with decentralized generation, and actively participating consumers. | and terrorist attacks The system is relatively insensitive to disasters ('dispersed' and with efficient recovery mechanisms) but may be sensitive to cyber attacks. 15.3 How is an intelligent network structured?
De problematiek voor het aanbrengen van de tweede laag in de MS-netten verschilt met die in de LS-netten. Dit wordt enerzijds veroorzaakt door de omvang van het vermogen en de bijbehorende aantallen aangeslotenen. Anderzijds wordt dit veroorzaakt door de verschillen in netstructuur, elektrische eigenschappen en opweksystemen. | The challenges of implementing the second layer in the medium-voltage (MV) networks differ from those in the low-voltage (LV) networks. This is partly due to the scale of the power and the corresponding number of connected users. Additionally, it is caused by differences in network structure, electrical properties, and generation systems. | a third layer with specific 'intelligent' applications will be added to this second layer, such as fault location, fault analysis, decentralized balance maintenance with decentralized generation, and actively participating consumers.
Zo zijn er in de MS-netten schakelmogelijkheden door de aanleg in open bedreven ringen, terwijl de LS-netten meestal stervormig aangelegd zijn, waardoor zij de voordelen ervan missen. | In the medium voltage networks, there are switching possibilities due to the installation in open-operated rings, while the low voltage networks are usually laid out in a star configuration, causing them to miss out on these advantages. | is partly due to the scale of the power and the corresponding number of connected users. Additionally, it is caused by differences in network structure, electrical properties, and generation systems.
De elektrische eigenschappen van de kabelverbindingen verschillen op beide spanningsniveaus, waardoor de invloed van vermogenstransport op de spanningshuishouding in een verbinding sterk verschilt. | The electrical properties of the cable connections differ at both voltage levels, causing the impact of power transmission on the voltage regulation in a connection to vary significantly. | switching possibilities due to the installation in open-operated rings, while the low voltage networks are usually laid out in a star configuration, causing them to miss out on these advantages.
De voedingstransformatoren van de MS-netten zijn voorzien van een spanningsregeling, terwijl de huidige nettransformatoren die de LS-netten voeden op een vaste overzetverhouding zijn ingesteld. | The supply transformers of the medium voltage (MV) networks are equipped with voltage regulation, while the current network transformers that supply the low voltage (LV) networks are set to a fixed transformation ratio. | these advantages. The electrical properties of the cable connections differ at both voltage levels, causing the impact of power transmission on the voltage regulation in a connection to vary significantly.
Bij de opweksystemen in de MS-netten is sprake van een klein aantal grote opwekeenheden, zoals WKK-systemen (1 tot 20 MW per aansluiting) en windturbines (1 tot 5 MW per aansluiting), terwijl in de LS-netten sprake is van grote aantallen kleine opwekeenheden, zoals micro-WKK (1 tot 5 kW per aansluiting) en PV-systemen (0,5 tot 2 kW per aansluiting). | In the generation systems in the medium voltage (MV) networks, there are a small number of large generation units, such as CHP systems (1 to 20 MW per connection) and wind turbines (1 to 5 MW per connection), while in the low voltage (LV) networks, there are large numbers of small generation units, such as micro-CHP (1 to 5 kW per connection) and PV systems (0.5 to 2 kW per connection). | of the medium voltage (MV) networks are equipped with voltage regulation, while the current network transformers that supply the low voltage (LV) networks are set to a fixed transformation ratio.
Gezien hun kosten en hun bijdrage in de vermogenshuishouding zullen energie-opslagsystemen voornamelijk op het LS-niveau worden geïntroduceerd. | Given their costs and their contribution to power management, energy storage systems will primarily be introduced at the LV level. | low voltage (LV) networks, there are large numbers of small generation units, such as micro-CHP (1 to 5 kW per connection) and PV systems (0.5 to 2 kW per connection).
Grote hoeveelheden decentrale opwekking kunnen met name in de MS-netten problemen veroorzaken met de beveiligingen en de spanningshuishouding. In de LS-netten geldt dat ook voor de beveiliging maar geldt dat minder voor de spanningshuishouding. In de LS-netten wordt de spanningshuishouding negatief beïnvloed door de toegenomen belasting als gevolg van de toenemende energietransitie van aangeslotenen. Hierdoor ontstaan in de LS-netten problemen ten aanzien van de belasting van netwerk en kabels. | Large amounts of decentralized generation can particularly cause problems in the MV networks with protections and voltage management. In the LV networks, this also applies to protection but less so to voltage management. In the LV networks, voltage management is negatively affected by the increased load due to the growing energy transition of connected users. This results in problems in the LV networks concerning the load on the network and cables. | connection) and PV systems (0.5 to 2 kW per connection). Given their costs and their contribution to power management, energy storage systems will primarily be introduced at the LV level.
De communicatie-infrastructuur in de LS-netten zal zich concentreren op de informatie-uitwisseling met aangeslotenen via de 'intelligente meters' en besturing van beïnvloedbare belasting, terwijl de communicatie-infrastructuur in de MS-netten zich hoofdzakelijk zal richten op de flexibiliteit van het net. | The communication infrastructure in the LV networks will focus on information exchange with connected users via 'smart meters' and control of controllable loads, while the communication infrastructure in the MV networks will primarily focus on the flexibility of the grid. | affected by the increased load due to the growing energy transition of connected users. This results in problems in the LV networks concerning the load on the network and cables.
Tabel 15.2 geeft een samenvatting van de genoemde verschillen. Vanwege al deze verschillen wordt de toepassing van intelligente netten in de elektriciteitsdistributie op MS-niveau anders benaderd dan op LS-niveau. | Table 15.2 provides a summary of the mentioned differences. Due to all these differences, the application of smart grids in electricity distribution at the MV level is approached differently than at the LV level. | information exchange with connected users via 'smart meters' and control of controllable loads, while the communication infrastructure in the MV networks will primarily focus on the flexibility of the grid.
Tabel 15.2 Verschillende aspecten van MS- en LS-netten | Table 15.2 Different aspects of MV and LV networks | summary of the mentioned differences. Due to all these differences, the application of smart grids in electricity distribution at the MV level is approached differently than at the LV level.
Item | Item | differences, the application of smart grids in electricity distribution at the MV level is approached differently than at the LV level. Table 15.2 Different aspects of MV and LV networks
MS-net | MV network | the application of smart grids in electricity distribution at the MV level is approached differently than at the LV level. Table 15.2 Different aspects of MV and LV networks Item
LS-net | LV network | of smart grids in electricity distribution at the MV level is approached differently than at the LV level. Table 15.2 Different aspects of MV and LV networks Item MV network
Netstructuur: schakelmogelijkheden | Network structure: switching options | grids in electricity distribution at the MV level is approached differently than at the LV level. Table 15.2 Different aspects of MV and LV networks Item MV network LV network
ja | ja | at the MV level is approached differently than at the LV level. Table 15.2 Different aspects of MV and LV networks Item MV network LV network Network structure: switching options
nee | nee | the MV level is approached differently than at the LV level. Table 15.2 Different aspects of MV and LV networks Item MV network LV network Network structure: switching options ja
Elektrische eigenschappen | Electrical properties | MV level is approached differently than at the LV level. Table 15.2 Different aspects of MV and LV networks Item MV network LV network Network structure: switching options ja nee
R/X-verhouding ongeveer 1 | R/X ratio approximately 1 | is approached differently than at the LV level. Table 15.2 Different aspects of MV and LV networks Item MV network LV network Network structure: switching options ja nee Electrical properties
R/X-verhouding groot | R/X ratio large | at the LV level. Table 15.2 Different aspects of MV and LV networks Item MV network LV network Network structure: switching options ja nee Electrical properties R/X ratio approximately 1
Transformatoren spanningsregeling | Transformer voltage regulation | level. Table 15.2 Different aspects of MV and LV networks Item MV network LV network Network structure: switching options ja nee Electrical properties R/X ratio approximately 1 R/X ratio large
ja | ja | Different aspects of MV and LV networks Item MV network LV network Network structure: switching options ja nee Electrical properties R/X ratio approximately 1 R/X ratio large Transformer voltage regulation
nee | nee | aspects of MV and LV networks Item MV network LV network Network structure: switching options ja nee Electrical properties R/X ratio approximately 1 R/X ratio large Transformer voltage regulation ja
Opwekeenheden | Opwekeenheden | of MV and LV networks Item MV network LV network Network structure: switching options ja nee Electrical properties R/X ratio approximately 1 R/X ratio large Transformer voltage regulation ja nee
WKK, windenergie | CHP, wind energy | MV and LV networks Item MV network LV network Network structure: switching options ja nee Electrical properties R/X ratio approximately 1 R/X ratio large Transformer voltage regulation ja nee Opwekeenheden
Micro-WKK, PV-systemen | Micro-CHP, PV systems | networks Item MV network LV network Network structure: switching options ja nee Electrical properties R/X ratio approximately 1 R/X ratio large Transformer voltage regulation ja nee Opwekeenheden CHP, wind energy
Opslagsystemen | Opslagsystemen | network LV network Network structure: switching options ja nee Electrical properties R/X ratio approximately 1 R/X ratio large Transformer voltage regulation ja nee Opwekeenheden CHP, wind energy Micro-CHP, PV systems
Nog beperkt mogelijk | Still limited possible | LV network Network structure: switching options ja nee Electrical properties R/X ratio approximately 1 R/X ratio large Transformer voltage regulation ja nee Opwekeenheden CHP, wind energy Micro-CHP, PV systems Opslagsystemen
Goed mogelijk | Quite possible | structure: switching options ja nee Electrical properties R/X ratio approximately 1 R/X ratio large Transformer voltage regulation ja nee Opwekeenheden CHP, wind energy Micro-CHP, PV systems Opslagsystemen Still limited possible
Problematiek DCO | Issues DCO | options ja nee Electrical properties R/X ratio approximately 1 R/X ratio large Transformer voltage regulation ja nee Opwekeenheden CHP, wind energy Micro-CHP, PV systems Opslagsystemen Still limited possible Quite possible
Beveiliging, spanningshuishouding | Protection, voltage management | nee Electrical properties R/X ratio approximately 1 R/X ratio large Transformer voltage regulation ja nee Opwekeenheden CHP, wind energy Micro-CHP, PV systems Opslagsystemen Still limited possible Quite possible Issues DCO
Beveiliging, beperkte mate spanningshuishouding | Protection, limited voltage management | R/X ratio approximately 1 R/X ratio large Transformer voltage regulation ja nee Opwekeenheden CHP, wind energy Micro-CHP, PV systems Opslagsystemen Still limited possible Quite possible Issues DCO Protection, voltage management
Problematiek energietransitie | Issues of the energy transition | R/X ratio large Transformer voltage regulation ja nee Opwekeenheden CHP, wind energy Micro-CHP, PV systems Opslagsystemen Still limited possible Quite possible Issues DCO Protection, voltage management Protection, limited voltage management
Fluctuerende netbelasting | Fluctuating grid load | regulation ja nee Opwekeenheden CHP, wind energy Micro-CHP, PV systems Opslagsystemen Still limited possible Quite possible Issues DCO Protection, voltage management Protection, limited voltage management Issues of the energy transition
Belasting netwerk en kabels, spanningshuishouding | Load on the network and cables, voltage management | Opwekeenheden CHP, wind energy Micro-CHP, PV systems Opslagsystemen Still limited possible Quite possible Issues DCO Protection, voltage management Protection, limited voltage management Issues of the energy transition Fluctuating grid load
Communicatie-infrastructuur | Communication infrastructure | Still limited possible Quite possible Issues DCO Protection, voltage management Protection, limited voltage management Issues of the energy transition Fluctuating grid load Load on the network and cables, voltage management
Flexibiliteit: meten en besturen netwerk | Flexibility: measuring and controlling the network | possible Quite possible Issues DCO Protection, voltage management Protection, limited voltage management Issues of the energy transition Fluctuating grid load Load on the network and cables, voltage management Communication infrastructure
Markt en netbelasting: meten en besturen belastingen | Market and grid load: measuring and controlling loads | voltage management Protection, limited voltage management Issues of the energy transition Fluctuating grid load Load on the network and cables, voltage management Communication infrastructure Flexibility: measuring and controlling the network
In alle netten is het met de bestaande middelen en netstructuren niet zonder meer mogelijk de capaciteit structureel te vergroten. Door het gebrek aan metingen is de beheersing van de capaciteit gering. Mogelijkheden van afstandsbediening voor vergroting van de flexibiliteit en tweerichtingsverkeer voor het inpassen van grote hoeveelheden decentrale opwekking zijn beperkt. Ook zijn substantiële verlaging van de netverliezen en verhoging van de betrouwbaarheid niet meer haalbaar. Hierom wordt voor de distributienetten naar nieuwe concepten gezocht. Een aantal concepten voor toepassing in de MS- en LS-netten wordt in de volgende paragrafen kort toegelicht. | In all networks, it is not possible to structurally increase capacity with the existing resources and network structures. Due to the lack of measurements, capacity control is limited. The possibilities for remote control to increase flexibility and bidirectional traffic to accommodate large amounts of decentralized generation are restricted. Additionally, substantial reductions in network losses and increases in reliability are no longer achievable. Therefore, new concepts are being sought for distribution networks. Several concepts for application in the medium-voltage (MV) and low-voltage (LV) networks are briefly explained in the following paragraphs. | the energy transition Fluctuating grid load Load on the network and cables, voltage management Communication infrastructure Flexibility: measuring and controlling the network Market and grid load: measuring and controlling loads
15.3.1 Intelligent MS-distributienet met gecombineerde netstructuur | 15.3.1 Intelligent MV Distribution Network with Combined Network Structure | longer achievable. Therefore, new concepts are being sought for distribution networks. Several concepts for application in the medium-voltage (MV) and low-voltage (LV) networks are briefly explained in the following paragraphs.
De eisen ten aanzien van duurzaamheid, flexibiliteit, betrouwbaarheid, benutting van de bedrijfsmiddelen en klantgerichtheid leiden tot een aantal maatregelen. Ten eerste is het onvermijdelijk dat de capaciteit van het distributienet vergroot moet worden en dat de vermogenstromen gemonitord moeten worden. Ten behoeve van de flexibiliteit moeten de voor de netconfiguratie essentiële vermogenschakelaars op afstand bedienbaar zijn. De beveiliging moet zodanig zijn ingericht dat tweerichtingsverkeer mogelijk is voor het elektrische vermogen. Als het door windparken en WKK-systemen opgewekte vermogen te groot wordt, zal dit op een hoger spanningsniveau moet worden ingepast. De zesde prioriteit van het European Technology Platform, verbetering van de energie-efficiëntie, kan worden bereikt door de netverliezen te reduceren. Dit kan worden bewerkstelligd door in de MS-netten een hoger spanningsniveau te kiezen. | The requirements regarding sustainability, flexibility, reliability, utilization of assets, and customer orientation lead to several measures. First, it is inevitable that the capacity of the distribution network must be increased and that power flows must be monitored. For the sake of flexibility, the power switches essential for network configuration must be remotely operable. The security must be configured in such a way that bidirectional traffic is possible for electrical power. If the power generated by wind farms and CHP systems becomes too large, it will need to be integrated at a higher voltage level. The sixth priority of the European Technology Platform, improving energy efficiency, can be achieved by reducing network losses. This can be accomplished by choosing a higher voltage level in the MV networks. | distribution networks. Several concepts for application in the medium-voltage (MV) and low-voltage (LV) networks are briefly explained in the following paragraphs. 15.3.1 Intelligent MV Distribution Network with Combined Network Structure
In | In | priority of the European Technology Platform, improving energy efficiency, can be achieved by reducing network losses. This can be accomplished by choosing a higher voltage level in the MV networks.
paragraaf 2.4.3 | section 2.4.3 | of the European Technology Platform, improving energy efficiency, can be achieved by reducing network losses. This can be accomplished by choosing a higher voltage level in the MV networks. In
is reeds een gecombineerde netstructuur besproken, waarmee aan bovenstaande eisen wordt tegemoet gekomen. In deze structuur wordt het 10 kV distributienet gevoed vanuit een 20 kV transportnet, dat is uitgevoerd als een gesloten bedreven ring met meerdere verdeelstations. Het voordeel van het 20 kV spanningsniveau is dat de techniek en de prijs van de commercieel verkrijgbare apparatuur niet veel verschilt van die op 10 kV niveau, terwijl het dubbele vermogen getransporteerd kan worden. In een gecombineerde netstructuur worden de verdeelstations in de 20 kV transportring als intelligente distributieruimte (IDR) ingericht. De IDR wordt op afstand gemonitord, beveiligd en bestuurd. In de verdeelstations kan, afhankelijk van de situatie bij de aangeslotenen, het vermogen in twee richtingen lopen. Het verdeelstation kan de 20 kV transportring voeden en voedt de 10 kV strengen waar zich de netstations bevinden. Ook deze netstations kunnen als intelligent netstation worden ingericht, zodat zij op afstand worden gemonitord, beveiligd en bestuurd. | A combined network structure has already been discussed, which meets the above requirements. In this structure, the 10 kV distribution network is fed from a 20 kV transmission network, which is configured as a closed-operated ring with multiple substations. The advantage of the 20 kV voltage level is that the technology and price of commercially available equipment do not differ much from those at the 10 kV level, while double the power can be transported. In a combined network structure, the substations in the 20 kV transmission ring are set up as Intelligent Distribution Rooms (IDR). The IDR is monitored, secured, and controlled remotely. In the substations, depending on the situation at the connected points, the power can flow in two directions. The substation can feed the 20 kV transmission ring and supply the 10 kV branches where the network stations are located. These network stations can also be set up as intelligent network stations, so they are monitored, secured, and controlled remotely. | European Technology Platform, improving energy efficiency, can be achieved by reducing network losses. This can be accomplished by choosing a higher voltage level in the MV networks. In section 2.4.3
Figuur 15.1 illustreert drie mogelijkheden om de gecombineerde netstructuur toe te passen. Het linker voorbeeld laat zien hoe een bestaand net wordt omgebouwd door de 10 kV strengen te voeden vanuit een 20/10 kV IDR. De 20 kV ring wordt bedreven als een gesloten transportring, waarbij elk 20 kV segment beveiligd wordt vanuit de IDR's. Bij een kortsluiting in een van de 20 kV segmenten zal dit direct vanuit de twee naburige IDR's worden afgeschakeld, waarna de levering als geopende transportring wordt gecontinueerd. Bij een kortsluiting in een van de 10 kV-strengen zal deze direct in de IDR worden afgeschakeld, waarna de levering op de traditionele manier via storingzoeken en herstelacties wordt gecontinueerd. | Figure 15.1 illustrates three possibilities for applying the combined network structure. The left example shows how an existing network is converted by feeding the 10 kV branches from a 20/10 kV IDR. The 20 kV ring is operated as a closed transport ring, with each 20 kV segment being secured from the IDRs. In the event of a short circuit in one of the 20 kV segments, it will be immediately disconnected from the two neighboring IDRs, after which the supply will continue as an open transport ring. In the event of a short circuit in one of the 10 kV branches, it will be immediately disconnected in the IDR, after which the supply will continue in the traditional way through fault finding and recovery actions. | the 10 kV branches where the network stations are located. These network stations can also be set up as intelligent network stations, so they are monitored, secured, and controlled remotely.
Het middelste voorbeeld laat zien dat deze opzet heel goed geschikt is voor een geleidelijke overgang van weinig naar veel intelligentie. In dit voorbeeld komen 10 kV strengen zonder intelligentie voor, maar ook 10 kV strengen met intelligente 10 kV netstations, die op afstand gemonitord, beveiligd en bestuurd worden. Bij een kortsluiting in een 10 kV segment zullen beide aangrenzende intelligente netstations direct afschakelen, waarna de levering ongestoord wordt gecontinueerd. In deze opzet kan er ook voor worden gekozen om bij nieuwbouw te kiezen voor het 20 kV spanningsniveau in de netstations. Deze worden dan ook als intelligent netstation ingericht. | The middle example shows that this setup is very well suited for a gradual transition from low to high intelligence. In this example, there are 10 kV branches without intelligence, but also 10 kV branches with intelligent 10 kV substations that are remotely monitored, secured, and controlled. In the event of a short circuit in a 10 kV segment, both adjacent intelligent substations will immediately disconnect, after which the supply will continue uninterrupted. In this setup, it is also possible to choose the 20 kV voltage level for new substations. These will then also be configured as intelligent substations. | one of the 10 kV branches, it will be immediately disconnected in the IDR, after which the supply will continue in the traditional way through fault finding and recovery actions.
Figuur 15.1 Gecombineerde netten met 20 kV transportring en 10 kV distributiestrengen | Figure 15.1 Combined networks with 20 kV transport ring and 10 kV distribution branches | supply will continue uninterrupted. In this setup, it is also possible to choose the 20 kV voltage level for new substations. These will then also be configured as intelligent substations.
Door het concept met de gecombineerde netstructuur worden de 10 kV strengen gemiddeld korter, omdat de grootste afstand door de 20 kV transportring wordt overbrugd. Het concept zorgt voor meer voedingspunten voor de 10 kV strengen, zodat per streng het aantal netstations kleiner is dan bij de traditionele opzet. Een gevolg hiervan is dat het aantal aangeslotenen per 10 kV streng kleiner is en daarmee de netbelasting in de streng. Hierdoor en door in de transportring een hoger spanningsniveau te kiezen is het netverlies in dit concept aanzienlijk kleiner, waarmee aan de eis ten aanzien van de duurzaamheid wordt tegemoetgekomen. | Due to the concept of the combined network structure, the 10 kV branches are on average shorter, as the greatest distance is bridged by the 20 kV transport ring. The concept provides more feeding points for the 10 kV branches, resulting in fewer substations per branch compared to the traditional setup. Consequently, the number of connections per 10 kV branch is smaller, and thus the network load in the branch is reduced. As a result, and by choosing a higher voltage level in the transport ring, the network loss in this concept is significantly smaller, thereby meeting the sustainability requirements. | 20 kV voltage level for new substations. These will then also be configured as intelligent substations. Figure 15.1 Combined networks with 20 kV transport ring and 10 kV distribution branches
De genoemde voordelen maken het mogelijk dat, in vergelijking met het traditionele netontwerp, nu grotere hoeveelheden decentrale opwekking kunnen worden ingepast in het distributienet, zowel op 10 kV als op 20 kV niveau. De opzet van het beveiligingsconcept is zodanig dat dit geen belemmering vormt voor het tweerichtingsverkeer van het elektrische vermogen. Ook de spanningshuishouding verbetert door de grotere transportcapaciteit van de transportring en doordat de strengen korter zijn. Door het beveiligingsconcept en doordat een 10 kV-streng minder aangeslotenen bedient, wordt het aantal storingsminuten aanzienlijk beperkt. | The mentioned advantages make it possible that, compared to the traditional network design, larger amounts of decentralized generation can now be integrated into the distribution network, both at the 10 kV and 20 kV levels. The design of the security concept is such that it does not hinder the bidirectional flow of electrical power. The voltage management also improves due to the greater transport capacity of the transport ring and because the sections are shorter. Due to the security concept and because a 10 kV section serves fewer connections, the number of outage minutes is significantly reduced. | is reduced. As a result, and by choosing a higher voltage level in the transport ring, the network loss in this concept is significantly smaller, thereby meeting the sustainability requirements.
Figuur 15.2 geeft een voorbeeld van een 20/10 kV IDR die 10 kV strengen met conventionele netstations voedt. De inkomende en uitgaande 10 en 20 kV kabels en de 20/10 kV transformator zijn beveiligd met op afstand bestuurbare vermogenschakelaars. Alle velden zijn voorzien van op afstand uitleesbare sensoren. | Figure 15.2 provides an example of a 20/10 kV IDR that feeds 10 kV strands with conventional substations. The incoming and outgoing 10 and 20 kV cables and the 20/10 kV transformer are protected with remotely controlled circuit breakers. All fields are equipped with remotely readable sensors. | transport ring and because the sections are shorter. Due to the security concept and because a 10 kV section serves fewer connections, the number of outage minutes is significantly reduced.
Figuur 15.2 Voorbeeld van een 20/10 kV IDR en 10 kV netstations | Figure 15.2 Example of a 20/10 kV IDR and 10 kV substations | substations. The incoming and outgoing 10 and 20 kV cables and the 20/10 kV transformer are protected with remotely controlled circuit breakers. All fields are equipped with remotely readable sensors.
De getoonde gecombineerde structuur kan ook goed worden toegepast in 10 kV netten zonder te kiezen voor omzetting van het vermogenstransport naar het 20 kV niveau. Hierbij worden extra investeringen voor de transformatoren en het 20 kV railsysteem in de IDR's uitgespaard. De voordelen van de toegenomen transportcapaciteit en de afgenomen verliezen vallen dan weg. Ook is dan de hoeveelheid in te passen decentrale opwekking minder groot. Wel is voor bi-directioneel vermogenstransport aanvullende richtingsgevoelige beveiliging nodig. | The shown combined structure can also be effectively applied in 10 kV networks without opting for the conversion of power transport to the 20 kV level. This avoids additional investments in transformers and the 20 kV bus system in the IDRs. However, the benefits of increased transport capacity and reduced losses are then lost. Additionally, the amount of decentralized generation that can be integrated is smaller. For bi-directional power transport, additional directional-sensitive protection is required. | 20/10 kV transformer are protected with remotely controlled circuit breakers. All fields are equipped with remotely readable sensors. Figure 15.2 Example of a 20/10 kV IDR and 10 kV substations
15.3.2 MS-distributienet met intelligent knooppunt in de open ring | 15.3.2 Medium Voltage Distribution Network with Intelligent Node in the Open Ring | increased transport capacity and reduced losses are then lost. Additionally, the amount of decentralized generation that can be integrated is smaller. For bi-directional power transport, additional directional-sensitive protection is required.
De bestaande MS-distributienetten zijn meestal met een ringstructuur uitgevoerd, maar worden radiaal bedreven. Het normale spanningsprofiel van de MS-strengen is een afnemende spanning met toenemende afstand van het onderstation. De maximale lengte en de maximale belasting van de strengen wordt onder andere begrensd door de maximale spanningsdaling (zie | The existing medium voltage (MV) distribution networks are usually designed with a ring structure but are operated radially. The normal voltage profile of the MV feeders shows a decreasing voltage with increasing distance from the substation. The maximum length and maximum load of the feeders are, among other things, limited by the maximum voltage drop (see | of decentralized generation that can be integrated is smaller. For bi-directional power transport, additional directional-sensitive protection is required. 15.3.2 Medium Voltage Distribution Network with Intelligent Node in the Open Ring
paragraaf 13.3 | paragraph 13.3 | shows a decreasing voltage with increasing distance from the substation. The maximum length and maximum load of the feeders are, among other things, limited by the maximum voltage drop (see
). Figuur 15.3 geeft een voorbeeld van twee MS-strengen, die beide worden gevoed vanuit een gezamenlijk onderstation. In de onderste van de twee afgebeelde strengen is een decentrale opwekker met een nominaal vermogen van 4 MVA aanwezig. De belasting van de netstations is 300 kW bij een cos(φ) van 0,9. De decentrale opwekker levert 3,2 MW met een cos(φ) van 0,85. | Figure 15.3 provides an example of two medium-voltage (MV) feeders, both supplied from a common substation. In the lower of the two depicted feeders, there is a decentralized generator with a nominal capacity of 4 MVA. The load of the network stations is 300 kW with a power factor (cos(φ)) of 0.9. The decentralized generator supplies 3.2 MW with a power factor (cos(φ)) of 0.85. | decreasing voltage with increasing distance from the substation. The maximum length and maximum load of the feeders are, among other things, limited by the maximum voltage drop (see paragraph 13.3
Figuur 15.3 MS-strengen met en zonder opwekking | Figure 15.3 Medium Voltage lines with and without generation | MVA. The load of the network stations is 300 kW with a power factor (cos(φ)) of 0.9. The decentralized generator supplies 3.2 MW with a power factor (cos(φ)) of 0.85.
Door het opgewekte vermogen in de onderste van de twee afgebeelde strengen is in de kabelsecties tussen het onderstation en de MS-ruimte, waar de generator is aangesloten, de richting van het vermogen naar het onderstation toe. Als gevolg stijgt de spanning in die streng, om in de netstations die verder weg liggen weer af te nemen. Figuur 15.4 laat dit zien voor de 'Open ring met opwekking', waar de spanning in dit voorbeeld oploopt tot 10,7 kV bij een spanning op de MS-rail in het onderstation van 10,54 kV. De spanning van de streng zonder opwekking daalt tot 10,35 kV. | Due to the generated power in the lower of the two depicted sections, the direction of power in the cable sections between the substation and the medium voltage (MV) room, where the generator is connected, is towards the substation. As a result, the voltage in that section rises, only to decrease again in the substations that are further away. Figure 15.4 illustrates this for the 'Open ring with generation,' where the voltage in this example increases to 10.7 kV with a voltage on the MV busbar in the substation of 10.54 kV. The voltage of the section without generation drops to 10.35 kV. | kW with a power factor (cos(φ)) of 0.9. The decentralized generator supplies 3.2 MW with a power factor (cos(φ)) of 0.85. Figure 15.3 Medium Voltage lines with and without generation
Indien de netopening gesloten zou worden, verbetert het spanningsprofiel, omdat het gevraagde vermogen in de bovenste streng nu gedeeltelijk geleverd wordt door de decentrale opwekker in de onderste streng. Figuur 15.4 laat dit zien voor de 'Gesloten ring wel/geen opwekking', waar de spanning maximaal 10,64 kV en minimaal 10,47 kV bedraagt. Het sluiten van de netopening heeft een positieve uitwerking voor de spanningskwaliteit, maar heeft als nadeel dat het kortsluitvermogen in het MS-net toeneemt. Om een selectieve beveiliging voor de configuratie met de gesloten ring te realiseren, moet de beveiliging worden uitgebreid, waardoor deze complexer wordt. | If the network opening were to be closed, the voltage profile would improve because the required power in the upper section would now be partially supplied by the decentralized generator in the lower section. Figure 15.4 illustrates this for the 'Closed ring with/without generation,' where the voltage ranges from a maximum of 10.64 kV to a minimum of 10.47 kV. Closing the network opening has a positive effect on voltage quality, but it has the drawback of increasing the short-circuit power in the MV network. To achieve selective protection for the configuration with the closed ring, the protection system must be expanded, making it more complex. | this example increases to 10.7 kV with a voltage on the MV busbar in the substation of 10.54 kV. The voltage of the section without generation drops to 10.35 kV.
Figuur 15.4 Spanningsprofiel in MS-strengen met en zonder opwekking | Figure 15.4 Voltage profile in MV feeders with and without generation | of increasing the short-circuit power in the MV network. To achieve selective protection for the configuration with the closed ring, the protection system must be expanded, making it more complex.
In de literatuur is voorgesteld op de plaats van de netopening van een open bedreven MS-ring een 'intelligent knooppunt' te plaatsen (Provoost, 2005-2). Het idee achter dit concept is de vermogens over twee strengen te verdelen met behulp van een vermogenselektronische power flow controller (PFC). Figuur 15.5 geeft een voorbeeld van een toepassing van het intelligente knooppunt. De stromen van de beide aangesloten strengen A en B worden gemeten en door de lokale autonome besturing verwerkt, evenals de spanningen aan beide zijden van de netopening, op de interne knooppunten A en B. Ook de stroom die ontstaat door de werking van de PFC wordt verwerkt. Met deze meetwaarden bestuurt het lokale autonome proces de PFC. | In the literature, it has been proposed to place an 'intelligent node' at the location of the network opening of an open-operated MV ring (Provoost, 2005-2). The idea behind this concept is to distribute the power over two branches using a power electronic power flow controller (PFC). Figure 15.5 provides an example of an application of the intelligent node. The currents of the two connected branches A and B are measured and processed by the local autonomous control, as well as the voltages on both sides of the network opening, at the internal nodes A and B. The current generated by the operation of the PFC is also processed. With these measurements, the local autonomous process controls the PFC. | selective protection for the configuration with the closed ring, the protection system must be expanded, making it more complex. Figure 15.4 Voltage profile in MV feeders with and without generation
Door toepassing van de PFC zal de spanningskwaliteit verbeteren op vergelijkbare wijze als door het sluiten van de netopening zal gebeuren. De PFC laat echter geen kortsluitstromen door, zodat het intelligente knooppunt geen invloed heeft op het kortsluitvermogen. | By applying the PFC, the voltage quality will improve in a similar manner as it would by closing the network opening. However, the PFC does not allow short-circuit currents to pass through, so the intelligent node does not affect the short-circuit capacity. | opening, at the internal nodes A and B. The current generated by the operation of the PFC is also processed. With these measurements, the local autonomous process controls the PFC.
Het intelligente knooppunt komt tegemoet aan de doelstelling om meer decentrale opwekking in het distributienet mogelijk te maken in die gevallen dat de vermogensverdeling over de diverse strengen ongelijk is. Ook bevordert het intelligente knooppunt de betrouwbaarheid, doordat tijdens het herstelproces na een kortsluiting de netopening direct op afstand gesloten kan worden nadat de gestoorde kabelsectie geïsoleerd is. Het probleem dat een grote hoeveelheid decentrale opwekking de beveiliging verblindt voor overbelasting wordt door het intelligente knooppunt niet weggenomen, zodat de beveiliging in dit concept toch aangepast moet worden. | The intelligent node meets the objective of enabling more decentralized generation in the distribution network in cases where the power distribution across various branches is unequal. The intelligent node also enhances reliability, as during the recovery process after a short circuit, the network opening can be closed remotely immediately after the faulty cable section is isolated. The issue that a large amount of decentralized generation blinds the protection against overload is not resolved by the intelligent node, so the protection in this concept still needs to be adjusted. | manner as it would by closing the network opening. However, the PFC does not allow short-circuit currents to pass through, so the intelligent node does not affect the short-circuit capacity.
Figuur 15.5 Toepassing van een intelligent knooppunt bij een netopening | Figure 15.5 Application of an intelligent node in a network opening | that a large amount of decentralized generation blinds the protection against overload is not resolved by the intelligent node, so the protection in this concept still needs to be adjusted.
15.3.3 Eerste stap naar een MS-distributienet met automatisering in de onderstations | 15.3.3 First step towards an MV distribution network with automation in the substations | overload is not resolved by the intelligent node, so the protection in this concept still needs to be adjusted. Figure 15.5 Application of an intelligent node in a network opening
De intelligente systemen die ondermeer voor het realiseren van intelligente knooppunten nodig zijn, verkeren in 2011 nog in de conceptuele fase. De eerste stappen naar intelligente systemen worden langzaam gemaakt. Uitgaande van het huidige traditionele MS-distributienet wordt gewerkt aan oplossingen, waarbij onderstations, schakelstations en regelstations worden voorzien van op afstand uitleesbare sensoren en bedienbare schakelaars. Dit is bijvoorbeeld mogelijk met een systeem als de SASensor, zoals beschreven in | The intelligent systems required for the realization of intelligent nodes are still in the conceptual phase as of 2011. The first steps towards intelligent systems are being taken slowly. Based on the current traditional MV distribution network, solutions are being developed where substations, switching stations, and control stations are equipped with remotely readable sensors and controllable switches. This is possible, for example, with a system like the SASensor, as described in | concept still needs to be adjusted. Figure 15.5 Application of an intelligent node in a network opening 15.3.3 First step towards an MV distribution network with automation in the substations
paragraaf 14.2.7 | paragraph 14.2.7 | where substations, switching stations, and control stations are equipped with remotely readable sensors and controllable switches. This is possible, for example, with a system like the SASensor, as described in
(Riet, 2005). Figuur 15.6 laat zien hoe in een proefproject de SASensor-techniek in een bestaande situatie naast de conventionele beveiliging wordt toegepast. Het systeem meet continu de spanning en stroom. Hierdoor kunnen de beveiligingsfuncties centraal door dit systeem worden uitgevoerd. De metingen staan ter beschikking aan bedrijfsvoering, zodat een betere bewaking mogelijk is. Door continu de kwaliteit van de spanning te bewaken kan tijdig worden ingespeeld op mogelijke problemen. In geval van een storing heeft bedrijfsvoering direct de beschikking over alle meetgegevens en kan met behulp van een foutplaatslokalisatiesysteem de fout snel opgespoord worden. | (Riet, 2005). Figure 15.6 shows how the SASensor technology is applied in an existing situation alongside conventional protection in a pilot project. The system continuously measures voltage and current. As a result, the protection functions can be centrally executed by this system. The measurements are available to operations, allowing for better monitoring. By continuously monitoring the quality of the voltage, potential problems can be addressed in a timely manner. In the event of a fault, operations have immediate access to all measurement data and can quickly locate the fault using a fault location system. | switching stations, and control stations are equipped with remotely readable sensors and controllable switches. This is possible, for example, with a system like the SASensor, as described in paragraph 14.2.7
Figuur 15.6 Onderstation 10 kV installatie met conventionele beveiliging en SASensortechniek | Figure 15.6 Substation 10 kV installation with conventional protection and SAS sensor technology | addressed in a timely manner. In the event of a fault, operations have immediate access to all measurement data and can quickly locate the fault using a fault location system.
De functies van een dergelijk systeem zijn, samengevat: | The functions of such a system are, in summary: | immediate access to all measurement data and can quickly locate the fault using a fault location system. Figure 15.6 Substation 10 kV installation with conventional protection and SAS sensor technology
nauwkeurige meting van stroom, spanning en vermogen | accurate measurement of current, voltage, and power | locate the fault using a fault location system. Figure 15.6 Substation 10 kV installation with conventional protection and SAS sensor technology The functions of such a system are, in summary:
standmelding van vermogenschakelaars, lastscheiders, aarders, kortsluitverklikkers | status indication of circuit breakers, load disconnectors, grounders, short-circuit indicators | system. Figure 15.6 Substation 10 kV installation with conventional protection and SAS sensor technology The functions of such a system are, in summary: accurate measurement of current, voltage, and power
signalering van beveiligingen en smeltveiligheden | signaling of protections and fuses | and SAS sensor technology The functions of such a system are, in summary: accurate measurement of current, voltage, and power status indication of circuit breakers, load disconnectors, grounders, short-circuit indicators
afstandbesturing schakelaars en lastscheiders | remote control of switches and load disconnectors | functions of such a system are, in summary: accurate measurement of current, voltage, and power status indication of circuit breakers, load disconnectors, grounders, short-circuit indicators signaling of protections and fuses
alarmafhandeling | alarmafhandeling | summary: accurate measurement of current, voltage, and power status indication of circuit breakers, load disconnectors, grounders, short-circuit indicators signaling of protections and fuses remote control of switches and load disconnectors
meting van de spanningskwaliteit | measurement of voltage quality | accurate measurement of current, voltage, and power status indication of circuit breakers, load disconnectors, grounders, short-circuit indicators signaling of protections and fuses remote control of switches and load disconnectors alarmafhandeling
foutplaatslokalisatie | foutplaatslokalisatie | voltage, and power status indication of circuit breakers, load disconnectors, grounders, short-circuit indicators signaling of protections and fuses remote control of switches and load disconnectors alarmafhandeling measurement of voltage quality
maximaal stroom-tijdbeveiliging | maximum current-time protection | and power status indication of circuit breakers, load disconnectors, grounders, short-circuit indicators signaling of protections and fuses remote control of switches and load disconnectors alarmafhandeling measurement of voltage quality foutplaatslokalisatie
aardfoutbeveiliging. | ground fault protection. | indication of circuit breakers, load disconnectors, grounders, short-circuit indicators signaling of protections and fuses remote control of switches and load disconnectors alarmafhandeling measurement of voltage quality foutplaatslokalisatie maximum current-time protection
Naast de onderstations kunnen ook strategische netstations worden uitgerust met afstandmeting, afstandsignalering en op afstand bestuurbare vermogenschakelaars. Hiermee is het al mogelijk een aanzienlijke reductie van de hersteltijd in geval van een kortsluiting te verkrijgen. Door toevoeging van automatisering kan hiermee een zelfherstellend distributienet worden gerealiseerd. | In addition to the substations, strategic network stations can also be equipped with remote measurement, remote signaling, and remotely controllable circuit breakers. This already makes it possible to achieve a significant reduction in recovery time in the event of a short circuit. By adding automation, a self-healing distribution network can be realized. | breakers, load disconnectors, grounders, short-circuit indicators signaling of protections and fuses remote control of switches and load disconnectors alarmafhandeling measurement of voltage quality foutplaatslokalisatie maximum current-time protection ground fault protection.
15.3.4 LS-distributienet | 15.3.4 Low Voltage Distribution Network | This already makes it possible to achieve a significant reduction in recovery time in the event of a short circuit. By adding automation, a self-healing distribution network can be realized.
De LS-distributienetten hebben de laagste automatiseringsgraad en de minste omschakelmogelijkheden. De nettransformatoren zijn voorzien van een vaste aftakking, zodat de spanning op dit niveau niet geregeld wordt, maar volledig afhangt van de spanningsregeling van de voedingstransformator in het onderstation. Als gevolg van de energietransitie zal de belasting sterk kunnen toenemen door toename van elektrisch rijden en ruimteverwarming met warmtepompen. Ook de hoeveelheid decentrale opwekking, voornamelijk bestaande uit micro-WKK en PV-systemen, zal toenemen. De impact van deze veranderingen op de LS-netten is naar verwachting groter dan de impact op de MS-netten. Het vermogenstransport in de LS-netten zal een veel sterker fluctuerend gedrag vertonen dan nu het geval is, met toenemende belasting van de kabels en nadelige gevolgen voor de spanningskwaliteit. Er zijn diverse ideeën, concepten en systemen om de nadelige gevolgen te beperken. De belangrijkste hebben betrekking op belastingsturing en opslag van elektrische energie. Vanwege de structuur van de LS-netten zijn de mogelijkheden om deze met afstandmeting en afstandbesturing te flexibiliseren vooralsnog gering. Om enig beeld te geven van aspecten die bij de huidige stand van de techniek nog ongewis blijken te zijn en verder onderzoek behoeven, wordt in paragraaf 15.4 een aantal initiatieven kort behandeld. | The low voltage (LV) distribution networks have the lowest degree of automation and the fewest switching options. The network transformers are equipped with a fixed tap, so the voltage at this level is not regulated but entirely depends on the voltage regulation of the supply transformer in the substation. As a result of the energy transition, the load can significantly increase due to the rise in electric vehicles and space heating with heat pumps. The amount of decentralized generation, mainly consisting of micro-CHP and PV systems, will also increase. The impact of these changes on the LV networks is expected to be greater than the impact on the medium voltage (MV) networks. Power transport in the LV networks will exhibit much more fluctuating behavior than it currently does, with increasing cable loads and adverse effects on voltage quality. There are various ideas, concepts, and systems to mitigate these adverse effects. The most important ones relate to load control and the storage of electrical energy. Due to the structure of the LV networks, the possibilities to make them more flexible with remote measurement and remote control are still limited. To provide some insight into aspects that are still uncertain with the current state of technology and require further research, a number of initiatives are briefly discussed in paragraph 15.4. | to achieve a significant reduction in recovery time in the event of a short circuit. By adding automation, a self-healing distribution network can be realized. 15.3.4 Low Voltage Distribution Network
Een voorbeeld van een initiatief met betrekking tot belastingsturing is een proefproject waarin met behulp van intelligente meters het beslisgedrag van aangeslotenen wordt onderzocht. In dit proefproject worden in een nieuw te bouwen woonomgeving 57 woningen en 246 appartementen voorzien van PV-systemen, warmtepompen en een gezamenlijke WKK-installatie. De aangeslotenen krijgen via een display een grote hoeveelheid informatie over onder andere de weersverwachting en actuele energietarieven. Zij kunnen met de aangeboden informatie beslissen wanneer het voordelig is om grote energieverbruikers als wasmachines in te schakelen. De vraag is of met aanvullende prijsprikkels de aangeslotenen tot een voorspelbaar verbruikspatroon zijn te verleiden. | An example of an initiative related to demand-side management is a pilot project in which the decision-making behavior of participants is studied using smart meters. In this pilot project, 57 houses and 246 apartments in a newly built residential area are equipped with PV systems, heat pumps, and a shared CHP installation. The participants receive a large amount of information via a display, including weather forecasts and current energy rates. With the provided information, they can decide when it is advantageous to turn on large energy consumers such as washing machines. The question is whether additional price incentives can entice the participants into a predictable consumption pattern. | To provide some insight into aspects that are still uncertain with the current state of technology and require further research, a number of initiatives are briefly discussed in paragraph 15.4.
15.4 Technieken | 15.4 Techniques | when it is advantageous to turn on large energy consumers such as washing machines. The question is whether additional price incentives can entice the participants into a predictable consumption pattern.
Op verschillende fronten worden anno 2011 technieken ontwikkeld die worden ingezet in proefprojecten om te komen tot een intelligent net. In deze proefprojecten worden technieken van diverse automatiseringsgraad toegepast. Als voorbeeld hebben deze proefprojecten betrekking op het afstemmen van belasting op opwekking met behulp van duurzame bronnen of betrekking op introductie van schakelende of regelende componenten in het laagspanningsnet. Daarnaast zijn er wereldwijd grote ontwikkelingen rondom de opslag van elektrische energie. Deze twee voorbeelden worden hieronder kort toegelicht. | On various fronts, techniques are being developed in 2011 that are used in pilot projects to create an intelligent grid. In these pilot projects, techniques of varying degrees of automation are applied. For example, these pilot projects involve matching load to generation using sustainable sources or the introduction of switching or regulating components in the low-voltage network. Additionally, there are significant global developments in the storage of electrical energy. These two examples are briefly explained below. | is advantageous to turn on large energy consumers such as washing machines. The question is whether additional price incentives can entice the participants into a predictable consumption pattern. 15.4 Techniques
15.4.1 Afstemmen van belasting op opwekking | 15.4.1 Matching Load to Generation | the introduction of switching or regulating components in the low-voltage network. Additionally, there are significant global developments in the storage of electrical energy. These two examples are briefly explained below.
In 2011 zijn systemen in ontwikkeling die in een distributienet met hoge concentratie aan decentrale opwekking vraag en aanbod van elektrische energie optimaliseert, gebaseerd op een mogelijk te behalen prijsvoordeel. Uitgangspunt is dat op de daken van woonhuizen zonnecollectoren zijn geïnstalleerd, in de huizen warmtepompen of micro-WKK installaties zijn opgesteld en dat bepaalde verbruikstoestellen automatisch worden aangestuurd. Zo een systeem is gericht op het meedoen in en deelnemen aan de elektriciteitsmarkt, waarbij een goede balans wordt gevonden tussen de belangen van de aangeslotene, de producenten en de netbeheerder. Door de klanten een prijssignaal te geven dat de situatie op de elektriciteitsmarkt weerspiegelt, zullen zij hun verbruik en hun productie (indien aanwezig) daarop afstemmen. De gedachte is dat in een periode van overschot aan duurzame energie, omdat het toevallig hard waait bij zonnig weer, de elektriciteitsprijs laag is en de verbruikers worden aangemoedigd de energie uit het distributienet af te nemen. Bij een tekort aan duurzame energie worden zij financieel aangemoedigd om minder af te nemen en eventueel meer te produceren. Het systeem zorgt dus voor een grotere betrokkenheid van de aangeslotenen bij de energievoorziening. Het bevordert eigen opwekking omdat er geld mee kan worden verdiend en het ondersteunt de duurzame samenleving. Het systeem fungeert als open flexibele marktplaats. Vooral duurzame energie zal hier profijt van hebben, omdat ondanks het variabele en moeilijk voorspelbare karakter van de duurzame bronnen de beschikbaarheid met financiële prikkels aantrekkelijk wordt gemaakt. De terugverdientijd op eigen investeringen in duurzame systemen wordt hierdoor sterk verbeterd. | In 2011, systems were being developed that optimize the supply and demand of electrical energy in a distribution network with a high concentration of decentralized generation, based on potential price advantages. The premise is that solar collectors are installed on the roofs of residential houses, heat pumps or micro-CHP installations are set up in the houses, and certain consumption devices are automatically controlled. Such a system is aimed at participating in and engaging with the electricity market, finding a good balance between the interests of the consumers, the producers, and the grid operator. By providing customers with a price signal that reflects the situation in the electricity market, they will adjust their consumption and production (if available) accordingly. The idea is that during periods of surplus sustainable energy, because it happens to be very windy and sunny, the electricity price is low, and consumers are encouraged to draw energy from the distribution network. In case of a shortage of sustainable energy, they are financially incentivized to consume less and possibly produce more. The system thus ensures greater involvement of consumers in the energy supply. It promotes self-generation because it can be profitable and supports a sustainable society. The system functions as an open flexible marketplace. Sustainable energy, in particular, will benefit from this, as despite the variable and unpredictable nature of sustainable sources, availability is made attractive with financial incentives. The payback period on personal investments in sustainable systems is thereby greatly improved. | regulating components in the low-voltage network. Additionally, there are significant global developments in the storage of electrical energy. These two examples are briefly explained below. 15.4.1 Matching Load to Generation
In een van de concepten van een dergelijk systeem wordt elk apparaat gerepresenteerd door een software-agent, die het proces van dat apparaat economisch optimaal probeert te laten werken (Kok, 2006). De software-agenten onderhandelen op een elektronische markt over hun verbruik of productie van elektriciteit. De resulterende marktprijs bepaalt het volume van het vermogen dat elk vertegenwoordigd apparaat mag verbruiken of produceren. De apparatuur wordt ingedeeld in een aantal klassen, waarvan de drie belangrijkste zijn: | In one of the concepts of such a system, each device is represented by a software agent, which tries to make the process of that device work economically optimally (Kok, 2006). The software agents negotiate on an electronic market about their consumption or production of electricity. The resulting market price determines the volume of power that each represented device is allowed to consume or produce. The equipment is classified into several categories, of which the three main ones are: | as despite the variable and unpredictable nature of sustainable sources, availability is made attractive with financial incentives. The payback period on personal investments in sustainable systems is thereby greatly improved.
apparaten met een stochastisch karakter: PV-systemen en windturbines zijn afhankelijk van het weer en hun productie kan sterk wisselen | devices with a stochastic nature: PV systems and wind turbines depend on the weather, and their production can vary greatly | price determines the volume of power that each represented device is allowed to consume or produce. The equipment is classified into several categories, of which the three main ones are:
apparaten waarvan het verbruik in tijd kan worden verschoven: dit zijn apparaten die gedurende een bepaalde tijdsduur moet werken, ongeacht het exacte tijdstip; voorbeelden zijn systemen voor wassen, verwarmen, koelen, ventilatie en oplaadbare auto's | devices whose consumption can be shifted in time: these are devices that need to operate for a certain duration, regardless of the exact time; examples include systems for washing, heating, cooling, ventilation, and rechargeable cars | into several categories, of which the three main ones are: devices with a stochastic nature: PV systems and wind turbines depend on the weather, and their production can vary greatly
apparaten waarvan de werking door de klant is ingesteld: dit zijn apparaten die door de klant worden aangezet om op het specifieke moment arbeid te verrichten; voorbeelden zijn verlichting, computers en apparatuur voor audio en video. | devices whose operation is set by the customer: these are devices that are turned on by the customer to perform work at a specific moment; examples include lighting, computers, and audio and video equipment. | shifted in time: these are devices that need to operate for a certain duration, regardless of the exact time; examples include systems for washing, heating, cooling, ventilation, and rechargeable cars
De agenten zorgen ervoor dat het verbruik zoveel mogelijk plaatsvindt tijdens momenten van lage energieprijzen en dat de productie van niet-duurzame bronnen zoveel mogelijk wordt verschoven naar momenten van hoge energieprijzen. Het systeem is voor een proefproject geïnstalleerd in een woonomgeving. | The agents ensure that consumption occurs as much as possible during periods of low energy prices and that the production from non-sustainable sources is shifted as much as possible to periods of high energy prices. The system has been installed in a residential environment for a pilot project. | set by the customer: these are devices that are turned on by the customer to perform work at a specific moment; examples include lighting, computers, and audio and video equipment.
15.4.2 Regelen in een laagspanningsnet | 15.4.2 Control in a Low Voltage Network | the production from non-sustainable sources is shifted as much as possible to periods of high energy prices. The system has been installed in a residential environment for a pilot project.
De spanning in een LS-distributienet wordt ten opzichte van het MS-niveau niet geregeld. De transformatoren in de netstations hebben een vaste overzetverhouding, die is ingesteld op een van vijf mogelijke standen. Omdat het in sommige gevallen toch wenselijk is de spanning op een vast niveau te kunnen regelen, is een MS/LS geregelde transformator geïntroduceerd. Deze transformator onderscheidt zich van een standaard distributietransformator door onder belasting te kunnen overschakelen naar een ander spanningsniveau. Bij zwakke netten of sterk wisselende belastingen zal de transformator met zijn traploze regelaar de spanning aan de LS-zijde stabiliseren, onafhankelijk van het getransporteerde vermogen. Dit concept is toegepast op een distributietransformator (10kV/400V, 50Hz, 3 fasen), voorzien van elektronische vermogensregeling en besturing. De wikkelingen van de transformator worden met IGBT-vermogenselektronica op 10kV niveau zodanig geschakeld dat spanningsfluctuaties aan LS-zijde continu en traploos worden weggeregeld, zowel in belaste als in onbelaste toestand. De werking is beschreven in paragraaf 4.3. De regelaar werkt autonoom, maar kan in een intelligent net worden bestuurd. | The voltage in a low voltage (LV) distribution network is not regulated relative to the medium voltage (MV) level. The transformers in the substations have a fixed transformation ratio, which is set to one of five possible positions. Because it is sometimes desirable to regulate the voltage at a fixed level, an MV/LV regulated transformer has been introduced. This transformer differs from a standard distribution transformer by being able to switch to a different voltage level under load. In weak networks or with highly variable loads, the transformer will stabilize the voltage on the LV side with its stepless regulator, regardless of the transmitted power. This concept has been applied to a distribution transformer (10kV/400V, 50Hz, 3 phases), equipped with electronic power regulation and control. The windings of the transformer are switched with IGBT power electronics at the 10kV level in such a way that voltage fluctuations on the LV side are continuously and steplessly regulated away, both under load and no-load conditions. The operation is described in section 4.3. The regulator operates autonomously but can be controlled in an intelligent network. | as much as possible to periods of high energy prices. The system has been installed in a residential environment for a pilot project. 15.4.2 Control in a Low Voltage Network
15.4.3 Opslagsystemen | 15.4.3 Storage Systems | continuously and steplessly regulated away, both under load and no-load conditions. The operation is described in section 4.3. The regulator operates autonomously but can be controlled in an intelligent network.
De grote fluctuatie in de vermogensvraag door de LS-netten leidt tot grote pieken en dalen in het vermogenstransport in het MS-net. Deze pieken en dalen kunnen met behulp van een opslagsysteem voor elektrische energie worden genivelleerd (peak shaving), waardoor meer ruimte voor elektriciteitstransport in het net ontstaat. Een van de mogelijkheden is om bij of onder een netstation een opslagsysteem te bouwen dat duurzame energie kan opslaan en bovendien het MS-net kan ontlasten. Dit concept wordt Smart Storage genoemd. Het systeem is geschikt voor netgekoppeld bedrijf en voor eilandbedrijf en het kan automatisch omschakelen tussen deze twee toestanden. Een bijkomend voordeel van dit systeem is dat bij een storing in het MS-net het achterliggende LS-net gedurende beperkte tijd kan worden gevoed, hetgeen de betrouwbaarheid vergroot. | The large fluctuations in power demand by the low-voltage (LV) networks lead to significant peaks and troughs in power transmission in the medium-voltage (MV) network. These peaks and troughs can be leveled out using an electrical energy storage system (peak shaving), thereby creating more capacity for electricity transmission in the network. One of the possibilities is to build a storage system at or under a substation that can store renewable energy and also relieve the MV network. This concept is called Smart Storage. The system is suitable for both grid-connected operation and island operation, and it can automatically switch between these two states. An additional advantage of this system is that in the event of a failure in the MV network, the underlying LV network can be supplied for a limited time, which increases reliability. | regulated away, both under load and no-load conditions. The operation is described in section 4.3. The regulator operates autonomously but can be controlled in an intelligent network. 15.4.3 Storage Systems
Figuur 15.7 Redox-flow opslagsysteem voor 10 kW en 100 kWh | Figure 15.7 Redox-flow storage system for 10 kW and 100 kWh | advantage of this system is that in the event of a failure in the MV network, the underlying LV network can be supplied for a limited time, which increases reliability.
Figuur 15.7 toont een Redox-flow opslagsysteem met een vermogen van 10 kW en een hoeveelheid opgeslagen energie van 100 kWh en illustreert dat de systemen voor opslag van elektrische energie nog niet erg compact zijn. | Figure 15.7 shows a Redox-flow storage system with a capacity of 10 kW and an amount of stored energy of 100 kWh, illustrating that the systems for storing electrical energy are not yet very compact. | failure in the MV network, the underlying LV network can be supplied for a limited time, which increases reliability. Figure 15.7 Redox-flow storage system for 10 kW and 100 kWh
Ook voor het MS-niveau worden systemen voor opslag ontwikkeld. Figuur 15.8 toont een Li-ion opslagsysteem dat is opgebouwd uit modules van 646 V en 41 Ah. Deze systemen worden gebruikt in statische blindvermogenscompensatiesystemen (static var) met mogelijkheden voor energieopslag. Een opslagsysteem dat met 8 modules is opgebouwd, is geschikt voor een nominale spanning van 5,2 kV en kan gedurende een uur 200 kW energie leveren (Saft, 2008). | Storage systems are also being developed for the medium voltage (MV) level. Figure 15.8 shows a Li-ion storage system composed of modules with 646 V and 41 Ah. These systems are used in static var compensation systems with energy storage capabilities. A storage system built with 8 modules is suitable for a nominal voltage of 5.2 kV and can deliver 200 kW of energy for one hour (Saft, 2008). | storage system with a capacity of 10 kW and an amount of stored energy of 100 kWh, illustrating that the systems for storing electrical energy are not yet very compact.
Figuur 15.9 toont een NaS opslagsysteem op basis van modules van 1 MW en een energie-inhoud van 7,2 MWh. De modules werken op een spanning van 480 V, die via step-up transformatoren wordt omgezet in 12,5 en 34,5 kV. | Figure 15.9 shows a NaS storage system based on modules of 1 MW and an energy content of 7.2 MWh. The modules operate at a voltage of 480 V, which is converted to 12.5 and 34.5 kV via step-up transformers. | storage capabilities. A storage system built with 8 modules is suitable for a nominal voltage of 5.2 kV and can deliver 200 kW of energy for one hour (Saft, 2008).
De ontwikkelingen in de batterijtechnologie in de afgelopen 20 jaar zijn voornamelijk te danken aan de inspanningen voor de consumentenelektronica. De ontwikkelingen in de batterijsystemen voor elektrische auto's hebben ertoe geleid dat de ontwikkelingen in batterijtechnologie voor de elektriciteitsystemen in een stroom-versnelling terecht kwamen. Ook ontwikkelingen die de vermogenselektronica economisch interessanter hebben gemaakt, zoals de ontwikkeling van betrouwbare converters, hebben daaraan bijgedragen. Voor de opslagsystemen zijn diverse elektrochemische technologieën ontwikkeld. Een zestal wordt hieronder kort behandeld. | The developments in battery technology over the past 20 years are primarily due to efforts in consumer electronics. The advancements in battery systems for electric cars have accelerated the developments in battery technology for power systems. Additionally, developments that have made power electronics more economically attractive, such as the development of reliable converters, have contributed to this progress. Various electrochemical technologies have been developed for storage systems. Six of these are briefly discussed below. | of 1 MW and an energy content of 7.2 MWh. The modules operate at a voltage of 480 V, which is converted to 12.5 and 34.5 kV via step-up transformers.
Figuur 15.8 Li-ion opslagsysteem met modules voor 646 V en 41 Ah | Figure 15.8 Li-ion storage system with modules for 646 V and 41 Ah | economically attractive, such as the development of reliable converters, have contributed to this progress. Various electrochemical technologies have been developed for storage systems. Six of these are briefly discussed below.
Figuur 15.9 Li-ion opslagsysteem op basis van modules van 1 MW en 7,2 MWh | Figure 15.9 Li-ion storage system based on modules of 1 MW and 7.2 MWh | progress. Various electrochemical technologies have been developed for storage systems. Six of these are briefly discussed below. Figure 15.8 Li-ion storage system with modules for 646 V and 41 Ah
Natrium zwavel | Sodium sulfur | briefly discussed below. Figure 15.8 Li-ion storage system with modules for 646 V and 41 Ah Figure 15.9 Li-ion storage system based on modules of 1 MW and 7.2 MWh
De natrium zwavel (NaS) batterij is een batterijsysteem dat op een hoge temperatuur werkt. Het bestaat uit een positieve elektrode van gesmolten zwavel en een negatieve elektrode van gesmolten natrium, gescheiden door een vaste bèta aluminiumoxide keramische elektrolyt. Het elektrolyt laat alleen positieve natriumionen passeren om met de zwavel te reageren. | The sodium sulfur (NaS) battery is a battery system that operates at a high temperature. It consists of a positive electrode made of molten sulfur and a negative electrode made of molten sodium, separated by a solid beta-alumina ceramic electrolyte. The electrolyte only allows positive sodium ions to pass through to react with the sulfur. | below. Figure 15.8 Li-ion storage system with modules for 646 V and 41 Ah Figure 15.9 Li-ion storage system based on modules of 1 MW and 7.2 MWh Sodium sulfur
Flow-batterij technologie | Flow battery technology | and a negative electrode made of molten sodium, separated by a solid beta-alumina ceramic electrolyte. The electrolyte only allows positive sodium ions to pass through to react with the sulfur.
Een flow-batterij is op elektrolyt gebaseerd waarin een of meer elektro-actieve stoffen door een elektrochemische cel stromen. In de cel wordt de chemische energie omgezet in elektrische energie en omgekeerd. De elektrolyt kan buiten het systeem worden opgeslagen en wordt door de elektrochemische cellen gepompt. Flow-batterijen kunnen eenvoudig worden ververst door de elektrolyt te vervangen. Figuur 15.7 toont een voorbeeld van een Redox-flow batterij. | A flow battery is based on an electrolyte in which one or more electro-active substances flow through an electrochemical cell. In the cell, chemical energy is converted into electrical energy and vice versa. The electrolyte can be stored outside the system and is pumped through the electrochemical cells. Flow batteries can be easily refreshed by replacing the electrolyte. Figure 15.7 shows an example of a Redox flow battery. | electrode made of molten sodium, separated by a solid beta-alumina ceramic electrolyte. The electrolyte only allows positive sodium ions to pass through to react with the sulfur. Flow battery technology
Nikkel-cadmium | Nickel-cadmium | outside the system and is pumped through the electrochemical cells. Flow batteries can be easily refreshed by replacing the electrolyte. Figure 15.7 shows an example of a Redox flow battery.
De Nikkel-cadmium-accu (NiCd) is een droge accu. In het verleden is bij NiCd-accu's onder zeer specifieke en uitzonderlijke omstandigheden een geheugeneffect aangetoond. Dat houdt in dat bij herhaaldelijk gedeeltelijk ontladen de capaciteit afneemt tot de daarbij daadwerkelijk gebruikte capaciteit. Moderne NiCd-accu's hebben geen last van het geheugeneffect. De capaciteit gaat omlaag door veroudering, te hoge temperatuur, te ver ontladen (hetgeen wel wordt gedaan als remedie tegen het geheugeneffect), te lang opladen, en verkeerd om aansluiten. | The Nickel-cadmium battery (NiCd) is a dry battery. In the past, under very specific and exceptional circumstances, a memory effect has been demonstrated in NiCd batteries. This means that with repeated partial discharges, the capacity decreases to the actually used capacity. Modern NiCd batteries do not suffer from the memory effect. The capacity decreases due to aging, high temperature, over-discharging (which is sometimes done as a remedy against the memory effect), overcharging, and incorrect polarity connection. | the system and is pumped through the electrochemical cells. Flow batteries can be easily refreshed by replacing the electrolyte. Figure 15.7 shows an example of a Redox flow battery. Nickel-cadmium
De energiedichtheid van NiCd-accu's is laag: 45Wh/kg. Daarentegen is de vermogensdichtheid van dit soort accu's hoog: 200W/kg. Tegenwoordig worden NiCd-accu's steeds minder gebruikt en winnen NiMH-accu's terrein. | The energy density of NiCd batteries is low: 45Wh/kg. On the other hand, the power density of this type of battery is high: 200W/kg. Nowadays, NiCd batteries are being used less and less, and NiMH batteries are gaining ground. | suffer from the memory effect. The capacity decreases due to aging, high temperature, over-discharging (which is sometimes done as a remedy against the memory effect), overcharging, and incorrect polarity connection.
Nikkel-metaalhydride | Nickel-metal hydride | On the other hand, the power density of this type of battery is high: 200W/kg. Nowadays, NiCd batteries are being used less and less, and NiMH batteries are gaining ground.
De nikkel-metaalhydride-accu (NiMH) gebruikt een waterstofabsorberende legering voor de negatieve elektrode in plaats van cadmium. Een NiMH-accu kan bij dezelfde afmetingen meer energie opslaan dan een NiCd-batterij maar heeft minder vermogen. Vergeleken met de lithium-ion-accu is de energiedichtheid lager en de zelfontlading hoger. NiMH-cellen worden geassembleerd tot opslagsystemen voor een hogere spanning zoals in elektrische auto's. | The nickel-metal hydride battery (NiMH) uses a hydrogen-absorbing alloy for the negative electrode instead of cadmium. A NiMH battery can store more energy than a NiCd battery of the same size but has less power. Compared to the lithium-ion battery, the energy density is lower and the self-discharge rate is higher. NiMH cells are assembled into storage systems for higher voltage applications, such as in electric cars. | other hand, the power density of this type of battery is high: 200W/kg. Nowadays, NiCd batteries are being used less and less, and NiMH batteries are gaining ground. Nickel-metal hydride
Lithium-ion | Lithium-ion | the lithium-ion battery, the energy density is lower and the self-discharge rate is higher. NiMH cells are assembled into storage systems for higher voltage applications, such as in electric cars.
De batterij-technologie die het meest wordt toegepast is lithium-ion. Deze technologie kan worden toegepast in tal van soorten en maten, zoals in een mobiele telefoon of lap top computer. Deze flexibiliteit gaat gepaard met een licht gewicht ten opzichte van op vloeistof gebaseerde batterijtechnologieën zoals lood-zuur. | The most commonly used battery technology is lithium-ion. This technology can be applied in a variety of types and sizes, such as in a mobile phone or laptop computer. This flexibility is accompanied by a light weight compared to liquid-based battery technologies like lead-acid. | lithium-ion battery, the energy density is lower and the self-discharge rate is higher. NiMH cells are assembled into storage systems for higher voltage applications, such as in electric cars. Lithium-ion
Lood-zuur | Lead-acid | a variety of types and sizes, such as in a mobile phone or laptop computer. This flexibility is accompanied by a light weight compared to liquid-based battery technologies like lead-acid.
Lood-zuur is de oudste en meest volwassen technologie. Vanwege de ruime ervaring in de autotechniek werden de eerste noodstroomvoorzieningen in de energietechniek met deze accu's uitgerust. Deze batterijsystemen worden nog steeds gebruikt voor back-up energiebronnen in grote centrales voor het uitvoeren van een 'black start' na noodsituaties. | Lead-acid is the oldest and most mature technology. Due to extensive experience in automotive engineering, the first emergency power supplies in energy technology were equipped with these batteries. These battery systems are still used for backup power sources in large power plants to perform a 'black start' after emergencies. | variety of types and sizes, such as in a mobile phone or laptop computer. This flexibility is accompanied by a light weight compared to liquid-based battery technologies like lead-acid. Lead-acid
Tabel 15.3 Elektrochemische technologieën voor opslagsystemen | Table 15.3 Electrochemical Technologies for Storage Systems | supplies in energy technology were equipped with these batteries. These battery systems are still used for backup power sources in large power plants to perform a 'black start' after emergencies.
Technologie | Technologie | these batteries. These battery systems are still used for backup power sources in large power plants to perform a 'black start' after emergencies. Table 15.3 Electrochemical Technologies for Storage Systems
Vermogen | Vermogen | batteries. These battery systems are still used for backup power sources in large power plants to perform a 'black start' after emergencies. Table 15.3 Electrochemical Technologies for Storage Systems Technologie
Capaciteit | Capaciteit | These battery systems are still used for backup power sources in large power plants to perform a 'black start' after emergencies. Table 15.3 Electrochemical Technologies for Storage Systems Technologie Vermogen
Rendement | Rendement | battery systems are still used for backup power sources in large power plants to perform a 'black start' after emergencies. Table 15.3 Electrochemical Technologies for Storage Systems Technologie Vermogen Capaciteit
Levensduur | Levensduur | systems are still used for backup power sources in large power plants to perform a 'black start' after emergencies. Table 15.3 Electrochemical Technologies for Storage Systems Technologie Vermogen Capaciteit Rendement
Zelfontlading | Zelfontlading | are still used for backup power sources in large power plants to perform a 'black start' after emergencies. Table 15.3 Electrochemical Technologies for Storage Systems Technologie Vermogen Capaciteit Rendement Levensduur
Kosten | Kosten | still used for backup power sources in large power plants to perform a 'black start' after emergencies. Table 15.3 Electrochemical Technologies for Storage Systems Technologie Vermogen Capaciteit Rendement Levensduur Zelfontlading
Lood-zwavelzuur | Lead-acid | used for backup power sources in large power plants to perform a 'black start' after emergencies. Table 15.3 Electrochemical Technologies for Storage Systems Technologie Vermogen Capaciteit Rendement Levensduur Zelfontlading Kosten
tot 20 MW | up to 20 MW | for backup power sources in large power plants to perform a 'black start' after emergencies. Table 15.3 Electrochemical Technologies for Storage Systems Technologie Vermogen Capaciteit Rendement Levensduur Zelfontlading Kosten Lead-acid
tot 40 MWh | up to 40 MWh | in large power plants to perform a 'black start' after emergencies. Table 15.3 Electrochemical Technologies for Storage Systems Technologie Vermogen Capaciteit Rendement Levensduur Zelfontlading Kosten Lead-acid up to 20 MW
75 - 80 % | 75 - 80% | to perform a 'black start' after emergencies. Table 15.3 Electrochemical Technologies for Storage Systems Technologie Vermogen Capaciteit Rendement Levensduur Zelfontlading Kosten Lead-acid up to 20 MW up to 40 MWh
200 - 1200 cycli | 200 - 1200 cycles | 'black start' after emergencies. Table 15.3 Electrochemical Technologies for Storage Systems Technologie Vermogen Capaciteit Rendement Levensduur Zelfontlading Kosten Lead-acid up to 20 MW up to 40 MWh 75 - 80%
2 - 5 % per maand | 2 - 5% per month | Table 15.3 Electrochemical Technologies for Storage Systems Technologie Vermogen Capaciteit Rendement Levensduur Zelfontlading Kosten Lead-acid up to 20 MW up to 40 MWh 75 - 80% 200 - 1200 cycles
200 - 900 EUR/kWh, | 200 - 900 EUR/kWh, | Storage Systems Technologie Vermogen Capaciteit Rendement Levensduur Zelfontlading Kosten Lead-acid up to 20 MW up to 40 MWh 75 - 80% 200 - 1200 cycles 2 - 5% per month
40 - 450 EUR/kW | 40 - 450 EUR/kW | Capaciteit Rendement Levensduur Zelfontlading Kosten Lead-acid up to 20 MW up to 40 MWh 75 - 80% 200 - 1200 cycles 2 - 5% per month 200 - 900 EUR/kWh,
Nikkel-Cadmium | Nickel-Cadmium | Kosten Lead-acid up to 20 MW up to 40 MWh 75 - 80% 200 - 1200 cycles 2 - 5% per month 200 - 900 EUR/kWh, 40 - 450 EUR/kW
tot 30 MW | up to 30 MW | Lead-acid up to 20 MW up to 40 MWh 75 - 80% 200 - 1200 cycles 2 - 5% per month 200 - 900 EUR/kWh, 40 - 450 EUR/kW Nickel-Cadmium
tot 40 MWh | up to 40 MWh | MW up to 40 MWh 75 - 80% 200 - 1200 cycles 2 - 5% per month 200 - 900 EUR/kWh, 40 - 450 EUR/kW Nickel-Cadmium up to 30 MW
60 - 70 % | 60 - 70% | MWh 75 - 80% 200 - 1200 cycles 2 - 5% per month 200 - 900 EUR/kWh, 40 - 450 EUR/kW Nickel-Cadmium up to 30 MW up to 40 MWh
1000 - 3000 cycli | 1000 - 3000 cycles | 80% 200 - 1200 cycles 2 - 5% per month 200 - 900 EUR/kWh, 40 - 450 EUR/kW Nickel-Cadmium up to 30 MW up to 40 MWh 60 - 70%
5 - 20 % per jaar | 5 - 20% per year | cycles 2 - 5% per month 200 - 900 EUR/kWh, 40 - 450 EUR/kW Nickel-Cadmium up to 30 MW up to 40 MWh 60 - 70% 1000 - 3000 cycles
600 - 1500 EUR/kW | 600 - 1500 EUR/kW | month 200 - 900 EUR/kWh, 40 - 450 EUR/kW Nickel-Cadmium up to 30 MW up to 40 MWh 60 - 70% 1000 - 3000 cycles 5 - 20% per year
Natrium-zwavel | Sodium-sulfur | EUR/kWh, 40 - 450 EUR/kW Nickel-Cadmium up to 30 MW up to 40 MWh 60 - 70% 1000 - 3000 cycles 5 - 20% per year 600 - 1500 EUR/kW
0,1 - 50 MW | 0.1 - 50 MW | 40 - 450 EUR/kW Nickel-Cadmium up to 30 MW up to 40 MWh 60 - 70% 1000 - 3000 cycles 5 - 20% per year 600 - 1500 EUR/kW Sodium-sulfur
tot 400 MWh | up to 400 MWh | Nickel-Cadmium up to 30 MW up to 40 MWh 60 - 70% 1000 - 3000 cycles 5 - 20% per year 600 - 1500 EUR/kW Sodium-sulfur 0.1 - 50 MW
85 - 90 % | 85 - 90% | MW up to 40 MWh 60 - 70% 1000 - 3000 cycles 5 - 20% per year 600 - 1500 EUR/kW Sodium-sulfur 0.1 - 50 MW up to 400 MWh
1000 - 4000 cycli | 1000 - 4000 cycles | 40 MWh 60 - 70% 1000 - 3000 cycles 5 - 20% per year 600 - 1500 EUR/kW Sodium-sulfur 0.1 - 50 MW up to 400 MWh 85 - 90%
200 - 350 EUR/kWh, | 200 - 350 EUR/kWh, | 70% 1000 - 3000 cycles 5 - 20% per year 600 - 1500 EUR/kW Sodium-sulfur 0.1 - 50 MW up to 400 MWh 85 - 90% 1000 - 4000 cycles
250 EUR/kW | 250 EUR/kW | cycles 5 - 20% per year 600 - 1500 EUR/kW Sodium-sulfur 0.1 - 50 MW up to 400 MWh 85 - 90% 1000 - 4000 cycles 200 - 350 EUR/kWh,
Lithium | Lithium | - 20% per year 600 - 1500 EUR/kW Sodium-sulfur 0.1 - 50 MW up to 400 MWh 85 - 90% 1000 - 4000 cycles 200 - 350 EUR/kWh, 250 EUR/kW
tot 2 MW | up to 2 MW | 20% per year 600 - 1500 EUR/kW Sodium-sulfur 0.1 - 50 MW up to 400 MWh 85 - 90% 1000 - 4000 cycles 200 - 350 EUR/kWh, 250 EUR/kW Lithium
tot 15 kWh | up to 15 kWh | - 1500 EUR/kW Sodium-sulfur 0.1 - 50 MW up to 400 MWh 85 - 90% 1000 - 4000 cycles 200 - 350 EUR/kWh, 250 EUR/kW Lithium up to 2 MW
95 % | 95% | 0.1 - 50 MW up to 400 MWh 85 - 90% 1000 - 4000 cycles 200 - 350 EUR/kWh, 250 EUR/kW Lithium up to 2 MW up to 15 kWh
3000 - 5000 cycli | 3000 - 5000 cycles | - 50 MW up to 400 MWh 85 - 90% 1000 - 4000 cycles 200 - 350 EUR/kWh, 250 EUR/kW Lithium up to 2 MW up to 15 kWh 95%
500 - 2500 EUR/kWh | 500 - 2500 EUR/kWh | to 400 MWh 85 - 90% 1000 - 4000 cycles 200 - 350 EUR/kWh, 250 EUR/kW Lithium up to 2 MW up to 15 kWh 95% 3000 - 5000 cycles
Redox Flow | Redox Flow | - 90% 1000 - 4000 cycles 200 - 350 EUR/kWh, 250 EUR/kW Lithium up to 2 MW up to 15 kWh 95% 3000 - 5000 cycles 500 - 2500 EUR/kWh
tot 12 MW | up to 12 MW | 1000 - 4000 cycles 200 - 350 EUR/kWh, 250 EUR/kW Lithium up to 2 MW up to 15 kWh 95% 3000 - 5000 cycles 500 - 2500 EUR/kWh Redox Flow
tot 40 MWh | up to 40 MWh | 200 - 350 EUR/kWh, 250 EUR/kW Lithium up to 2 MW up to 15 kWh 95% 3000 - 5000 cycles 500 - 2500 EUR/kWh Redox Flow up to 12 MW
65 - 75 % | 65 - 75% | 250 EUR/kW Lithium up to 2 MW up to 15 kWh 95% 3000 - 5000 cycles 500 - 2500 EUR/kWh Redox Flow up to 12 MW up to 40 MWh
1000 cycli | 1000 cycles | up to 2 MW up to 15 kWh 95% 3000 - 5000 cycles 500 - 2500 EUR/kWh Redox Flow up to 12 MW up to 40 MWh 65 - 75%
nihil | nihil | 2 MW up to 15 kWh 95% 3000 - 5000 cycles 500 - 2500 EUR/kWh Redox Flow up to 12 MW up to 40 MWh 65 - 75% 1000 cycles
500 - 1000 EUR/kWh, | 500 - 1000 EUR/kWh, | MW up to 15 kWh 95% 3000 - 5000 cycles 500 - 2500 EUR/kWh Redox Flow up to 12 MW up to 40 MWh 65 - 75% 1000 cycles nihil
500 EUR/kW | 500 EUR/kW | kWh 95% 3000 - 5000 cycles 500 - 2500 EUR/kWh Redox Flow up to 12 MW up to 40 MWh 65 - 75% 1000 cycles nihil 500 - 1000 EUR/kWh,
Tabel 15.3 geeft een samenvatting van een aantal kenmerken van elektrochemische technologieën voor enkele opslagsystemen. De ontwikkelingen van nieuwe technieken gaan snel, zodat de informatie in de tabel snel verouderd zal zijn. Figuur 15.10 geeft een overzicht van de omvang van diverse soorten opslagsystemen. Op de horizontale as is de energie-inhoud per gewichtseenheid uitgezet, in Wh per kilogram. Op de verticale as is het vermogen per gewichtseenheid uitgezet, in W per kilogram (Battery, 2011). In de figuur is goed te zien dat de nieuwe technologieën een veel hogere capaciteit en vermogen per gewichtseenheid hebben dan de oude. Oudere typen, gebaseerd op lood-zwavelzuur, hebben een lage capaciteit en vermogen per gewichtseenheid. Dit betekent dat deze accusystemen vaak groot en zwaar zijn. Dit in tegenstelling tot moderne opslagsystemen, die voor dezelfde capaciteit veel kleiner en lichter zijn. | Table 15.3 provides a summary of several characteristics of electrochemical technologies for some storage systems. The development of new techniques is progressing rapidly, so the information in the table will quickly become outdated. Figure 15.10 provides an overview of the scale of various types of storage systems. On the horizontal axis, the energy content per unit of weight is plotted, in Wh per kilogram. On the vertical axis, the power per unit of weight is plotted, in W per kilogram (Battery, 2011). The figure clearly shows that new technologies have a much higher capacity and power per unit of weight than the old ones. Older types, based on lead-acid, have a low capacity and power per unit of weight. This means that these battery systems are often large and heavy. This is in contrast to modern storage systems, which are much smaller and lighter for the same capacity. | 3000 - 5000 cycles 500 - 2500 EUR/kWh Redox Flow up to 12 MW up to 40 MWh 65 - 75% 1000 cycles nihil 500 - 1000 EUR/kWh, 500 EUR/kW
Figuur 15.10 Specifieke energie en vermogen van elektrochemische opslagsystemen | Figure 15.10 Specific energy and power of electrochemical storage systems | weight. This means that these battery systems are often large and heavy. This is in contrast to modern storage systems, which are much smaller and lighter for the same capacity.
Momenteel zijn de op een vaste plaats gestationeerde batterijsystemen nog vaak gebaseerd op lood-zuuraccu's, omdat afmeting en gewicht niet zo doorslaggevend zijn als bij mobiele toepassingen. Ook het beperkte aantal op- en ontlaadcycli (zie tabel 15.3) hoeft niet bezwaarlijk te zijn als deze systemen niet geheel ontladen worden en 'minder diepe' laad- en ontlaadcycli hebben. NiCd batterijen worden gebruikt indien het opslagsysteem wel regelmatig geheel ontladen wordt. Deze batterijen kunnen beter tegen hoge en lage temperaturen dan lood-zuuraccu's. NiCd batterijsystemen zijn echter nog een factor 4 duurder dan lood-zuuraccusystemen. De nieuwste ontwikkelingen voor gebruik in het elektriciteitsnet zijn gebaseerd op NiMH en Li-ion batterijsystemen. Deze systemen hebben een groot temperatuurbereik en de mogelijkheid om 'diep' te ontladen en om snel op te laden. Opslagsystemen, gebaseerd op deze technieken, hebben een lange levensduur. Door hun geringe gewicht zijn deze opslagsystemen ook geschikt voor mobiele uitvoering, zoals voor noodvoorzieningen. Zolang de nieuwe batterijsystemen nog vrij duur zijn, zal op grote schaal nog gebruik gemaakt worden van lood-zuuraccu's. | Currently, stationary battery systems are often still based on lead-acid batteries because size and weight are not as critical as in mobile applications. The limited number of charge and discharge cycles (see Table 15.3) also does not need to be a drawback if these systems are not fully discharged and have 'shallower' charge and discharge cycles. NiCd batteries are used if the storage system is regularly fully discharged. These batteries can withstand high and low temperatures better than lead-acid batteries. However, NiCd battery systems are still about four times more expensive than lead-acid battery systems. The latest developments for use in the power grid are based on NiMH and Li-ion battery systems. These systems have a wide temperature range and the ability to be 'deeply' discharged and quickly recharged. Storage systems based on these technologies have a long lifespan. Due to their light weight, these storage systems are also suitable for mobile applications, such as emergency power supplies. As long as the new battery systems remain relatively expensive, lead-acid batteries will still be used on a large scale. | and heavy. This is in contrast to modern storage systems, which are much smaller and lighter for the same capacity. Figure 15.10 Specific energy and power of electrochemical storage systems
15.5 Toepassingen | 15.5 Applications | also suitable for mobile applications, such as emergency power supplies. As long as the new battery systems remain relatively expensive, lead-acid batteries will still be used on a large scale.
In | In | for mobile applications, such as emergency power supplies. As long as the new battery systems remain relatively expensive, lead-acid batteries will still be used on a large scale. 15.5 Applications
paragraaf 15.1 | paragraph 15.1 | mobile applications, such as emergency power supplies. As long as the new battery systems remain relatively expensive, lead-acid batteries will still be used on a large scale. 15.5 Applications In
is aangetoond dat een intelligent net het tweerichtingsverkeer van het elektrische vermogen toelaat en daarmee de verduurzaming van de energievoorziening ondersteunt. Het intelligente net is op meer plaatsen dan een traditioneel net bemeten en kan bovendien op afstand automatisch bestuurd worden. Door de toevoeging van moderne ICT-technologie en vermogenselektrotechnische oplossingen kan het intelligente net de energiestromen controleren, sturen en beheren. Om een intelligent net te kunnen realiseren is een aantal technische toepassingen in ontwikkeling, waarbij enkele al zijn gerealiseerd: | It has been demonstrated that a smart grid allows for the bidirectional flow of electrical power and thereby supports the sustainability of the energy supply. The smart grid is metered at more locations than a traditional grid and can also be automatically controlled remotely. By incorporating modern ICT technology and power electronics solutions, the smart grid can monitor, direct, and manage energy flows. To realize a smart grid, several technical applications are in development, with some already implemented: | such as emergency power supplies. As long as the new battery systems remain relatively expensive, lead-acid batteries will still be used on a large scale. 15.5 Applications In paragraph 15.1
Bewaking van de spanningshuishouding (handhaven van de Power Quality) | Monitoring of voltage management (maintaining Power Quality) | technology and power electronics solutions, the smart grid can monitor, direct, and manage energy flows. To realize a smart grid, several technical applications are in development, with some already implemented:
Signaleren knelpunten | Identifying bottlenecks | grid can monitor, direct, and manage energy flows. To realize a smart grid, several technical applications are in development, with some already implemented: Monitoring of voltage management (maintaining Power Quality)
Conditiebewaking netcomponenten | Condition monitoring of grid components | monitor, direct, and manage energy flows. To realize a smart grid, several technical applications are in development, with some already implemented: Monitoring of voltage management (maintaining Power Quality) Identifying bottlenecks
Foutplaatslokalisatie | Foutplaatslokalisatie | flows. To realize a smart grid, several technical applications are in development, with some already implemented: Monitoring of voltage management (maintaining Power Quality) Identifying bottlenecks Condition monitoring of grid components
Automatisch netherstel | Automatic grid restoration | To realize a smart grid, several technical applications are in development, with some already implemented: Monitoring of voltage management (maintaining Power Quality) Identifying bottlenecks Condition monitoring of grid components Foutplaatslokalisatie
Optimalisering van onderhoud en investeringen | Optimization of maintenance and investments | smart grid, several technical applications are in development, with some already implemented: Monitoring of voltage management (maintaining Power Quality) Identifying bottlenecks Condition monitoring of grid components Foutplaatslokalisatie Automatic grid restoration
Belastingsturing en sturing van de beïnvloedbare opwekking | Load control and control of controllable generation | are in development, with some already implemented: Monitoring of voltage management (maintaining Power Quality) Identifying bottlenecks Condition monitoring of grid components Foutplaatslokalisatie Automatic grid restoration Optimization of maintenance and investments
Opladen van elektrische auto's (smart charging) | Charging of electric cars (smart charging) | Monitoring of voltage management (maintaining Power Quality) Identifying bottlenecks Condition monitoring of grid components Foutplaatslokalisatie Automatic grid restoration Optimization of maintenance and investments Load control and control of controllable generation
Op afstand uitleesbare elektriciteitsmeters | Remotely readable electricity meters | Quality) Identifying bottlenecks Condition monitoring of grid components Foutplaatslokalisatie Automatic grid restoration Optimization of maintenance and investments Load control and control of controllable generation Charging of electric cars (smart charging)
Fraudebestrijding | Fraudebestrijding | monitoring of grid components Foutplaatslokalisatie Automatic grid restoration Optimization of maintenance and investments Load control and control of controllable generation Charging of electric cars (smart charging) Remotely readable electricity meters
Minimaliseren netverlies | Minimizing grid loss | of grid components Foutplaatslokalisatie Automatic grid restoration Optimization of maintenance and investments Load control and control of controllable generation Charging of electric cars (smart charging) Remotely readable electricity meters Fraudebestrijding
Tariefdifferentiatie | Tariefdifferentiatie | Foutplaatslokalisatie Automatic grid restoration Optimization of maintenance and investments Load control and control of controllable generation Charging of electric cars (smart charging) Remotely readable electricity meters Fraudebestrijding Minimizing grid loss
Aan- en afschakelen op afstand | Remote switching on and off | Automatic grid restoration Optimization of maintenance and investments Load control and control of controllable generation Charging of electric cars (smart charging) Remotely readable electricity meters Fraudebestrijding Minimizing grid loss Tariefdifferentiatie
Power Quality monitoring | Power Quality monitoring | maintenance and investments Load control and control of controllable generation Charging of electric cars (smart charging) Remotely readable electricity meters Fraudebestrijding Minimizing grid loss Tariefdifferentiatie Remote switching on and off
Faciliteren VPP | Facilitating VPP | Load control and control of controllable generation Charging of electric cars (smart charging) Remotely readable electricity meters Fraudebestrijding Minimizing grid loss Tariefdifferentiatie Remote switching on and off Power Quality monitoring
Het bestaande net wordt niet in een simpele handomdraai omgezet in een intelligent net. Het net wordt met graduele toevoegingen van nieuwe technische functionaliteiten stapsgewijs en proefondervindelijk steeds intelligenter gemaakt. In een enkel geval wordt een bestaand net door een omvangrijke projectmatige aanpak op substantiële wijze flexibel en intelligent gemaakt. De basis om te komen tot meer flexibiliteit en intelligentie is een uitgebreid en betrouwbaar meetnetwerk en een systeem om deze metingen efficiënt te verwerken. Vervolgens moet duidelijk zijn wat er met de metingen wordt gedaan: welke meetresultaten worden bewaard en welke metingen zijn alleen beschikbaar voor het verkrijgen van inzicht? Alle opgeslagen gegevens moeten eenvoudig en snel kunnen worden opgevraagd en bewerkt. Dit bevordert het gebruik in de praktijk. Planners, netontwerpers en bedrijfsvoerders zijn met de vele nieuwe gegevens in staat de doelstellingen voor het intelligente net te verwezenlijken. Hieronder worden kort drie concepten genoemd die in 2011 in enkele projecten worden toegepast. | The existing grid is not transformed into an intelligent grid with a simple flick of a switch. The grid is gradually and experimentally made more intelligent through the incremental addition of new technical functionalities. In some cases, an existing grid is made substantially flexible and intelligent through a comprehensive project-based approach. The foundation for achieving more flexibility and intelligence is an extensive and reliable measurement network and a system to efficiently process these measurements. It must then be clear what is done with the measurements: which measurement results are stored and which measurements are only available for gaining insights? All stored data must be easily and quickly retrievable and editable. This promotes practical use. Planners, grid designers, and operators are able to achieve the objectives for the intelligent grid with the many new data points. Below, three concepts that were applied in several projects in 2011 are briefly mentioned. | and control of controllable generation Charging of electric cars (smart charging) Remotely readable electricity meters Fraudebestrijding Minimizing grid loss Tariefdifferentiatie Remote switching on and off Power Quality monitoring Facilitating VPP
15.5.1 Het Mobile Smart Grid concept | 15.5.1 The Mobile Smart Grid concept | are able to achieve the objectives for the intelligent grid with the many new data points. Below, three concepts that were applied in several projects in 2011 are briefly mentioned.
Voor het optimaal inpassen van elektrische auto's in de bestaande MS- en LS-elektriciteitsinfrastructuur wordt het Mobile Smart Grid concept ontwikkeld (Veldman, 2011). In dit concept wordt een besturingslaag ontwikkeld om zo goed mogelijk gebruik te kunnen maken van de capaciteit in het distributienet voor het grootschalig aansluiten van elektrische auto's en duurzame bronnen. In veel MS- en LS-distributienetten is een aanzienlijke hoeveelheid capaciteit aan reserve beschikbaar voor het geval dat het net voor herstel na een storing wordt omgeschakeld. In de perioden dat het net niet hoeft te worden omgeschakeld maakt het Mobile Smart Grid concept gebruik van deze reservecapaciteit voor het opladen van elektrische auto's. Door het opladen van de elektrische auto's te regelen kan de totale belasting worden geoptimaliseerd en wordt de transportcapaciteit van het distributienet beter benut. De werking berust op de planning van de bestuurder. | To optimally integrate electric cars into the existing medium-voltage (MV) and low-voltage (LV) electricity infrastructure, the Mobile Smart Grid concept is being developed (Veldman, 2011). In this concept, a control layer is developed to make the best possible use of the capacity in the distribution network for the large-scale connection of electric cars and renewable sources. In many MV and LV distribution networks, a significant amount of reserve capacity is available in case the network needs to be switched for recovery after a failure. During periods when the network does not need to be switched, the Mobile Smart Grid concept uses this reserve capacity for charging electric cars. By regulating the charging of electric cars, the total load can be optimized, and the transport capacity of the distribution network can be better utilized. The operation relies on the planning of the driver. | for the intelligent grid with the many new data points. Below, three concepts that were applied in several projects in 2011 are briefly mentioned. 15.5.1 The Mobile Smart Grid concept
De bestuurder geeft van te voren via een website op hoever hij moet rijden en wanneer. Deze gegevens worden vervolgens gekoppeld aan de lader in de auto. In het concept wordt op basis van het gemeten en voorspelde gedrag van flexibele belastingen een schema voor het opladen van elektrische auto's opgesteld, rekening houdend met de wensen van de klant, de capaciteit van het distributienet en de actuele en geplande beschikbaarheid van decentraal opgewekte energie. | The driver specifies in advance via a website how far he needs to drive and when. This information is then linked to the charger in the car. In the concept, a schedule for charging electric cars is created based on the measured and predicted behavior of flexible loads, taking into account the customer's preferences, the capacity of the distribution network, and the current and planned availability of decentralized generated energy. | of electric cars, the total load can be optimized, and the transport capacity of the distribution network can be better utilized. The operation relies on the planning of the driver.
De communicatie-infrastructuur voor de benodigde gegevensstromen wordt onder andere geleverd door het internet. Het oplaadproces wordt hierbij, binnen het oplaadschema, zoveel mogelijk aangepast aan de fluctuerende beschikbaarheid van de duurzaam opgewekte energie. In een noodgeval, bijvoorbeeld door een storing in het distributienet, kan het oplaadproces worden uitgesteld. Op deze manier kan gebruik gemaakt worden van de reservecapaciteit in het net, terwijl toch de storingsreserve volledig ter beschikking blijft staan. | The communication infrastructure for the necessary data streams is provided, among other things, by the internet. The charging process is, within the charging schedule, adjusted as much as possible to the fluctuating availability of sustainably generated energy. In an emergency, for example, due to a failure in the distribution network, the charging process can be postponed. This way, the reserve capacity in the network can be utilized, while the fault reserve remains fully available. | the measured and predicted behavior of flexible loads, taking into account the customer's preferences, the capacity of the distribution network, and the current and planned availability of decentralized generated energy.
15.5.2 Opslag van elektrische energie | 15.5.2 Storage of electrical energy | a failure in the distribution network, the charging process can be postponed. This way, the reserve capacity in the network can be utilized, while the fault reserve remains fully available.
Op diverse plaatsen worden proeven gedaan met opslag van elektrische energie in de LS-netten. Hierbij wordt de vermogensbalans automatisch bewaakt. In een demonstratieproject is in een vakantiepark een systeem op basis van lood-zwavelaccu's operationeel, in combinatie met PV-panelen op de daken van de vakantiehuisjes. De overdag opgewekte elektriciteit wordt opgeslagen en kan in de nacht worden gebruikt. Het systeem probeert de energie-uitwisseling met het net zo laag mogelijk te houden. Een ander project voor energieopslag, ook op basis van lood-zwavelaccu's, maakt deel uit van een woningbouwproject. Ook zijn er projecten waar een accusysteem op basis van Li-ion-accu's wordt gebruikt (CE, 2010). Het doel van deze projecten is aantonen dat opslagsystemen kunnen bijdragen aan het reduceren van de nu optredende pieken en dalen in het energietransport en dat het werkingsprincipe juist is. Tevens wordt onderzocht hoe deze systemen zo compact mogelijk gebouwd kunnen worden. | In various locations, experiments are being conducted with the storage of electrical energy in low-voltage networks. The power balance is automatically monitored in these experiments. In a demonstration project at a vacation park, a system based on lead-sulfur batteries is operational, in combination with PV panels on the roofs of the vacation homes. The electricity generated during the day is stored and can be used at night. The system aims to keep energy exchange with the grid as low as possible. Another energy storage project, also based on lead-sulfur batteries, is part of a housing project. There are also projects where a battery system based on Li-ion batteries is used (CE, 2010). The goal of these projects is to demonstrate that storage systems can help reduce the current peaks and troughs in energy transport and that the operating principle is correct. Additionally, research is being conducted on how to build these systems as compactly as possible. | network, the charging process can be postponed. This way, the reserve capacity in the network can be utilized, while the fault reserve remains fully available. 15.5.2 Storage of electrical energy
Figuur 15.11 toont de functionele opbouw van een netstation met een opslagsysteem. De opzet is zodanig dat het LS-net zowel in gekoppeld bedrijf als in eilandbedrijf kan functioneren en automatisch tussen deze toestanden kan omschakelen. De inverter werkt twee kanten op en kan het opslagsysteem opladen en ontladen. De inverter wordt aangestuurd door het Smart Storage systeem. Bij uitval van het MS-net moet het netstation worden vrijgeschakeld indien het tot eilandbedrijf overgaat. Dit omdat anders de spanning aan de MS-zijde van de transformator blijft bestaan. | Figure 15.11 shows the functional layout of a substation with a storage system. The setup is such that the low-voltage (LV) network can operate both in grid-connected mode and in island mode, and can automatically switch between these states. The inverter operates bidirectionally and can charge and discharge the storage system. The inverter is controlled by the Smart Storage system. In the event of a medium-voltage (MV) network outage, the substation must be disconnected if it switches to island mode. This is because otherwise, the voltage on the MV side of the transformer would remain. | the current peaks and troughs in energy transport and that the operating principle is correct. Additionally, research is being conducted on how to build these systems as compactly as possible.
Figuur 15.11 Functioneel schema van een netstation met opslag | Figure 15.11 Functional diagram of a substation with storage | medium-voltage (MV) network outage, the substation must be disconnected if it switches to island mode. This is because otherwise, the voltage on the MV side of the transformer would remain.
15.5.3 Intelligent distributiestation | 15.5.3 Intelligent distribution substation | if it switches to island mode. This is because otherwise, the voltage on the MV side of the transformer would remain. Figure 15.11 Functional diagram of a substation with storage
Een intelligent distributiestation (IntDS) is een concept dat in eerste instantie is opgezet om de mogelijkheden van de combinatie van vermogenselektronica en opslagsystemen bij het handhaven of verbeteren van de Power Quality in een LS-net te onderzoeken. De doelen van het IntDS zijn: | An intelligent distribution substation (IntDS) is a concept initially set up to explore the possibilities of combining power electronics and storage systems to maintain or improve Power Quality in a low-voltage network. The goals of the IntDS are: | island mode. This is because otherwise, the voltage on the MV side of the transformer would remain. Figure 15.11 Functional diagram of a substation with storage 15.5.3 Intelligent distribution substation
beperken van langzame spanningsvariaties | limiting slow voltage variations | initially set up to explore the possibilities of combining power electronics and storage systems to maintain or improve Power Quality in a low-voltage network. The goals of the IntDS are:
reduceren van harmonische vervuiling | reducing harmonic distortion | explore the possibilities of combining power electronics and storage systems to maintain or improve Power Quality in a low-voltage network. The goals of the IntDS are: limiting slow voltage variations
verzamelen van informatie over vermogensstromen in het LS-net met decentrale opwekking. | collecting information about power flows in the low-voltage network with decentralized generation. | of combining power electronics and storage systems to maintain or improve Power Quality in a low-voltage network. The goals of the IntDS are: limiting slow voltage variations reducing harmonic distortion
Het intelligente distributiestation is gebaseerd op een standaard MS/LS-netstation, maar is aangevuld met een op basis van vermogenselektronica regelende nettransformator (SmartTrafo, | The intelligent distribution station is based on a standard medium-voltage/low-voltage (MV/LV) substation, but is supplemented with a power electronics-controlled network transformer (SmartTrafo). | Quality in a low-voltage network. The goals of the IntDS are: limiting slow voltage variations reducing harmonic distortion collecting information about power flows in the low-voltage network with decentralized generation.
paragraaf 4.3 | section 4.3 | flows in the low-voltage network with decentralized generation. The intelligent distribution station is based on a standard medium-voltage/low-voltage (MV/LV) substation, but is supplemented with a power electronics-controlled network transformer (SmartTrafo).
), een via een bidirectionele inverter aangesloten opslagsysteem en een uitgebreid meetsysteem (SASensor, | ), a storage system connected via a bidirectional inverter, and an extensive measurement system (SASensor, | the low-voltage network with decentralized generation. The intelligent distribution station is based on a standard medium-voltage/low-voltage (MV/LV) substation, but is supplemented with a power electronics-controlled network transformer (SmartTrafo). section 4.3
paragraaf 14.2.7 | section 14.2.7 | medium-voltage/low-voltage (MV/LV) substation, but is supplemented with a power electronics-controlled network transformer (SmartTrafo). section 4.3 ), a storage system connected via a bidirectional inverter, and an extensive measurement system (SASensor,
). Figuur 15.12 toont het concept van het intelligente distributiestation, met het voedende MS-net en een aantal uitgaande LS-strengen. Het IntDS is zowel aan MS- als aan LS-zijde voorzien van spanning- en stroommetingen. Aan de LS-zijde is bovendien een power qualitymeting aangebracht. De on-line metingen worden uitgevoerd met het SASensorsysteem. Een aanzienlijk aantal woningen heeft een micro-WKK-installatie. Om het effect van de regelingen te bestuderen zijn sommige woningen voorzien van een power qualitymeting. Het systeem is beschreven in een publicatie (Kester, 2009). | Figure 15.12 shows the concept of the intelligent distribution station, with the feeding medium-voltage (MV) network and several outgoing low-voltage (LV) branches. The IntDS is equipped with voltage and current measurements on both the MV and LV sides. Additionally, a power quality measurement is installed on the LV side. The online measurements are performed using the SASensor system. A significant number of homes have a micro-CHP installation. To study the effect of the regulations, some homes are equipped with a power quality measurement. The system is described in a publication (Kester, 2009). | substation, but is supplemented with a power electronics-controlled network transformer (SmartTrafo). section 4.3 ), a storage system connected via a bidirectional inverter, and an extensive measurement system (SASensor, section 14.2.7
Figuur 15.12 Overzicht van het IntDS concept | Figure 15.12 Overview of the IntDS concept | homes have a micro-CHP installation. To study the effect of the regulations, some homes are equipped with a power quality measurement. The system is described in a publication (Kester, 2009).
Het IntDS heeft een aantal mogelijkheden om de Power Quality in het LS-net te verbeteren, waaronder: spanningsregeling, reductie van harmonische vervuiling, compensatie van spanningsdips en compensatie van flikker. | The IntDS has several capabilities to improve Power Quality in the LV network, including: voltage regulation, reduction of harmonic distortion, compensation for voltage dips, and compensation for flicker. | the effect of the regulations, some homes are equipped with a power quality measurement. The system is described in a publication (Kester, 2009). Figure 15.12 Overview of the IntDS concept
Spanningsregeling | Spanningsregeling | IntDS concept The IntDS has several capabilities to improve Power Quality in the LV network, including: voltage regulation, reduction of harmonic distortion, compensation for voltage dips, and compensation for flicker.
De MS/LS-nettransformator is een SmartTrafo, die met behulp van vermogenselektronica continu regelbaar is. Hiermee wordt een nagenoeg constante spanning op het LS-rek verkregen. De ingestelde waarde wordt zodanig gekozen dat alle aangeslotenen gemiddeld genomen de beste spanning hebben. | The MV/LV network transformer is a SmartTrafo, which is continuously adjustable using power electronics. This ensures an almost constant voltage at the LV rack. The set value is chosen in such a way that all connected users have the best possible voltage on average. | concept The IntDS has several capabilities to improve Power Quality in the LV network, including: voltage regulation, reduction of harmonic distortion, compensation for voltage dips, and compensation for flicker. Spanningsregeling
Reductie van harmonische vervuiling | Reduction of harmonic distortion | This ensures an almost constant voltage at the LV rack. The set value is chosen in such a way that all connected users have the best possible voltage on average.
Harmonische spanningen worden veroorzaakt door de harmonische vervuiling in het voedende MS-net, door de nettransformator en door de harmonische vervuiling van de aangeslotenen in het LS-net. De harmonischen op het LS-rek kunnen op twee manieren worden gereduceerd: | Harmonic voltages are caused by harmonic distortion in the supplying MV network, by the network transformer, and by the harmonic distortion from the connected users in the LV network. The harmonics on the LV rack can be reduced in two ways: | constant voltage at the LV rack. The set value is chosen in such a way that all connected users have the best possible voltage on average. Reduction of harmonic distortion
resistieve harmonische demping door de bidirectionele inverter; de harmonischen worden geabsorbeerd door een virtuele impedantie; de demping werkt tot en met de dertiende harmonische | resistive harmonic damping by the bidirectional inverter; the harmonics are absorbed by a virtual impedance; the damping works up to and including the thirteenth harmonic | network, by the network transformer, and by the harmonic distortion from the connected users in the LV network. The harmonics on the LV rack can be reduced in two ways:
passieve harmonische demping door de condensatoren van de bidirectionele inverter. | passive harmonic damping by the capacitors of the bidirectional inverter. | be reduced in two ways: resistive harmonic damping by the bidirectional inverter; the harmonics are absorbed by a virtual impedance; the damping works up to and including the thirteenth harmonic
Compensatie van spanningsdips | Compensation of voltage dips | bidirectional inverter; the harmonics are absorbed by a virtual impedance; the damping works up to and including the thirteenth harmonic passive harmonic damping by the capacitors of the bidirectional inverter.
De spanningsdips op het LS-rek worden gecompenseerd door de regeling van de SmartTrafo en door de regelende werking van de bidirectionele inverter van het opslagsysteem. | The voltage dips on the low-voltage rack are compensated by the control of the SmartTrafo and by the regulating function of the bidirectional inverter of the storage system. | are absorbed by a virtual impedance; the damping works up to and including the thirteenth harmonic passive harmonic damping by the capacitors of the bidirectional inverter. Compensation of voltage dips
Compensatie van flikker | Compensation of flicker | voltage dips The voltage dips on the low-voltage rack are compensated by the control of the SmartTrafo and by the regulating function of the bidirectional inverter of the storage system.
Ook de flikker van de spanning op het LS-rek wordt gecompenseerd door de regeling van de SmartTrafo en door de regelende werking van de bidirectionele inverter van het opslagsysteem. | The flicker of the voltage on the low-voltage rack is also compensated by the control of the SmartTrafo and by the regulating function of the bidirectional inverter of the storage system. | voltage dips on the low-voltage rack are compensated by the control of the SmartTrafo and by the regulating function of the bidirectional inverter of the storage system. Compensation of flicker
Het concept wordt in een proefproject toegepast op een netstation in een woonwijk, waar in 180 woningen micro-WKK installaties zijn geplaatst. Het systeem is gedurende drie maanden getest (Melnik, 2011). Tijdens de test en de periode daarna is gebleken dat de spanningsregeling de spanningsfluctuaties op het LS-rek en bij de bemeten aangeslotenen aanzienlijk reduceert. De harmonische vervuiling wordt ook aanzienlijk gereduceerd. De spanningsdips kwamen in de testperiode te weinig voor. De flikkercompensatie had een positieve invloed op het niveau en de pieken op het LS-rek. | The concept is being applied in a pilot project at a substation in a residential area, where micro-CHP installations have been placed in 180 homes. The system was tested for three months (Melnik, 2011). During the test and the subsequent period, it was found that the voltage regulation significantly reduces voltage fluctuations on the low-voltage rack and at the measured connections. Harmonic distortion is also significantly reduced. Voltage dips occurred too infrequently during the test period. The flicker compensation had a positive impact on the level and peaks on the low-voltage rack. | flicker of the voltage on the low-voltage rack is also compensated by the control of the SmartTrafo and by the regulating function of the bidirectional inverter of the storage system.