## Sheet1
Original Text | Translated Text | Previous Context
Modellen | Modellen
Hoofdstuk 8 geeft een beschrijving van de meeste modellen van componenten waaruit een elektriciteitsnet is opgebouwd en van apparaten die op een elektriciteitsnet kunnen zijn aangesloten. De modellen worden gebruikt bij het uitvoeren van loadflow- en kortsluitstroomberekeningen. | Chapter 8 provides a description of most models of components that make up an electrical grid and of devices that can be connected to an electrical grid. The models are used for performing load flow and short-circuit current calculations. | Modellen
8 Modellen | 8 Models | components that make up an electrical grid and of devices that can be connected to an electrical grid. The models are used for performing load flow and short-circuit current calculations.
8.1 Het externe net | 8.1 The external grid | make up an electrical grid and of devices that can be connected to an electrical grid. The models are used for performing load flow and short-circuit current calculations. 8 Models
8.2 Kabels | 8.2 Cables | grid and of devices that can be connected to an electrical grid. The models are used for performing load flow and short-circuit current calculations. 8 Models 8.1 The external grid
8.2.1 Normale impedantie | 8.2.1 Normal impedance | of devices that can be connected to an electrical grid. The models are used for performing load flow and short-circuit current calculations. 8 Models 8.1 The external grid 8.2 Cables
8.2.2 Inverse impedantie | 8.2.2 Inverse impedance | can be connected to an electrical grid. The models are used for performing load flow and short-circuit current calculations. 8 Models 8.1 The external grid 8.2 Cables 8.2.1 Normal impedance
8.2.3 Verlies | 8.2.3 Loss | to an electrical grid. The models are used for performing load flow and short-circuit current calculations. 8 Models 8.1 The external grid 8.2 Cables 8.2.1 Normal impedance 8.2.2 Inverse impedance
8.2.4 Maximale stroombelastbaarheid | 8.2.4 Maximum current-carrying capacity | electrical grid. The models are used for performing load flow and short-circuit current calculations. 8 Models 8.1 The external grid 8.2 Cables 8.2.1 Normal impedance 8.2.2 Inverse impedance 8.2.3 Loss
8.2.5 Homopolaire impedantie | 8.2.5 Homopolar impedance | are used for performing load flow and short-circuit current calculations. 8 Models 8.1 The external grid 8.2 Cables 8.2.1 Normal impedance 8.2.2 Inverse impedance 8.2.3 Loss 8.2.4 Maximum current-carrying capacity
8.2.6 Invloed aardelektrode en aarde | 8.2.6 Influence of grounding electrode and earth | performing load flow and short-circuit current calculations. 8 Models 8.1 The external grid 8.2 Cables 8.2.1 Normal impedance 8.2.2 Inverse impedance 8.2.3 Loss 8.2.4 Maximum current-carrying capacity 8.2.5 Homopolar impedance
8.2.7 Meting van de homopolaire impedantie | 8.2.7 Measurement of the homopolar impedance | 8 Models 8.1 The external grid 8.2 Cables 8.2.1 Normal impedance 8.2.2 Inverse impedance 8.2.3 Loss 8.2.4 Maximum current-carrying capacity 8.2.5 Homopolar impedance 8.2.6 Influence of grounding electrode and earth
8.2.8 Uitgebreid model voor de laagspanningskabel | 8.2.8 Extended model for the low-voltage cable | 8.2 Cables 8.2.1 Normal impedance 8.2.2 Inverse impedance 8.2.3 Loss 8.2.4 Maximum current-carrying capacity 8.2.5 Homopolar impedance 8.2.6 Influence of grounding electrode and earth 8.2.7 Measurement of the homopolar impedance
8.3 Transformatoren | 8.3 Transformers | impedance 8.2.3 Loss 8.2.4 Maximum current-carrying capacity 8.2.5 Homopolar impedance 8.2.6 Influence of grounding electrode and earth 8.2.7 Measurement of the homopolar impedance 8.2.8 Extended model for the low-voltage cable
8.3.1 Wikkelconfiguratie | 8.3.1 Winding Configuration | Loss 8.2.4 Maximum current-carrying capacity 8.2.5 Homopolar impedance 8.2.6 Influence of grounding electrode and earth 8.2.7 Measurement of the homopolar impedance 8.2.8 Extended model for the low-voltage cable 8.3 Transformers
8.3.2 Overzetverhouding | 8.3.2 Transformation Ratio | current-carrying capacity 8.2.5 Homopolar impedance 8.2.6 Influence of grounding electrode and earth 8.2.7 Measurement of the homopolar impedance 8.2.8 Extended model for the low-voltage cable 8.3 Transformers 8.3.1 Winding Configuration
8.3.3 Parameters voor transformatoren met twee wikkelingen | 8.3.3 Parameters for transformers with two windings | Homopolar impedance 8.2.6 Influence of grounding electrode and earth 8.2.7 Measurement of the homopolar impedance 8.2.8 Extended model for the low-voltage cable 8.3 Transformers 8.3.1 Winding Configuration 8.3.2 Transformation Ratio
8.3.4 Parameters voor transformatoren met drie wikkelingen | 8.3.4 Parameters for transformers with three windings | and earth 8.2.7 Measurement of the homopolar impedance 8.2.8 Extended model for the low-voltage cable 8.3 Transformers 8.3.1 Winding Configuration 8.3.2 Transformation Ratio 8.3.3 Parameters for transformers with two windings
8.3.5 Inverse impedantie | 8.3.5 Inverse Impedance | impedance 8.2.8 Extended model for the low-voltage cable 8.3 Transformers 8.3.1 Winding Configuration 8.3.2 Transformation Ratio 8.3.3 Parameters for transformers with two windings 8.3.4 Parameters for transformers with three windings
8.3.6 Homopolaire parameters | 8.3.6 Homopolar parameters | model for the low-voltage cable 8.3 Transformers 8.3.1 Winding Configuration 8.3.2 Transformation Ratio 8.3.3 Parameters for transformers with two windings 8.3.4 Parameters for transformers with three windings 8.3.5 Inverse Impedance
8.3.7 Correctie voor kortsluitberekeningen volgens IEC | 8.3.7 Correction for short-circuit calculations according to IEC | low-voltage cable 8.3 Transformers 8.3.1 Winding Configuration 8.3.2 Transformation Ratio 8.3.3 Parameters for transformers with two windings 8.3.4 Parameters for transformers with three windings 8.3.5 Inverse Impedance 8.3.6 Homopolar parameters
8.3.8 Inrushstromen | 8.3.8 Inrush Currents | Transformation Ratio 8.3.3 Parameters for transformers with two windings 8.3.4 Parameters for transformers with three windings 8.3.5 Inverse Impedance 8.3.6 Homopolar parameters 8.3.7 Correction for short-circuit calculations according to IEC
8.4 Aardingstransformator en nulpunttransformator | 8.4 Grounding Transformer and Neutral Point Transformer | Parameters for transformers with two windings 8.3.4 Parameters for transformers with three windings 8.3.5 Inverse Impedance 8.3.6 Homopolar parameters 8.3.7 Correction for short-circuit calculations according to IEC 8.3.8 Inrush Currents
8.5 Smoorspoelen | 8.5 Reactors | Parameters for transformers with three windings 8.3.5 Inverse Impedance 8.3.6 Homopolar parameters 8.3.7 Correction for short-circuit calculations according to IEC 8.3.8 Inrush Currents 8.4 Grounding Transformer and Neutral Point Transformer
8.6 Belasting | 8.6 Load | transformers with three windings 8.3.5 Inverse Impedance 8.3.6 Homopolar parameters 8.3.7 Correction for short-circuit calculations according to IEC 8.3.8 Inrush Currents 8.4 Grounding Transformer and Neutral Point Transformer 8.5 Reactors
8.7 Opwekking | 8.7 Generation | three windings 8.3.5 Inverse Impedance 8.3.6 Homopolar parameters 8.3.7 Correction for short-circuit calculations according to IEC 8.3.8 Inrush Currents 8.4 Grounding Transformer and Neutral Point Transformer 8.5 Reactors 8.6 Load
8.8 Generatoren | 8.8 Generators | 8.3.5 Inverse Impedance 8.3.6 Homopolar parameters 8.3.7 Correction for short-circuit calculations according to IEC 8.3.8 Inrush Currents 8.4 Grounding Transformer and Neutral Point Transformer 8.5 Reactors 8.6 Load 8.7 Generation
8.9 Motoren | 8.9 Motors | Impedance 8.3.6 Homopolar parameters 8.3.7 Correction for short-circuit calculations according to IEC 8.3.8 Inrush Currents 8.4 Grounding Transformer and Neutral Point Transformer 8.5 Reactors 8.6 Load 8.7 Generation 8.8 Generators
8.10 Converters en gelijkrichters | 8.10 Converters and rectifiers | Homopolar parameters 8.3.7 Correction for short-circuit calculations according to IEC 8.3.8 Inrush Currents 8.4 Grounding Transformer and Neutral Point Transformer 8.5 Reactors 8.6 Load 8.7 Generation 8.8 Generators 8.9 Motors
8.11 Windturbinegeneratoren | 8.11 Wind Turbine Generators | for short-circuit calculations according to IEC 8.3.8 Inrush Currents 8.4 Grounding Transformer and Neutral Point Transformer 8.5 Reactors 8.6 Load 8.7 Generation 8.8 Generators 8.9 Motors 8.10 Converters and rectifiers
8 Modellen | 8 Models | to IEC 8.3.8 Inrush Currents 8.4 Grounding Transformer and Neutral Point Transformer 8.5 Reactors 8.6 Load 8.7 Generation 8.8 Generators 8.9 Motors 8.10 Converters and rectifiers 8.11 Wind Turbine Generators
Alle berekeningen aan een elektriciteitsnet maken gebruik van specifieke eigenschappen van de componenten, die zijn vastgelegd in modellen. Een model beschrijft het gedrag van een component voor de gewenste berekeningen. Elke soort berekeningen gebruikt een eigen model voor elk componenttype. Dit hoofdstuk beschrijft de modellen voor: | All calculations on an electrical grid use specific properties of the components, which are defined in models. A model describes the behavior of a component for the desired calculations. Each type of calculation uses its own model for each component type. This chapter describes the models for: | 8.3.8 Inrush Currents 8.4 Grounding Transformer and Neutral Point Transformer 8.5 Reactors 8.6 Load 8.7 Generation 8.8 Generators 8.9 Motors 8.10 Converters and rectifiers 8.11 Wind Turbine Generators 8 Models
extern net | external network | A model describes the behavior of a component for the desired calculations. Each type of calculation uses its own model for each component type. This chapter describes the models for:
kabel | kabel | describes the behavior of a component for the desired calculations. Each type of calculation uses its own model for each component type. This chapter describes the models for: external network
transformator | transformator | the behavior of a component for the desired calculations. Each type of calculation uses its own model for each component type. This chapter describes the models for: external network kabel
belasting | belasting | behavior of a component for the desired calculations. Each type of calculation uses its own model for each component type. This chapter describes the models for: external network kabel transformator
generator | generator | of a component for the desired calculations. Each type of calculation uses its own model for each component type. This chapter describes the models for: external network kabel transformator belasting
motor | motor | a component for the desired calculations. Each type of calculation uses its own model for each component type. This chapter describes the models for: external network kabel transformator belasting generator
8.1 Het externe net | 8.1 The External Network | component for the desired calculations. Each type of calculation uses its own model for each component type. This chapter describes the models for: external network kabel transformator belasting generator motor
Voor de bestudering van een elektriciteitsnet beperkt de expert zich altijd tot het deel dat ontworpen of aangepast moet worden. Dat houdt in dat het netmodel meestal bestaat uit een beperkt gedeelte van het totale net, waarbij het te bestuderen deelnet aangesloten is op een extern net dat de buitenwereld representeert. Het externe net is een vereenvoudiging van alles wat niet gemodelleerd wordt, maar wel van belang is voor de berekening. Dat kan een hoger gelegen stuk distributienet zijn, een middenspanningstransportnet of een hoogspanningsnet. Uitgangspunt hierbij is dat het hoger gelegen voedende net een constant gedrag vertoont in verhouding tot het te bestuderen netdeel. Daarom wordt het vereenvoudigd tot een simpele netvoeding. | For the study of an electrical network, the expert always limits themselves to the part that needs to be designed or modified. This means that the network model usually consists of a limited portion of the total network, with the part to be studied connected to an external network that represents the outside world. The external network is a simplification of everything that is not modeled but is still important for the calculation. This can be a higher-level distribution network, a medium-voltage transmission network, or a high-voltage network. The basic principle here is that the higher-level supplying network exhibits constant behavior in relation to the network segment being studied. Therefore, it is simplified to a basic network supply. | calculations. Each type of calculation uses its own model for each component type. This chapter describes the models for: external network kabel transformator belasting generator motor 8.1 The External Network
Een netvoeding representeert het externe net, waarvoor wordt aangenomen dat de spanning tijdens normaal bedrijf bekend is. Het is niet zo dat de spanning te allen tijde constant is. Indien de spanning over een groot gebied varieert, worden de berekeningen meestal voor de uiterste situaties van maximale en minimale voedingsspanning uitgevoerd. Bij loadflowberekeningen zorgt de netvoeding ervoor dat de spanning op het knooppunt waarop deze is aangesloten constant blijft. Dat wil dus zeggen dat van de spanningsvector de absolute waarde en de hoek vastliggen. | A network supply represents the external grid, for which it is assumed that the voltage during normal operation is known. It is not the case that the voltage is constant at all times. If the voltage varies over a large area, calculations are usually performed for the extreme situations of maximum and minimum supply voltage. In load flow calculations, the network supply ensures that the voltage at the node to which it is connected remains constant. This means that the magnitude and angle of the voltage vector are fixed. | The basic principle here is that the higher-level supplying network exhibits constant behavior in relation to the network segment being studied. Therefore, it is simplified to a basic network supply.
[ | [ | the network supply ensures that the voltage at the node to which it is connected remains constant. This means that the magnitude and angle of the voltage vector are fixed.
8.1 | 8.1 | network supply ensures that the voltage at the node to which it is connected remains constant. This means that the magnitude and angle of the voltage vector are fixed. [
] | ] | supply ensures that the voltage at the node to which it is connected remains constant. This means that the magnitude and angle of the voltage vector are fixed. [ 8.1
waarin: | in which: | ensures that the voltage at the node to which it is connected remains constant. This means that the magnitude and angle of the voltage vector are fixed. [ 8.1 ]
U | U | the voltage at the node to which it is connected remains constant. This means that the magnitude and angle of the voltage vector are fixed. [ 8.1 ] in which:
eff | eff | voltage at the node to which it is connected remains constant. This means that the magnitude and angle of the voltage vector are fixed. [ 8.1 ] in which: U
effectieve waarde van de spanning van de netvoeding | effective value of the mains voltage | at the node to which it is connected remains constant. This means that the magnitude and angle of the voltage vector are fixed. [ 8.1 ] in which: U eff
θ | θ | is connected remains constant. This means that the magnitude and angle of the voltage vector are fixed. [ 8.1 ] in which: U eff effective value of the mains voltage
hoek van de spanningsvector van de netvoeding | angle of the voltage vector of the mains supply | connected remains constant. This means that the magnitude and angle of the voltage vector are fixed. [ 8.1 ] in which: U eff effective value of the mains voltage θ
Tijdens een kortsluiting mag de spanning van de netvoeding niet meer constant verondersteld worden zoals in normale situaties. De netvoeding vertegenwoordigt een stuk elektriciteitsnet en dat heeft een bepaalde impedantie. Deze impedantie is met name zichtbaar in kortsluitsituaties en wordt daarom de kortsluitimpedantie genoemd. Tijdens een kortsluiting in een middenspanningsnet kunnen dusdanig grote stromen gaan lopen dat de spanning op het voedingspunt aanzienlijk daalt. | During a short circuit, the voltage of the mains supply can no longer be assumed to be constant as in normal situations. The mains supply represents a section of the electrical grid and has a certain impedance. This impedance is particularly noticeable in short circuit situations and is therefore called the short circuit impedance. During a short circuit in a medium voltage network, such large currents can flow that the voltage at the supply point drops significantly. | angle of the voltage vector are fixed. [ 8.1 ] in which: U eff effective value of the mains voltage θ angle of the voltage vector of the mains supply
Op een bepaald voedingspunt is de kortsluitimpedantie niet zonder meer bekend. Wel kan het kortsluitvermogen | At a certain supply point, the short circuit impedance is not readily known. However, the short circuit power can | is therefore called the short circuit impedance. During a short circuit in a medium voltage network, such large currents can flow that the voltage at the supply point drops significantly.
S | S | can flow that the voltage at the supply point drops significantly. At a certain supply point, the short circuit impedance is not readily known. However, the short circuit power can
kQ | kQ | flow that the voltage at the supply point drops significantly. At a certain supply point, the short circuit impedance is not readily known. However, the short circuit power can S
" | " | that the voltage at the supply point drops significantly. At a certain supply point, the short circuit impedance is not readily known. However, the short circuit power can S kQ
of de kortsluitstroombijdrage I | or the short circuit current contribution I | the voltage at the supply point drops significantly. At a certain supply point, the short circuit impedance is not readily known. However, the short circuit power can S kQ "
kQ | kQ | significantly. At a certain supply point, the short circuit impedance is not readily known. However, the short circuit power can S kQ " or the short circuit current contribution I
" worden gemeten of berekend. Hieruit wordt de kortsluitimpedantie | "can be measured or calculated. From this, the short circuit impedance" | At a certain supply point, the short circuit impedance is not readily known. However, the short circuit power can S kQ " or the short circuit current contribution I kQ
Z | Z | readily known. However, the short circuit power can S kQ " or the short circuit current contribution I kQ "can be measured or calculated. From this, the short circuit impedance"
Q | Q | known. However, the short circuit power can S kQ " or the short circuit current contribution I kQ "can be measured or calculated. From this, the short circuit impedance" Z
berekend volgens: | calculated according to: | However, the short circuit power can S kQ " or the short circuit current contribution I kQ "can be measured or calculated. From this, the short circuit impedance" Z Q
[ | [ | circuit power can S kQ " or the short circuit current contribution I kQ "can be measured or calculated. From this, the short circuit impedance" Z Q calculated according to:
8.2 | 8.2 | power can S kQ " or the short circuit current contribution I kQ "can be measured or calculated. From this, the short circuit impedance" Z Q calculated according to: [
] | ] | can S kQ " or the short circuit current contribution I kQ "can be measured or calculated. From this, the short circuit impedance" Z Q calculated according to: [ 8.2
Hierin is | Herein is | S kQ " or the short circuit current contribution I kQ "can be measured or calculated. From this, the short circuit impedance" Z Q calculated according to: [ 8.2 ]
U | U | " or the short circuit current contribution I kQ "can be measured or calculated. From this, the short circuit impedance" Z Q calculated according to: [ 8.2 ] Herein is
nQ | nQ | or the short circuit current contribution I kQ "can be measured or calculated. From this, the short circuit impedance" Z Q calculated according to: [ 8.2 ] Herein is U
de nominale gekoppelde spanning van de netvoeding voor de kortsluitsituatie. De factor | the nominal coupled voltage of the power supply for the short circuit situation. The factor | the short circuit current contribution I kQ "can be measured or calculated. From this, the short circuit impedance" Z Q calculated according to: [ 8.2 ] Herein is U nQ
c | c | short circuit impedance" Z Q calculated according to: [ 8.2 ] Herein is U nQ the nominal coupled voltage of the power supply for the short circuit situation. The factor
is een correctiefactor. Deze is geïntroduceerd voor kortsluitberekeningen volgens de internationale norm IEC 60909. Met deze factor wordt een aantal onzekerheden in het externe net verdisconteerd, zoals: | is a correction factor. This has been introduced for short-circuit calculations according to the international standard IEC 60909. This factor accounts for a number of uncertainties in the external network, such as: | circuit impedance" Z Q calculated according to: [ 8.2 ] Herein is U nQ the nominal coupled voltage of the power supply for the short circuit situation. The factor c
willekeurige spanningsvariaties in tijd en plaats | random voltage variations in time and place | correction factor. This has been introduced for short-circuit calculations according to the international standard IEC 60909. This factor accounts for a number of uncertainties in the external network, such as:
veranderende transformatortrapstanden | changing transformer tap positions | short-circuit calculations according to the international standard IEC 60909. This factor accounts for a number of uncertainties in the external network, such as: random voltage variations in time and place
verwaarlozen van belastingen en capaciteiten | neglecting loads and capacities | the international standard IEC 60909. This factor accounts for a number of uncertainties in the external network, such as: random voltage variations in time and place changing transformer tap positions
het subtransiënte gedrag van generatoren en motoren. | the subtransient behavior of generators and motors. | 60909. This factor accounts for a number of uncertainties in the external network, such as: random voltage variations in time and place changing transformer tap positions neglecting loads and capacities
De waarde van de factor | The value of the factor | of uncertainties in the external network, such as: random voltage variations in time and place changing transformer tap positions neglecting loads and capacities the subtransient behavior of generators and motors.
c | c | network, such as: random voltage variations in time and place changing transformer tap positions neglecting loads and capacities the subtransient behavior of generators and motors. The value of the factor
hangt af van de berekening en van het spanningsniveau. Tabel 8.1 geeft een overzicht, zoals gehanteerd in IEC 60909. | depends on the calculation and the voltage level. Table 8.1 provides an overview, as used in IEC 60909. | such as: random voltage variations in time and place changing transformer tap positions neglecting loads and capacities the subtransient behavior of generators and motors. The value of the factor c
Tabel 8.1 Spanningsfactoren volgens IEC 60909 | Table 8.1 Voltage Factors According to IEC 60909 | subtransient behavior of generators and motors. The value of the factor c depends on the calculation and the voltage level. Table 8.1 provides an overview, as used in IEC 60909.
Nominale spanning | Nominal voltage | of the factor c depends on the calculation and the voltage level. Table 8.1 provides an overview, as used in IEC 60909. Table 8.1 Voltage Factors According to IEC 60909
Spanningsfactor | Spanningsfactor | factor c depends on the calculation and the voltage level. Table 8.1 provides an overview, as used in IEC 60909. Table 8.1 Voltage Factors According to IEC 60909 Nominal voltage
c | c | c depends on the calculation and the voltage level. Table 8.1 provides an overview, as used in IEC 60909. Table 8.1 Voltage Factors According to IEC 60909 Nominal voltage Spanningsfactor
voor de berekening van | for the calculation of | depends on the calculation and the voltage level. Table 8.1 provides an overview, as used in IEC 60909. Table 8.1 Voltage Factors According to IEC 60909 Nominal voltage Spanningsfactor c
maximum kortsluitstroom | maximum short-circuit current | and the voltage level. Table 8.1 provides an overview, as used in IEC 60909. Table 8.1 Voltage Factors According to IEC 60909 Nominal voltage Spanningsfactor c for the calculation of
minimum kortsluitstroom | minimum short-circuit current | level. Table 8.1 provides an overview, as used in IEC 60909. Table 8.1 Voltage Factors According to IEC 60909 Nominal voltage Spanningsfactor c for the calculation of maximum short-circuit current
Laagspanningssystemen met: | Low voltage systems with: | provides an overview, as used in IEC 60909. Table 8.1 Voltage Factors According to IEC 60909 Nominal voltage Spanningsfactor c for the calculation of maximum short-circuit current minimum short-circuit current
• een tolerantie van +6% | • a tolerance of +6% | used in IEC 60909. Table 8.1 Voltage Factors According to IEC 60909 Nominal voltage Spanningsfactor c for the calculation of maximum short-circuit current minimum short-circuit current Low voltage systems with:
• een tolerantie van +10% | • a tolerance of +10% | 8.1 Voltage Factors According to IEC 60909 Nominal voltage Spanningsfactor c for the calculation of maximum short-circuit current minimum short-circuit current Low voltage systems with: • a tolerance of +6%
1.05 | 1.05 | IEC 60909 Nominal voltage Spanningsfactor c for the calculation of maximum short-circuit current minimum short-circuit current Low voltage systems with: • a tolerance of +6% • a tolerance of +10%
1.10 | 1.10 | 60909 Nominal voltage Spanningsfactor c for the calculation of maximum short-circuit current minimum short-circuit current Low voltage systems with: • a tolerance of +6% • a tolerance of +10% 1.05
0.95 | 0.95 | Nominal voltage Spanningsfactor c for the calculation of maximum short-circuit current minimum short-circuit current Low voltage systems with: • a tolerance of +6% • a tolerance of +10% 1.05 1.10
0.95 | 0.95 | voltage Spanningsfactor c for the calculation of maximum short-circuit current minimum short-circuit current Low voltage systems with: • a tolerance of +6% • a tolerance of +10% 1.05 1.10 0.95
Middenspanning en hoogspanning | Medium voltage and high voltage | Spanningsfactor c for the calculation of maximum short-circuit current minimum short-circuit current Low voltage systems with: • a tolerance of +6% • a tolerance of +10% 1.05 1.10 0.95 0.95
1.10 | 1.10 | of maximum short-circuit current minimum short-circuit current Low voltage systems with: • a tolerance of +6% • a tolerance of +10% 1.05 1.10 0.95 0.95 Medium voltage and high voltage
1.00 | 1.00 | maximum short-circuit current minimum short-circuit current Low voltage systems with: • a tolerance of +6% • a tolerance of +10% 1.05 1.10 0.95 0.95 Medium voltage and high voltage 1.10
Voor alle andere berekeningen is de factor | For all other calculations, the factor is | short-circuit current minimum short-circuit current Low voltage systems with: • a tolerance of +6% • a tolerance of +10% 1.05 1.10 0.95 0.95 Medium voltage and high voltage 1.10 1.00
c | c | systems with: • a tolerance of +6% • a tolerance of +10% 1.05 1.10 0.95 0.95 Medium voltage and high voltage 1.10 1.00 For all other calculations, the factor is
gelijk aan 1. | equal to 1. | with: • a tolerance of +6% • a tolerance of +10% 1.05 1.10 0.95 0.95 Medium voltage and high voltage 1.10 1.00 For all other calculations, the factor is c
De weerstand en de reactantie van de netvoedingsimpedantie worden berekend uit de R/X-verhouding: | The resistance and reactance of the network supply impedance are calculated from the R/X ratio: | tolerance of +6% • a tolerance of +10% 1.05 1.10 0.95 0.95 Medium voltage and high voltage 1.10 1.00 For all other calculations, the factor is c equal to 1.
[ | [ | high voltage 1.10 1.00 For all other calculations, the factor is c equal to 1. The resistance and reactance of the network supply impedance are calculated from the R/X ratio:
8.3 | 8.3 | voltage 1.10 1.00 For all other calculations, the factor is c equal to 1. The resistance and reactance of the network supply impedance are calculated from the R/X ratio: [
] | ] | 1.10 1.00 For all other calculations, the factor is c equal to 1. The resistance and reactance of the network supply impedance are calculated from the R/X ratio: [ 8.3
Indien de R/X-verhouding niet bekend is, mag volgens IEC 60909 worden aangenomen: | If the R/X ratio is not known, it may be assumed according to IEC 60909: | 1.00 For all other calculations, the factor is c equal to 1. The resistance and reactance of the network supply impedance are calculated from the R/X ratio: [ 8.3 ]
voor spanningsniveaus hoger dan 35 kV: | for voltage levels higher than 35 kV: | reactance of the network supply impedance are calculated from the R/X ratio: [ 8.3 ] If the R/X ratio is not known, it may be assumed according to IEC 60909:
R/X = 0,0 | R/X = 0.0 | calculated from the R/X ratio: [ 8.3 ] If the R/X ratio is not known, it may be assumed according to IEC 60909: for voltage levels higher than 35 kV:
voor spanningsniveaus lager dan of gelijk aan 35 kV: | for voltage levels lower than or equal to 35 kV: | R/X ratio: [ 8.3 ] If the R/X ratio is not known, it may be assumed according to IEC 60909: for voltage levels higher than 35 kV: R/X = 0.0
R/X = 0,1 | R/X = 0.1 | not known, it may be assumed according to IEC 60909: for voltage levels higher than 35 kV: R/X = 0.0 for voltage levels lower than or equal to 35 kV:
In Nederlandse middenspanningsnetten is dichtbij een onderstation een waarde van 0,1 voor de R/X-verhouding redelijk, maar verder in het MS-net wordt deze waarde groter door de R/X-verhouding van de MS-kabels. Voor de voeding van een LS-net wordt in netberekeningen meestal uitgegaan van de voeding aan de MS-zijde van de nettransformator. | In Dutch medium voltage networks, a value of 0.1 for the R/X ratio is reasonable near a substation, but further into the MV network, this value increases due to the R/X ratio of the MV cables. For the supply of an LV network, network calculations usually assume supply from the MV side of the network transformer. | may be assumed according to IEC 60909: for voltage levels higher than 35 kV: R/X = 0.0 for voltage levels lower than or equal to 35 kV: R/X = 0.1
Voor berekeningen aan asymmetrische situaties en voor berekeningen aan situaties waarin contact wordt gemaakt met aarde, zoals een fase-aardsluiting, wordt gebruik gemaakt van de symmetrische componentenmethode (zie hoofdstuk 7). De hiervoor gebruikte impedanties zijn de normale impedantie, die gelijk is aan de kortsluitimpedantie, de inverse impedantie, die gelijk is aan de normale impedantie en de homopolaire impedantie, die wordt uitgedrukt in de verhouding van | For calculations involving asymmetrical situations and situations where contact is made with the ground, such as a phase-to-ground fault, the symmetrical components method is used (see Chapter 7). The impedances used for this are the normal impedance, which is equal to the short-circuit impedance, the inverse impedance, which is equal to the normal impedance, and the homopolar impedance, which is expressed in the ratio of | increases due to the R/X ratio of the MV cables. For the supply of an LV network, network calculations usually assume supply from the MV side of the network transformer.
Z | Z | normal impedance, which is equal to the short-circuit impedance, the inverse impedance, which is equal to the normal impedance, and the homopolar impedance, which is expressed in the ratio of
0 | 0 | impedance, which is equal to the short-circuit impedance, the inverse impedance, which is equal to the normal impedance, and the homopolar impedance, which is expressed in the ratio of Z
/Z | /Z | which is equal to the short-circuit impedance, the inverse impedance, which is equal to the normal impedance, and the homopolar impedance, which is expressed in the ratio of Z 0
1 | 1 | is equal to the short-circuit impedance, the inverse impedance, which is equal to the normal impedance, and the homopolar impedance, which is expressed in the ratio of Z 0 /Z
: | : | equal to the short-circuit impedance, the inverse impedance, which is equal to the normal impedance, and the homopolar impedance, which is expressed in the ratio of Z 0 /Z 1
[ | [ | to the short-circuit impedance, the inverse impedance, which is equal to the normal impedance, and the homopolar impedance, which is expressed in the ratio of Z 0 /Z 1 :
8.4 | 8.4 | the short-circuit impedance, the inverse impedance, which is equal to the normal impedance, and the homopolar impedance, which is expressed in the ratio of Z 0 /Z 1 : [
] | ] | short-circuit impedance, the inverse impedance, which is equal to the normal impedance, and the homopolar impedance, which is expressed in the ratio of Z 0 /Z 1 : [ 8.4
De verhouding van | The ratio of | impedance, the inverse impedance, which is equal to the normal impedance, and the homopolar impedance, which is expressed in the ratio of Z 0 /Z 1 : [ 8.4 ]
Z | Z | impedance, which is equal to the normal impedance, and the homopolar impedance, which is expressed in the ratio of Z 0 /Z 1 : [ 8.4 ] The ratio of
0 | 0 | which is equal to the normal impedance, and the homopolar impedance, which is expressed in the ratio of Z 0 /Z 1 : [ 8.4 ] The ratio of Z
/Z | /Z | is equal to the normal impedance, and the homopolar impedance, which is expressed in the ratio of Z 0 /Z 1 : [ 8.4 ] The ratio of Z 0
1 | 1 | equal to the normal impedance, and the homopolar impedance, which is expressed in the ratio of Z 0 /Z 1 : [ 8.4 ] The ratio of Z 0 /Z
kan worden berekend uit de driefasenkortsluitstroom | can be calculated from the three-phase short-circuit current | to the normal impedance, and the homopolar impedance, which is expressed in the ratio of Z 0 /Z 1 : [ 8.4 ] The ratio of Z 0 /Z 1
I | I | which is expressed in the ratio of Z 0 /Z 1 : [ 8.4 ] The ratio of Z 0 /Z 1 can be calculated from the three-phase short-circuit current
k,3 | k,3 | is expressed in the ratio of Z 0 /Z 1 : [ 8.4 ] The ratio of Z 0 /Z 1 can be calculated from the three-phase short-circuit current I
" | " | expressed in the ratio of Z 0 /Z 1 : [ 8.4 ] The ratio of Z 0 /Z 1 can be calculated from the three-phase short-circuit current I k,3
en de fase-aardkortsluitstroom | and the phase-to-ground short-circuit current | in the ratio of Z 0 /Z 1 : [ 8.4 ] The ratio of Z 0 /Z 1 can be calculated from the three-phase short-circuit current I k,3 "
I | I | 0 /Z 1 : [ 8.4 ] The ratio of Z 0 /Z 1 can be calculated from the three-phase short-circuit current I k,3 " and the phase-to-ground short-circuit current
k,1 | k,1 | /Z 1 : [ 8.4 ] The ratio of Z 0 /Z 1 can be calculated from the three-phase short-circuit current I k,3 " and the phase-to-ground short-circuit current I
" | " | 1 : [ 8.4 ] The ratio of Z 0 /Z 1 can be calculated from the three-phase short-circuit current I k,3 " and the phase-to-ground short-circuit current I k,1
van de netvoeding: | from the power supply: | : [ 8.4 ] The ratio of Z 0 /Z 1 can be calculated from the three-phase short-circuit current I k,3 " and the phase-to-ground short-circuit current I k,1 "
[ | [ | The ratio of Z 0 /Z 1 can be calculated from the three-phase short-circuit current I k,3 " and the phase-to-ground short-circuit current I k,1 " from the power supply:
8.5 | 8.5 | ratio of Z 0 /Z 1 can be calculated from the three-phase short-circuit current I k,3 " and the phase-to-ground short-circuit current I k,1 " from the power supply: [
] | ] | of Z 0 /Z 1 can be calculated from the three-phase short-circuit current I k,3 " and the phase-to-ground short-circuit current I k,1 " from the power supply: [ 8.5
De driefasenkortsluitstroom is de kortsluitbijdrage van het externe net. Deze bijdrage wordt voor het aansluitpunt van het externe net met het te bestuderen deelnet bepaald en is niet afhankelijk van het deelnet. De fase-aardkortsluitstroombijdrage van het externe net is echter wel afhankelijk van het te bestuderen net. Daarom is de fase-aardkortsluitstroombijdrage gedefinieerd als de fase-aardkortsluitstroom bij afwezigheid van het te bestuderen net. Indien de netvoeding geen homopolaire stroom kan voeren is de verhouding van | The three-phase short-circuit current is the short-circuit contribution from the external grid. This contribution is determined for the connection point of the external grid with the network segment under study and is not dependent on the network segment. However, the phase-to-ground short-circuit current contribution from the external grid does depend on the network under study. Therefore, the phase-to-ground short-circuit current contribution is defined as the phase-to-ground short-circuit current in the absence of the network under study. If the power supply cannot carry homopolar current, the ratio of | Z 0 /Z 1 can be calculated from the three-phase short-circuit current I k,3 " and the phase-to-ground short-circuit current I k,1 " from the power supply: [ 8.5 ]
Z | Z | phase-to-ground short-circuit current contribution is defined as the phase-to-ground short-circuit current in the absence of the network under study. If the power supply cannot carry homopolar current, the ratio of
0 | 0 | short-circuit current contribution is defined as the phase-to-ground short-circuit current in the absence of the network under study. If the power supply cannot carry homopolar current, the ratio of Z
/Z | /Z | current contribution is defined as the phase-to-ground short-circuit current in the absence of the network under study. If the power supply cannot carry homopolar current, the ratio of Z 0
1 | 1 | contribution is defined as the phase-to-ground short-circuit current in the absence of the network under study. If the power supply cannot carry homopolar current, the ratio of Z 0 /Z
oneindig. Dit is het geval als de netvoeding een zwevend net is. Indien in het externe net het sterpunt impedantie-geaard is, is de verhouding niet oneindig maar in de grootteorde van 1. De impedantiehoek van de homopolaire impedantie | infinite. This is the case when the power supply is an isolated network. If the neutral point in the external network is impedance-grounded, the ratio is not infinite but on the order of 1. The impedance angle of the homopolar impedance | is defined as the phase-to-ground short-circuit current in the absence of the network under study. If the power supply cannot carry homopolar current, the ratio of Z 0 /Z 1
Z | Z | isolated network. If the neutral point in the external network is impedance-grounded, the ratio is not infinite but on the order of 1. The impedance angle of the homopolar impedance
0 | 0 | network. If the neutral point in the external network is impedance-grounded, the ratio is not infinite but on the order of 1. The impedance angle of the homopolar impedance Z
wordt gelijk verondersteld aan die van de normale impedantie | is assumed to be equal to that of the normal impedance | If the neutral point in the external network is impedance-grounded, the ratio is not infinite but on the order of 1. The impedance angle of the homopolar impedance Z 0
Z | Z | ratio is not infinite but on the order of 1. The impedance angle of the homopolar impedance Z 0 is assumed to be equal to that of the normal impedance
1 | 1 | is not infinite but on the order of 1. The impedance angle of the homopolar impedance Z 0 is assumed to be equal to that of the normal impedance Z
. | . | not infinite but on the order of 1. The impedance angle of the homopolar impedance Z 0 is assumed to be equal to that of the normal impedance Z 1
8.2 Kabels | 8.2 Cables | infinite but on the order of 1. The impedance angle of the homopolar impedance Z 0 is assumed to be equal to that of the normal impedance Z 1 .
De spanningsval over een kabelverbinding wordt volgens de wet van Ohm bepaald door de stroomsterkte door en door de impedantie van de kabel. De impedanties van kabels zijn meestal redelijk beschreven in de brochures van de kabelfabrikanten. Soms ontbreken gegevens, die dan met behulp van de constructiegegevens te berekenen zijn. Sommige impedanties zijn echter afhankelijk van omgevingsfactoren, waardoor het gedrag van een kabelverbinding in de praktijk in bepaalde gevallen moeilijk te voorspellen valt. Deze paragraaf geeft een toelichting op de berekening van de kabelimpedanties en de invloed hierop van de omgeving. | The voltage drop over a cable connection is determined according to Ohm's law by the current through and the impedance of the cable. The impedances of cables are usually reasonably described in the brochures of cable manufacturers. Sometimes data is missing, which can then be calculated using the construction data. However, some impedances are dependent on environmental factors, making the behavior of a cable connection in practice difficult to predict in certain cases. This paragraph provides an explanation of the calculation of cable impedances and the influence of the environment on them. | on the order of 1. The impedance angle of the homopolar impedance Z 0 is assumed to be equal to that of the normal impedance Z 1 . 8.2 Cables
Voor het uitvoeren van kortsluitberekeningen wordt meestal gebruik gemaakt van de methode van symmetrische componenten (hoofdstuk 7). Deze methode maakt het mogelijk om in een symmetrisch driefasesysteem met behulp van een transformatie gemakkelijker asymmetrische belastingen en verstoringen te berekenen. | For performing short-circuit calculations, the method of symmetrical components (chapter 7) is usually used. This method makes it possible to more easily calculate asymmetrical loads and disturbances in a symmetrical three-phase system using a transformation. | a cable connection in practice difficult to predict in certain cases. This paragraph provides an explanation of the calculation of cable impedances and the influence of the environment on them.
Voor de gewone symmetrische berekeningen zijn de gegevens van het normale stelsel voldoende. Voor het berekenen van asymmetrische verschijnselen, zoals fase-aardsluitingen, zijn ook de inverse en homopolaire gegevens van onder meer kabels en transformatoren noodzakelijk. De inverse gegevens zijn in de meeste gevallen gelijk aan de normale gegevens. De homopolaire gegevens zijn niet gelijk aan de normale gegevens en hangen bij kabels af van onder meer de aarding en de ligging in de grond. Ook de nabijheid van andere geleidende objecten, zoals stalen buizen of tramrails heeft invloed op de homopolaire impedantie. Om deze reden wordt de homopolaire impedantie van kabels meestal niet door de fabrikanten gespecificeerd. | For standard symmetrical calculations, the data from the normal system are sufficient. For calculating asymmetrical phenomena, such as phase-to-ground faults, the inverse and homopolar data of cables and transformers, among others, are also necessary. The inverse data are in most cases equal to the normal data. The homopolar data are not equal to the normal data and, in the case of cables, depend on factors such as grounding and their position in the ground. The proximity of other conductive objects, such as steel pipes or tram rails, also affects the homopolar impedance. For this reason, the homopolar impedance of cables is usually not specified by manufacturers. | method of symmetrical components (chapter 7) is usually used. This method makes it possible to more easily calculate asymmetrical loads and disturbances in a symmetrical three-phase system using a transformation.
Een kabel kan worden gemodelleerd met een normale, een inverse en een homopolaire impedantie. De normale impedantie is gelijk aan de bedrijfsimpedantie. Deze is meestal wel bekend en kan worden afgeleid uit brochures en naamplaatgegevens. De inverse impedantie van kabels is gelijk aan de normale impedantie. De werkelijke homopolaire impedantie kan alleen door meting van het bestaande circuit verkregen worden. Hoogspanningslijnen worden altijd gemeten en de modelimpedanties zijn in die gevallen goed bekend bij de netbeheerder. De impedanties van MS-kabelverbindingen zijn in de meeste gevallen niet gemeten. Voor een kabel is slechts een beperkte algemene richtlijn te geven voor de waarde van de impedanties. De impedanties zijn onder meer afhankelijk van: | A cable can be modeled with a normal, an inverse, and a homopolar impedance. The normal impedance is equal to the operational impedance. This is usually known and can be derived from brochures and nameplate data. The inverse impedance of cables is equal to the normal impedance. The actual homopolar impedance can only be obtained by measuring the existing circuit. High-voltage lines are always measured, and the model impedances are well known to the grid operator in those cases. The impedances of medium-voltage cable connections are, in most cases, not measured. For a cable, only a limited general guideline can be given for the value of the impedances. The impedances depend, among other things, on: | of other conductive objects, such as steel pipes or tram rails, also affects the homopolar impedance. For this reason, the homopolar impedance of cables is usually not specified by manufacturers.
uitvoering: drie éénfasekabels of één driefasenkabel | configuration: three single-phase cables or one three-phase cable | are, in most cases, not measured. For a cable, only a limited general guideline can be given for the value of the impedances. The impedances depend, among other things, on:
ligging: onderlinge afstand in plat vlak of in driehoek | position: mutual distance in a flat plane or in a triangle | cable, only a limited general guideline can be given for the value of the impedances. The impedances depend, among other things, on: configuration: three single-phase cables or one three-phase cable
aanwezigheid van andere geleidende objecten zoals andere kabels of pijpleidingen. | presence of other conductive objects such as other cables or pipelines. | value of the impedances. The impedances depend, among other things, on: configuration: three single-phase cables or one three-phase cable position: mutual distance in a flat plane or in a triangle
Omdat de homopolaire gegevens worden beïnvloed door de liggingsomstandigheden en de omgeving, kunnen deze het best gemeten worden aan de bestaande verbinding voordat deze in bedrijf genomen wordt. Voor planningsdoeleinden moeten deze waarden geschat worden. Indien geen betrouwbare waarden beschikbaar zijn, moet een schatting gemaakt worden. | Because the homopolar data are influenced by the laying conditions and the environment, they are best measured on the existing connection before it is put into operation. For planning purposes, these values must be estimated. If no reliable values are available, an estimate must be made. | configuration: three single-phase cables or one three-phase cable position: mutual distance in a flat plane or in a triangle presence of other conductive objects such as other cables or pipelines.
Samenvattend zijn van de kabel te onderscheiden: | In summary, the following can be distinguished from the cable: | measured on the existing connection before it is put into operation. For planning purposes, these values must be estimated. If no reliable values are available, an estimate must be made.
normale impedantie: Z | normal impedance: Z | operation. For planning purposes, these values must be estimated. If no reliable values are available, an estimate must be made. In summary, the following can be distinguished from the cable:
1 | 1 | purposes, these values must be estimated. If no reliable values are available, an estimate must be made. In summary, the following can be distinguished from the cable: normal impedance: Z
these values must be estimated. If no reliable values are available, an estimate must be made. In summary, the following can be distinguished from the cable: normal impedance: Z 1
1 | 1 | must be estimated. If no reliable values are available, an estimate must be made. In summary, the following can be distinguished from the cable: normal impedance: Z 1 = R
+ jX | + jX | be estimated. If no reliable values are available, an estimate must be made. In summary, the following can be distinguished from the cable: normal impedance: Z 1 = R 1
1 | 1 | If no reliable values are available, an estimate must be made. In summary, the following can be distinguished from the cable: normal impedance: Z 1 = R 1 + jX
homopolaire impedantie: Z | homopolar impedance: Z | no reliable values are available, an estimate must be made. In summary, the following can be distinguished from the cable: normal impedance: Z 1 = R 1 + jX 1
0 | 0 | are available, an estimate must be made. In summary, the following can be distinguished from the cable: normal impedance: Z 1 = R 1 + jX 1 homopolar impedance: Z
available, an estimate must be made. In summary, the following can be distinguished from the cable: normal impedance: Z 1 = R 1 + jX 1 homopolar impedance: Z 0
0 | 0 | estimate must be made. In summary, the following can be distinguished from the cable: normal impedance: Z 1 = R 1 + jX 1 homopolar impedance: Z 0 = R
+ jX | + jX | must be made. In summary, the following can be distinguished from the cable: normal impedance: Z 1 = R 1 + jX 1 homopolar impedance: Z 0 = R 0
0 | 0 | made. In summary, the following can be distinguished from the cable: normal impedance: Z 1 = R 1 + jX 1 homopolar impedance: Z 0 = R 0 + jX
normale capaciteit: C | normal capacitance: C | In summary, the following can be distinguished from the cable: normal impedance: Z 1 = R 1 + jX 1 homopolar impedance: Z 0 = R 0 + jX 0
1 | 1 | following can be distinguished from the cable: normal impedance: Z 1 = R 1 + jX 1 homopolar impedance: Z 0 = R 0 + jX 0 normal capacitance: C
homopolaire capaciteit: C | homopolar capacitance: C | can be distinguished from the cable: normal impedance: Z 1 = R 1 + jX 1 homopolar impedance: Z 0 = R 0 + jX 0 normal capacitance: C 1
0 | 0 | from the cable: normal impedance: Z 1 = R 1 + jX 1 homopolar impedance: Z 0 = R 0 + jX 0 normal capacitance: C 1 homopolar capacitance: C
8.2.1 Normale impedantie | 8.2.1 Normal Impedance | the cable: normal impedance: Z 1 = R 1 + jX 1 homopolar impedance: Z 0 = R 0 + jX 0 normal capacitance: C 1 homopolar capacitance: C 0
De impedantie voor de normale component bestaat uit de normale weerstand en de normale reactantie. De normale impedantie wordt gebruikt voor alle berekeningen. | The impedance for the normal component consists of the normal resistance and the normal reactance. The normal impedance is used for all calculations. | impedance: Z 1 = R 1 + jX 1 homopolar impedance: Z 0 = R 0 + jX 0 normal capacitance: C 1 homopolar capacitance: C 0 8.2.1 Normal Impedance
Normale weerstand | Normal resistance | homopolar capacitance: C 0 8.2.1 Normal Impedance The impedance for the normal component consists of the normal resistance and the normal reactance. The normal impedance is used for all calculations.
De normale weerstand | The normal resistance | C 0 8.2.1 Normal Impedance The impedance for the normal component consists of the normal resistance and the normal reactance. The normal impedance is used for all calculations. Normal resistance
R | R | Normal Impedance The impedance for the normal component consists of the normal resistance and the normal reactance. The normal impedance is used for all calculations. Normal resistance The normal resistance
1 | 1 | Impedance The impedance for the normal component consists of the normal resistance and the normal reactance. The normal impedance is used for all calculations. Normal resistance The normal resistance R
is gelijk aan de bedrijfsweerstand. Deze wordt meestal door de fabrikant gespecificeerd | is equal to the operating resistance. This is usually specified by the manufacturer. | The impedance for the normal component consists of the normal resistance and the normal reactance. The normal impedance is used for all calculations. Normal resistance The normal resistance R 1
als R | as R | normal reactance. The normal impedance is used for all calculations. Normal resistance The normal resistance R 1 is equal to the operating resistance. This is usually specified by the manufacturer.
DC,20 | DC,20 | The normal impedance is used for all calculations. Normal resistance The normal resistance R 1 is equal to the operating resistance. This is usually specified by the manufacturer. as R
, de gelijkstroomweerstand bij 20°C. Indien deze waarde niet bekend is, kan deze worden opgezocht in de standaard IEC 60228 'Conductors of insulated cables', in de tabellen voor Class 1 (Solid conductors) en Class 2 (Stranded conductors). Soms geeft de fabrikant de wisselstroomweerstand voor de gegeven frequentie en de maximum bedrijfstemperatuur. | , the direct current resistance at 20°C. If this value is not known, it can be looked up in the standard IEC 60228 'Conductors of insulated cables', in the tables for Class 1 (Solid conductors) and Class 2 (Stranded conductors). Sometimes the manufacturer provides the alternating current resistance for the given frequency and the maximum operating temperature. | normal impedance is used for all calculations. Normal resistance The normal resistance R 1 is equal to the operating resistance. This is usually specified by the manufacturer. as R DC,20
Bij kortsluitberekeningen volgens IEC 60909 moet voor berekening van de initiële kortsluitstroom de weerstand bij 20°C gebruikt worden. Bij loadflowberekeningen kan daarvan afgeweken worden. Soms geeft de fabrikant de weerstand op bij maximum geleidertemperatuur. Het is echter niet altijd reëel om met de weerstand te werken bij de maximum geleidertemperatuur (50°C voor GPLK kabels, 65°C voor Alkudia kabels en 90°C voor XLPE kabels). De meeste kabels zijn immers niet continu vol belast, waardoor de temperatuur nooit de maximum waarde zal bereiken. Een bedrijfsspecifieke waarde kan door de organisatie van de gebruiker zelf worden vastgesteld. De geleiderweerstand wordt dan berekend met onderstaande formule. | For short-circuit calculations according to IEC 60909, the resistance at 20°C must be used to calculate the initial short-circuit current. For load flow calculations, deviations from this can be made. Sometimes the manufacturer provides the resistance at the maximum conductor temperature. However, it is not always realistic to work with the resistance at the maximum conductor temperature (50°C for GPLK cables, 65°C for Alkudia cables, and 90°C for XLPE cables). Most cables are not continuously fully loaded, so the temperature will never reach the maximum value. A company-specific value can be determined by the user's organization. The conductor resistance is then calculated using the formula below. | in the tables for Class 1 (Solid conductors) and Class 2 (Stranded conductors). Sometimes the manufacturer provides the alternating current resistance for the given frequency and the maximum operating temperature.
[ | [ | loaded, so the temperature will never reach the maximum value. A company-specific value can be determined by the user's organization. The conductor resistance is then calculated using the formula below.
8.6 | 8.6 | so the temperature will never reach the maximum value. A company-specific value can be determined by the user's organization. The conductor resistance is then calculated using the formula below. [
] | ] | the temperature will never reach the maximum value. A company-specific value can be determined by the user's organization. The conductor resistance is then calculated using the formula below. [ 8.6
waarin: | in which: | temperature will never reach the maximum value. A company-specific value can be determined by the user's organization. The conductor resistance is then calculated using the formula below. [ 8.6 ]
R | R | never reach the maximum value. A company-specific value can be determined by the user's organization. The conductor resistance is then calculated using the formula below. [ 8.6 ] in which:
DC,20 | DC,20 | reach the maximum value. A company-specific value can be determined by the user's organization. The conductor resistance is then calculated using the formula below. [ 8.6 ] in which: R
geleider gelijkstroomweerstand bij 20 graden Celcius, volgens opgave fabrikant (W/m) | conductor direct current resistance at 20 degrees Celsius, according to manufacturer specifications (Ω/m) | the maximum value. A company-specific value can be determined by the user's organization. The conductor resistance is then calculated using the formula below. [ 8.6 ] in which: R DC,20
α | alpha | The conductor resistance is then calculated using the formula below. [ 8.6 ] in which: R DC,20 conductor direct current resistance at 20 degrees Celsius, according to manufacturer specifications (Ω/m)
20 | 20 | conductor resistance is then calculated using the formula below. [ 8.6 ] in which: R DC,20 conductor direct current resistance at 20 degrees Celsius, according to manufacturer specifications (Ω/m) alpha
temperatuurcoëfficiënt (0,00403 per graad Celsius voor aluminium; | temperature coefficient (0.00403 per degree Celsius for aluminum; | resistance is then calculated using the formula below. [ 8.6 ] in which: R DC,20 conductor direct current resistance at 20 degrees Celsius, according to manufacturer specifications (Ω/m) alpha 20
0,00393 per graad Celsius voor koper) | 0.00393 per degree Celsius for copper) | [ 8.6 ] in which: R DC,20 conductor direct current resistance at 20 degrees Celsius, according to manufacturer specifications (Ω/m) alpha 20 temperature coefficient (0.00403 per degree Celsius for aluminum;
θ | theta | DC,20 conductor direct current resistance at 20 degrees Celsius, according to manufacturer specifications (Ω/m) alpha 20 temperature coefficient (0.00403 per degree Celsius for aluminum; 0.00393 per degree Celsius for copper)
geleidertemperatuur (graden Celsius) | conductor temperature (degrees Celsius) | conductor direct current resistance at 20 degrees Celsius, according to manufacturer specifications (Ω/m) alpha 20 temperature coefficient (0.00403 per degree Celsius for aluminum; 0.00393 per degree Celsius for copper) theta
In laagspanningsnetten heeft de geleiderweerstand de grootste invloed en speelt de zelfinductie een veel kleinere rol. Daarom is de invloed van de temperatuur op de spanningen voornamelijk beperkt tot de laagspanningsnetten. De temperatuurcoëfficiënt | In low voltage networks, the conductor resistance has the greatest influence, and self-induction plays a much smaller role. Therefore, the impact of temperature on voltages is mainly limited to low voltage networks. The temperature coefficient | at 20 degrees Celsius, according to manufacturer specifications (Ω/m) alpha 20 temperature coefficient (0.00403 per degree Celsius for aluminum; 0.00393 per degree Celsius for copper) theta conductor temperature (degrees Celsius)
α | alpha | conductor resistance has the greatest influence, and self-induction plays a much smaller role. Therefore, the impact of temperature on voltages is mainly limited to low voltage networks. The temperature coefficient
20 | 20 | resistance has the greatest influence, and self-induction plays a much smaller role. Therefore, the impact of temperature on voltages is mainly limited to low voltage networks. The temperature coefficient alpha
leidt ongeveer tot een afwijking van 0,4 % van de geleiderweerstand per graad en tot een even zo grote afwijking van de spanningsval over de betreffende kabel. Dat betekent dat een verhoging van de geleidertemperatuur van 30 graden naar 55 graden Celsius leidt tot een verandering van de spanningsval over de kabel van ongeveer 10 %. | leads to a deviation of approximately 0.4% of the conductor resistance per degree and an equally large deviation of the voltage drop over the respective cable. This means that an increase in conductor temperature from 30 degrees to 55 degrees Celsius results in a change in the voltage drop over the cable of approximately 10%. | has the greatest influence, and self-induction plays a much smaller role. Therefore, the impact of temperature on voltages is mainly limited to low voltage networks. The temperature coefficient alpha 20
De berekende waarde voor | The calculated value for | cable. This means that an increase in conductor temperature from 30 degrees to 55 degrees Celsius results in a change in the voltage drop over the cable of approximately 10%.
R' | R' | an increase in conductor temperature from 30 degrees to 55 degrees Celsius results in a change in the voltage drop over the cable of approximately 10%. The calculated value for
is de voor de temperatuur gecorrigeerde gelijkstroomweerstand. Formeel moet deze berekende waarde nog gecorrigeerd worden voor het skin-effect en het proximity-effect om de wisselstroomweerstand te krijgen. Voor standaard kabels geldt: | is the temperature-corrected direct current resistance. Formally, this calculated value must still be corrected for the skin effect and the proximity effect to obtain the alternating current resistance. For standard cables: | increase in conductor temperature from 30 degrees to 55 degrees Celsius results in a change in the voltage drop over the cable of approximately 10%. The calculated value for R'
[ | [ | the temperature-corrected direct current resistance. Formally, this calculated value must still be corrected for the skin effect and the proximity effect to obtain the alternating current resistance. For standard cables:
8.7 | 8.7 | temperature-corrected direct current resistance. Formally, this calculated value must still be corrected for the skin effect and the proximity effect to obtain the alternating current resistance. For standard cables: [
] | ] | direct current resistance. Formally, this calculated value must still be corrected for the skin effect and the proximity effect to obtain the alternating current resistance. For standard cables: [ 8.7
met: | with: | current resistance. Formally, this calculated value must still be corrected for the skin effect and the proximity effect to obtain the alternating current resistance. For standard cables: [ 8.7 ]
y | y | resistance. Formally, this calculated value must still be corrected for the skin effect and the proximity effect to obtain the alternating current resistance. For standard cables: [ 8.7 ] with:
s | s | Formally, this calculated value must still be corrected for the skin effect and the proximity effect to obtain the alternating current resistance. For standard cables: [ 8.7 ] with: y
skin-effect factor | skin effect factor | this calculated value must still be corrected for the skin effect and the proximity effect to obtain the alternating current resistance. For standard cables: [ 8.7 ] with: y s
y | y | must still be corrected for the skin effect and the proximity effect to obtain the alternating current resistance. For standard cables: [ 8.7 ] with: y s skin effect factor
p | p | still be corrected for the skin effect and the proximity effect to obtain the alternating current resistance. For standard cables: [ 8.7 ] with: y s skin effect factor y
proximity-effect factor | proximity effect factor | be corrected for the skin effect and the proximity effect to obtain the alternating current resistance. For standard cables: [ 8.7 ] with: y s skin effect factor y p
Het skin-effect wordt veroorzaakt doordat in een geleider de stroom aan het geleideroppervlak wil gaan vloeien, waardoor de stroomdichtheid in het midden van de geleider kleiner is dan aan het oppervlak en waardoor de effectieve weerstand toeneemt. De skin-effect factor kan berekend worden volgens IEC 60287 met onderstaande formule: | The skin effect is caused by the tendency of current to flow on the surface of a conductor, resulting in a lower current density in the center of the conductor compared to the surface, thereby increasing the effective resistance. The skin effect factor can be calculated according to IEC 60287 using the following formula: | the skin effect and the proximity effect to obtain the alternating current resistance. For standard cables: [ 8.7 ] with: y s skin effect factor y p proximity effect factor
[ | [ | in the center of the conductor compared to the surface, thereby increasing the effective resistance. The skin effect factor can be calculated according to IEC 60287 using the following formula:
8.8 | 8.8 | the center of the conductor compared to the surface, thereby increasing the effective resistance. The skin effect factor can be calculated according to IEC 60287 using the following formula: [
] | ] | center of the conductor compared to the surface, thereby increasing the effective resistance. The skin effect factor can be calculated according to IEC 60287 using the following formula: [ 8.8
met: | with: | of the conductor compared to the surface, thereby increasing the effective resistance. The skin effect factor can be calculated according to IEC 60287 using the following formula: [ 8.8 ]
f | f | the conductor compared to the surface, thereby increasing the effective resistance. The skin effect factor can be calculated according to IEC 60287 using the following formula: [ 8.8 ] with:
conductor compared to the surface, thereby increasing the effective resistance. The skin effect factor can be calculated according to IEC 60287 using the following formula: [ 8.8 ] with: f
Waarden voor | Values for | the surface, thereby increasing the effective resistance. The skin effect factor can be calculated according to IEC 60287 using the following formula: [ 8.8 ] with: f = frequency (Hz)
k | k | thereby increasing the effective resistance. The skin effect factor can be calculated according to IEC 60287 using the following formula: [ 8.8 ] with: f = frequency (Hz) Values for
s | s | increasing the effective resistance. The skin effect factor can be calculated according to IEC 60287 using the following formula: [ 8.8 ] with: f = frequency (Hz) Values for k
worden gegeven door IEC 60287. Voor ronde geslagen geleiders is | provided by IEC 60287. For round stranded conductors, it is | the effective resistance. The skin effect factor can be calculated according to IEC 60287 using the following formula: [ 8.8 ] with: f = frequency (Hz) Values for k s
k | k | according to IEC 60287 using the following formula: [ 8.8 ] with: f = frequency (Hz) Values for k s provided by IEC 60287. For round stranded conductors, it is
s | s | to IEC 60287 using the following formula: [ 8.8 ] with: f = frequency (Hz) Values for k s provided by IEC 60287. For round stranded conductors, it is k
gelijk aan 1. Voor ronde massieve aluminium geleiders wordt 1 aangenomen. | equal to 1. For round solid aluminum conductors, 1 is assumed. | IEC 60287 using the following formula: [ 8.8 ] with: f = frequency (Hz) Values for k s provided by IEC 60287. For round stranded conductors, it is k s
Het proximity-effect wordt veroorzaakt in naburige geleiders, waarin als gevolg van het magnetische veld gelijkgerichte stromen elkaar afstoten. Als gevolg van de stroomverdringing neemt de effectieve weerstand toe. De proximity-effect factor is afhankelijk van de ligging van de geleiders ten opzichte van elkaar en kan berekend worden volgens IEC 60287 met onderstaande formule: | The proximity effect is caused in neighboring conductors, where like-directed currents repel each other due to the magnetic field. As a result of current displacement, the effective resistance increases. The proximity effect factor depends on the position of the conductors relative to each other and can be calculated according to IEC 60287 using the formula below:
[ | [ | effective resistance increases. The proximity effect factor depends on the position of the conductors relative to each other and can be calculated according to IEC 60287 using the formula below:
8.9 | 8.9 | resistance increases. The proximity effect factor depends on the position of the conductors relative to each other and can be calculated according to IEC 60287 using the formula below: [
] | ] | increases. The proximity effect factor depends on the position of the conductors relative to each other and can be calculated according to IEC 60287 using the formula below: [ 8.9
met: | with: | The proximity effect factor depends on the position of the conductors relative to each other and can be calculated according to IEC 60287 using the formula below: [ 8.9 ]
d | d | proximity effect factor depends on the position of the conductors relative to each other and can be calculated according to IEC 60287 using the formula below: [ 8.9 ] with:
c | c | effect factor depends on the position of the conductors relative to each other and can be calculated according to IEC 60287 using the formula below: [ 8.9 ] with: d
diameter van de geleider (mm) | diameter of the conductor (mm) | factor depends on the position of the conductors relative to each other and can be calculated according to IEC 60287 using the formula below: [ 8.9 ] with: d c
s | s | of the conductors relative to each other and can be calculated according to IEC 60287 using the formula below: [ 8.9 ] with: d c diameter of the conductor (mm)
hart op hart afstand van naastgelegen geleiders (mm) | center-to-center distance of adjacent conductors (mm) | the conductors relative to each other and can be calculated according to IEC 60287 using the formula below: [ 8.9 ] with: d c diameter of the conductor (mm) s
Waarden voor | Values for | and can be calculated according to IEC 60287 using the formula below: [ 8.9 ] with: d c diameter of the conductor (mm) s center-to-center distance of adjacent conductors (mm)
k | k | be calculated according to IEC 60287 using the formula below: [ 8.9 ] with: d c diameter of the conductor (mm) s center-to-center distance of adjacent conductors (mm) Values for
p | p | calculated according to IEC 60287 using the formula below: [ 8.9 ] with: d c diameter of the conductor (mm) s center-to-center distance of adjacent conductors (mm) Values for k
worden gegeven door IEC 60287. Voor ronde geslagen geleiders is | given by IEC 60287. For round stranded conductors, it is | according to IEC 60287 using the formula below: [ 8.9 ] with: d c diameter of the conductor (mm) s center-to-center distance of adjacent conductors (mm) Values for k p
k | k | ] with: d c diameter of the conductor (mm) s center-to-center distance of adjacent conductors (mm) Values for k p given by IEC 60287. For round stranded conductors, it is
p | p | with: d c diameter of the conductor (mm) s center-to-center distance of adjacent conductors (mm) Values for k p given by IEC 60287. For round stranded conductors, it is k
gelijk aan 1. Voor ronde massieve aluminium geleiders wordt 1 aangenomen. | equal to 1. For round solid aluminum conductors, 1 is assumed. | d c diameter of the conductor (mm) s center-to-center distance of adjacent conductors (mm) Values for k p given by IEC 60287. For round stranded conductors, it is k p
Tabel 8.2 geeft als voorbeeld de berekende waarden van het skin- en proximity-effect van enkele LS- en MS-kabels. De tabel illustreert hoe het skin-effect afhangt van de gelijkstroomweerstand: beneden een geleiderdoorsnede van 240 mm | Table 8.2 provides an example of the calculated values of the skin and proximity effect for some LV and MV cables. The table illustrates how the skin effect depends on the DC resistance: below a conductor cross-section of 240 mm | adjacent conductors (mm) Values for k p given by IEC 60287. For round stranded conductors, it is k p equal to 1. For round solid aluminum conductors, 1 is assumed.
2 | 2 | the skin and proximity effect for some LV and MV cables. The table illustrates how the skin effect depends on the DC resistance: below a conductor cross-section of 240 mm
is de factor klein tot verwaarloosbaar en daarboven wordt de factor snel groter. Bovendien is het skin-effect bij kabels met Cu-geleider groter dan bij kabels met Al-geleider. Ook het proximity-effect neemt toe bij afnemende gelijkstroomweerstand. Bij de enkeladerige kabels van 1000 mm | the factor is small to negligible, and above that, the factor increases rapidly. Moreover, the skin effect is greater in cables with Cu conductors than in cables with Al conductors. The proximity effect also increases with decreasing DC resistance. For single-core cables of 1000 mm | skin and proximity effect for some LV and MV cables. The table illustrates how the skin effect depends on the DC resistance: below a conductor cross-section of 240 mm 2
2 | 2 | skin effect is greater in cables with Cu conductors than in cables with Al conductors. The proximity effect also increases with decreasing DC resistance. For single-core cables of 1000 mm
geleiderdoorsnede is goed te zien dat het proximity-effect bij ligging in driehoeksformatie, waarbij de kabels elkaar raken, veel groter is dan bij ligging in een plat vlak, waarbij de kabels elkaar niet raken (70 mm tussenruimte). | It is clearly visible that the proximity effect in a triangular formation, where the cables touch each other, is much greater than in a flat formation, where the cables do not touch each other (70 mm spacing). | effect is greater in cables with Cu conductors than in cables with Al conductors. The proximity effect also increases with decreasing DC resistance. For single-core cables of 1000 mm 2
Tabel 8.2 Skin- en proximity-effect bij enkele distributiekabels | Table 8.2 Skin and proximity effect in individual distribution cables | effect in a triangular formation, where the cables touch each other, is much greater than in a flat formation, where the cables do not touch each other (70 mm spacing).
Kabeltype | Kabeltype | other, is much greater than in a flat formation, where the cables do not touch each other (70 mm spacing). Table 8.2 Skin and proximity effect in individual distribution cables
Skin-effect factor | Skin-effect factor | is much greater than in a flat formation, where the cables do not touch each other (70 mm spacing). Table 8.2 Skin and proximity effect in individual distribution cables Kabeltype
Proximity-effect factor | Proximity-effect factor | greater than in a flat formation, where the cables do not touch each other (70 mm spacing). Table 8.2 Skin and proximity effect in individual distribution cables Kabeltype Skin-effect factor
3x240 mm | 3x240 mm | in a flat formation, where the cables do not touch each other (70 mm spacing). Table 8.2 Skin and proximity effect in individual distribution cables Kabeltype Skin-effect factor Proximity-effect factor
2 | 2 | flat formation, where the cables do not touch each other (70 mm spacing). Table 8.2 Skin and proximity effect in individual distribution cables Kabeltype Skin-effect factor Proximity-effect factor 3x240 mm
Al 0,6/1 kV | Al 0.6/1 kV | formation, where the cables do not touch each other (70 mm spacing). Table 8.2 Skin and proximity effect in individual distribution cables Kabeltype Skin-effect factor Proximity-effect factor 3x240 mm 2
0,004 | 0.004 | cables do not touch each other (70 mm spacing). Table 8.2 Skin and proximity effect in individual distribution cables Kabeltype Skin-effect factor Proximity-effect factor 3x240 mm 2 Al 0.6/1 kV
0,011 | 0.011 | do not touch each other (70 mm spacing). Table 8.2 Skin and proximity effect in individual distribution cables Kabeltype Skin-effect factor Proximity-effect factor 3x240 mm 2 Al 0.6/1 kV 0.004
3x240 mm | 3x240 mm | not touch each other (70 mm spacing). Table 8.2 Skin and proximity effect in individual distribution cables Kabeltype Skin-effect factor Proximity-effect factor 3x240 mm 2 Al 0.6/1 kV 0.004 0.011
2 | 2 | each other (70 mm spacing). Table 8.2 Skin and proximity effect in individual distribution cables Kabeltype Skin-effect factor Proximity-effect factor 3x240 mm 2 Al 0.6/1 kV 0.004 0.011 3x240 mm
Cu 0,6/1 kV | Cu 0.6/1 kV | other (70 mm spacing). Table 8.2 Skin and proximity effect in individual distribution cables Kabeltype Skin-effect factor Proximity-effect factor 3x240 mm 2 Al 0.6/1 kV 0.004 0.011 3x240 mm 2
0,010 | 0.010 | spacing). Table 8.2 Skin and proximity effect in individual distribution cables Kabeltype Skin-effect factor Proximity-effect factor 3x240 mm 2 Al 0.6/1 kV 0.004 0.011 3x240 mm 2 Cu 0.6/1 kV
0,030 | 0.030 | Table 8.2 Skin and proximity effect in individual distribution cables Kabeltype Skin-effect factor Proximity-effect factor 3x240 mm 2 Al 0.6/1 kV 0.004 0.011 3x240 mm 2 Cu 0.6/1 kV 0.010
3x50 mm | 3x50 mm | 8.2 Skin and proximity effect in individual distribution cables Kabeltype Skin-effect factor Proximity-effect factor 3x240 mm 2 Al 0.6/1 kV 0.004 0.011 3x240 mm 2 Cu 0.6/1 kV 0.010 0.030
2 | 2 | and proximity effect in individual distribution cables Kabeltype Skin-effect factor Proximity-effect factor 3x240 mm 2 Al 0.6/1 kV 0.004 0.011 3x240 mm 2 Cu 0.6/1 kV 0.010 0.030 3x50 mm
Cu 6/10 kV | Cu 6/10 kV | proximity effect in individual distribution cables Kabeltype Skin-effect factor Proximity-effect factor 3x240 mm 2 Al 0.6/1 kV 0.004 0.011 3x240 mm 2 Cu 0.6/1 kV 0.010 0.030 3x50 mm 2
<0,001 | <0.001 | individual distribution cables Kabeltype Skin-effect factor Proximity-effect factor 3x240 mm 2 Al 0.6/1 kV 0.004 0.011 3x240 mm 2 Cu 0.6/1 kV 0.010 0.030 3x50 mm 2 Cu 6/10 kV
<0,001 | <0.001 | distribution cables Kabeltype Skin-effect factor Proximity-effect factor 3x240 mm 2 Al 0.6/1 kV 0.004 0.011 3x240 mm 2 Cu 0.6/1 kV 0.010 0.030 3x50 mm 2 Cu 6/10 kV <0.001
3x95 mm | 3x95 mm | cables Kabeltype Skin-effect factor Proximity-effect factor 3x240 mm 2 Al 0.6/1 kV 0.004 0.011 3x240 mm 2 Cu 0.6/1 kV 0.010 0.030 3x50 mm 2 Cu 6/10 kV <0.001 <0.001
2 | 2 | Skin-effect factor Proximity-effect factor 3x240 mm 2 Al 0.6/1 kV 0.004 0.011 3x240 mm 2 Cu 0.6/1 kV 0.010 0.030 3x50 mm 2 Cu 6/10 kV <0.001 <0.001 3x95 mm
Cu 6/10 kV | Cu 6/10 kV | factor Proximity-effect factor 3x240 mm 2 Al 0.6/1 kV 0.004 0.011 3x240 mm 2 Cu 0.6/1 kV 0.010 0.030 3x50 mm 2 Cu 6/10 kV <0.001 <0.001 3x95 mm 2
0,001 | 0.001 | 3x240 mm 2 Al 0.6/1 kV 0.004 0.011 3x240 mm 2 Cu 0.6/1 kV 0.010 0.030 3x50 mm 2 Cu 6/10 kV <0.001 <0.001 3x95 mm 2 Cu 6/10 kV
0,002 | 0.002 | mm 2 Al 0.6/1 kV 0.004 0.011 3x240 mm 2 Cu 0.6/1 kV 0.010 0.030 3x50 mm 2 Cu 6/10 kV <0.001 <0.001 3x95 mm 2 Cu 6/10 kV 0.001
3x150 mm | 3x150 mm | 2 Al 0.6/1 kV 0.004 0.011 3x240 mm 2 Cu 0.6/1 kV 0.010 0.030 3x50 mm 2 Cu 6/10 kV <0.001 <0.001 3x95 mm 2 Cu 6/10 kV 0.001 0.002
2 | 2 | 0.6/1 kV 0.004 0.011 3x240 mm 2 Cu 0.6/1 kV 0.010 0.030 3x50 mm 2 Cu 6/10 kV <0.001 <0.001 3x95 mm 2 Cu 6/10 kV 0.001 0.002 3x150 mm
Cu 6/10 kV | Cu 6/10 kV | kV 0.004 0.011 3x240 mm 2 Cu 0.6/1 kV 0.010 0.030 3x50 mm 2 Cu 6/10 kV <0.001 <0.001 3x95 mm 2 Cu 6/10 kV 0.001 0.002 3x150 mm 2
0,003 | 0.003 | 3x240 mm 2 Cu 0.6/1 kV 0.010 0.030 3x50 mm 2 Cu 6/10 kV <0.001 <0.001 3x95 mm 2 Cu 6/10 kV 0.001 0.002 3x150 mm 2 Cu 6/10 kV
0,005 | 0.005 | mm 2 Cu 0.6/1 kV 0.010 0.030 3x50 mm 2 Cu 6/10 kV <0.001 <0.001 3x95 mm 2 Cu 6/10 kV 0.001 0.002 3x150 mm 2 Cu 6/10 kV 0.003
3x240 mm | 3x240 mm | 2 Cu 0.6/1 kV 0.010 0.030 3x50 mm 2 Cu 6/10 kV <0.001 <0.001 3x95 mm 2 Cu 6/10 kV 0.001 0.002 3x150 mm 2 Cu 6/10 kV 0.003 0.005
2 | 2 | 0.6/1 kV 0.010 0.030 3x50 mm 2 Cu 6/10 kV <0.001 <0.001 3x95 mm 2 Cu 6/10 kV 0.001 0.002 3x150 mm 2 Cu 6/10 kV 0.003 0.005 3x240 mm
Cu 6/10 kV | Cu 6/10 kV | kV 0.010 0.030 3x50 mm 2 Cu 6/10 kV <0.001 <0.001 3x95 mm 2 Cu 6/10 kV 0.001 0.002 3x150 mm 2 Cu 6/10 kV 0.003 0.005 3x240 mm 2
0,008 | 0.008 | 3x50 mm 2 Cu 6/10 kV <0.001 <0.001 3x95 mm 2 Cu 6/10 kV 0.001 0.002 3x150 mm 2 Cu 6/10 kV 0.003 0.005 3x240 mm 2 Cu 6/10 kV
0,015 | 0.015 | mm 2 Cu 6/10 kV <0.001 <0.001 3x95 mm 2 Cu 6/10 kV 0.001 0.002 3x150 mm 2 Cu 6/10 kV 0.003 0.005 3x240 mm 2 Cu 6/10 kV 0.008
3 x 1x240 mm | 3 x 1x240 mm | 2 Cu 6/10 kV <0.001 <0.001 3x95 mm 2 Cu 6/10 kV 0.001 0.002 3x150 mm 2 Cu 6/10 kV 0.003 0.005 3x240 mm 2 Cu 6/10 kV 0.008 0.015
2 | 2 | <0.001 <0.001 3x95 mm 2 Cu 6/10 kV 0.001 0.002 3x150 mm 2 Cu 6/10 kV 0.003 0.005 3x240 mm 2 Cu 6/10 kV 0.008 0.015 3 x 1x240 mm
Al 6/10 kV, driehoek | Al 6/10 kV, delta | <0.001 3x95 mm 2 Cu 6/10 kV 0.001 0.002 3x150 mm 2 Cu 6/10 kV 0.003 0.005 3x240 mm 2 Cu 6/10 kV 0.008 0.015 3 x 1x240 mm 2
0,003 | 0.003 | Cu 6/10 kV 0.001 0.002 3x150 mm 2 Cu 6/10 kV 0.003 0.005 3x240 mm 2 Cu 6/10 kV 0.008 0.015 3 x 1x240 mm 2 Al 6/10 kV, delta
0,003 | 0.003 | 6/10 kV 0.001 0.002 3x150 mm 2 Cu 6/10 kV 0.003 0.005 3x240 mm 2 Cu 6/10 kV 0.008 0.015 3 x 1x240 mm 2 Al 6/10 kV, delta 0.003
3 x 1x630 mm | 3 x 1x630 mm | kV 0.001 0.002 3x150 mm 2 Cu 6/10 kV 0.003 0.005 3x240 mm 2 Cu 6/10 kV 0.008 0.015 3 x 1x240 mm 2 Al 6/10 kV, delta 0.003 0.003
2 | 2 | mm 2 Cu 6/10 kV 0.003 0.005 3x240 mm 2 Cu 6/10 kV 0.008 0.015 3 x 1x240 mm 2 Al 6/10 kV, delta 0.003 0.003 3 x 1x630 mm
Al 6/10 kV, driehoek | Al 6/10 kV, delta | 2 Cu 6/10 kV 0.003 0.005 3x240 mm 2 Cu 6/10 kV 0.008 0.015 3 x 1x240 mm 2 Al 6/10 kV, delta 0.003 0.003 3 x 1x630 mm 2
0,022 | 0.022 | 0.003 0.005 3x240 mm 2 Cu 6/10 kV 0.008 0.015 3 x 1x240 mm 2 Al 6/10 kV, delta 0.003 0.003 3 x 1x630 mm 2 Al 6/10 kV, delta
0,031 | 0.031 | 0.005 3x240 mm 2 Cu 6/10 kV 0.008 0.015 3 x 1x240 mm 2 Al 6/10 kV, delta 0.003 0.003 3 x 1x630 mm 2 Al 6/10 kV, delta 0.022
3 x 1x800 mm | 3 x 1x800 mm | 3x240 mm 2 Cu 6/10 kV 0.008 0.015 3 x 1x240 mm 2 Al 6/10 kV, delta 0.003 0.003 3 x 1x630 mm 2 Al 6/10 kV, delta 0.022 0.031
2 | 2 | 6/10 kV 0.008 0.015 3 x 1x240 mm 2 Al 6/10 kV, delta 0.003 0.003 3 x 1x630 mm 2 Al 6/10 kV, delta 0.022 0.031 3 x 1x800 mm
Al 6/10 kV, driehoek | Al 6/10 kV, delta | kV 0.008 0.015 3 x 1x240 mm 2 Al 6/10 kV, delta 0.003 0.003 3 x 1x630 mm 2 Al 6/10 kV, delta 0.022 0.031 3 x 1x800 mm 2
0,036 | 0.036 | x 1x240 mm 2 Al 6/10 kV, delta 0.003 0.003 3 x 1x630 mm 2 Al 6/10 kV, delta 0.022 0.031 3 x 1x800 mm 2 Al 6/10 kV, delta
0,053 | 0.053 | 1x240 mm 2 Al 6/10 kV, delta 0.003 0.003 3 x 1x630 mm 2 Al 6/10 kV, delta 0.022 0.031 3 x 1x800 mm 2 Al 6/10 kV, delta 0.036
3 x 1x240 mm | 3 x 1x240 mm | mm 2 Al 6/10 kV, delta 0.003 0.003 3 x 1x630 mm 2 Al 6/10 kV, delta 0.022 0.031 3 x 1x800 mm 2 Al 6/10 kV, delta 0.036 0.053
2 | 2 | kV, delta 0.003 0.003 3 x 1x630 mm 2 Al 6/10 kV, delta 0.022 0.031 3 x 1x800 mm 2 Al 6/10 kV, delta 0.036 0.053 3 x 1x240 mm
Cu 6/10 kV, driehoek | Cu 6/10 kV, delta | delta 0.003 0.003 3 x 1x630 mm 2 Al 6/10 kV, delta 0.022 0.031 3 x 1x800 mm 2 Al 6/10 kV, delta 0.036 0.053 3 x 1x240 mm 2
0,009 | 0.009 | x 1x630 mm 2 Al 6/10 kV, delta 0.022 0.031 3 x 1x800 mm 2 Al 6/10 kV, delta 0.036 0.053 3 x 1x240 mm 2 Cu 6/10 kV, delta
0,010 | 0.010 | 1x630 mm 2 Al 6/10 kV, delta 0.022 0.031 3 x 1x800 mm 2 Al 6/10 kV, delta 0.036 0.053 3 x 1x240 mm 2 Cu 6/10 kV, delta 0.009
3 x 1x1000 mm | 3 x 1x1000 mm | mm 2 Al 6/10 kV, delta 0.022 0.031 3 x 1x800 mm 2 Al 6/10 kV, delta 0.036 0.053 3 x 1x240 mm 2 Cu 6/10 kV, delta 0.009 0.010
2 | 2 | kV, delta 0.022 0.031 3 x 1x800 mm 2 Al 6/10 kV, delta 0.036 0.053 3 x 1x240 mm 2 Cu 6/10 kV, delta 0.009 0.010 3 x 1x1000 mm
Cu 6/10 kV, driehoek | Cu 6/10 kV, delta | delta 0.022 0.031 3 x 1x800 mm 2 Al 6/10 kV, delta 0.036 0.053 3 x 1x240 mm 2 Cu 6/10 kV, delta 0.009 0.010 3 x 1x1000 mm 2
0,148 | 0.148 | x 1x800 mm 2 Al 6/10 kV, delta 0.036 0.053 3 x 1x240 mm 2 Cu 6/10 kV, delta 0.009 0.010 3 x 1x1000 mm 2 Cu 6/10 kV, delta
0,187 | 0.187 | 1x800 mm 2 Al 6/10 kV, delta 0.036 0.053 3 x 1x240 mm 2 Cu 6/10 kV, delta 0.009 0.010 3 x 1x1000 mm 2 Cu 6/10 kV, delta 0.148
3 x 1x1000 mm | 3 x 1x1000 mm | mm 2 Al 6/10 kV, delta 0.036 0.053 3 x 1x240 mm 2 Cu 6/10 kV, delta 0.009 0.010 3 x 1x1000 mm 2 Cu 6/10 kV, delta 0.148 0.187
2 | 2 | kV, delta 0.036 0.053 3 x 1x240 mm 2 Cu 6/10 kV, delta 0.009 0.010 3 x 1x1000 mm 2 Cu 6/10 kV, delta 0.148 0.187 3 x 1x1000 mm
Cu 6/10 kV, plat vlak | Cu 6/10 kV, flat surface | delta 0.036 0.053 3 x 1x240 mm 2 Cu 6/10 kV, delta 0.009 0.010 3 x 1x1000 mm 2 Cu 6/10 kV, delta 0.148 0.187 3 x 1x1000 mm 2
0,148 | 0.148 | 1x240 mm 2 Cu 6/10 kV, delta 0.009 0.010 3 x 1x1000 mm 2 Cu 6/10 kV, delta 0.148 0.187 3 x 1x1000 mm 2 Cu 6/10 kV, flat surface
0,037 | 0.037 | mm 2 Cu 6/10 kV, delta 0.009 0.010 3 x 1x1000 mm 2 Cu 6/10 kV, delta 0.148 0.187 3 x 1x1000 mm 2 Cu 6/10 kV, flat surface 0.148
Normale reactantie | Normal reactance | 2 Cu 6/10 kV, delta 0.009 0.010 3 x 1x1000 mm 2 Cu 6/10 kV, delta 0.148 0.187 3 x 1x1000 mm 2 Cu 6/10 kV, flat surface 0.148 0.037
De normale reactantie kan eenvoudig worden afgeleid uit de specificatie van de inductie in de brochure van de fabrikant. Deze is voor drie- en vieraderige kabels onafhankelijk van externe omstandigheden. Bij enkeladerige midden- en hoogspanningskabels is de ligging (driehoek of plat vlak) van belang. | The normal reactance can easily be derived from the induction specification in the manufacturer's brochure. This is independent of external conditions for three- and four-core cables. For single-core medium- and high-voltage cables, the configuration (triangle or flat surface) is important. | 6/10 kV, delta 0.009 0.010 3 x 1x1000 mm 2 Cu 6/10 kV, delta 0.148 0.187 3 x 1x1000 mm 2 Cu 6/10 kV, flat surface 0.148 0.037 Normal reactance
In het geval dat de inductie niet gegeven is, kan deze berekend worden. De inductie | In the event that the inductance is not provided, it can be calculated. The inductance | specification in the manufacturer's brochure. This is independent of external conditions for three- and four-core cables. For single-core medium- and high-voltage cables, the configuration (triangle or flat surface) is important.
L | L | cables. For single-core medium- and high-voltage cables, the configuration (triangle or flat surface) is important. In the event that the inductance is not provided, it can be calculated. The inductance
van een ideale ronde oneindig lange geleider, in het geval van twee parallelle geleiders, kan worden berekend volgens (Heinhold, 1999): | of an ideal round infinitely long conductor, in the case of two parallel conductors, can be calculated according to (Heinhold, 1999): | For single-core medium- and high-voltage cables, the configuration (triangle or flat surface) is important. In the event that the inductance is not provided, it can be calculated. The inductance L
[ | [ | not provided, it can be calculated. The inductance L of an ideal round infinitely long conductor, in the case of two parallel conductors, can be calculated according to (Heinhold, 1999):
8.10 | 8.10 | provided, it can be calculated. The inductance L of an ideal round infinitely long conductor, in the case of two parallel conductors, can be calculated according to (Heinhold, 1999): [
] | ] | it can be calculated. The inductance L of an ideal round infinitely long conductor, in the case of two parallel conductors, can be calculated according to (Heinhold, 1999): [ 8.10
waarin: | where: | can be calculated. The inductance L of an ideal round infinitely long conductor, in the case of two parallel conductors, can be calculated according to (Heinhold, 1999): [ 8.10 ]
µ | µ | be calculated. The inductance L of an ideal round infinitely long conductor, in the case of two parallel conductors, can be calculated according to (Heinhold, 1999): [ 8.10 ] where:
0 | 0 | calculated. The inductance L of an ideal round infinitely long conductor, in the case of two parallel conductors, can be calculated according to (Heinhold, 1999): [ 8.10 ] where: µ
permeabiliteitsconstante in vacuum: | permeability constant in vacuum: | The inductance L of an ideal round infinitely long conductor, in the case of two parallel conductors, can be calculated according to (Heinhold, 1999): [ 8.10 ] where: µ 0
µ | µ | an ideal round infinitely long conductor, in the case of two parallel conductors, can be calculated according to (Heinhold, 1999): [ 8.10 ] where: µ 0 permeability constant in vacuum:
0 | 0 | ideal round infinitely long conductor, in the case of two parallel conductors, can be calculated according to (Heinhold, 1999): [ 8.10 ] where: µ 0 permeability constant in vacuum: µ
round infinitely long conductor, in the case of two parallel conductors, can be calculated according to (Heinhold, 1999): [ 8.10 ] where: µ 0 permeability constant in vacuum: µ 0
-7 | -7 | long conductor, in the case of two parallel conductors, can be calculated according to (Heinhold, 1999): [ 8.10 ] where: µ 0 permeability constant in vacuum: µ 0 = 4π10
H/m | H/m | conductor, in the case of two parallel conductors, can be calculated according to (Heinhold, 1999): [ 8.10 ] where: µ 0 permeability constant in vacuum: µ 0 = 4π10 -7
s | s | in the case of two parallel conductors, can be calculated according to (Heinhold, 1999): [ 8.10 ] where: µ 0 permeability constant in vacuum: µ 0 = 4π10 -7 H/m
hartafstand van de geleiders in driehoeksformatie (mm) of | center-to-center distance of the conductors in triangular formation (mm) or | the case of two parallel conductors, can be calculated according to (Heinhold, 1999): [ 8.10 ] where: µ 0 permeability constant in vacuum: µ 0 = 4π10 -7 H/m s
3 | 3 | to (Heinhold, 1999): [ 8.10 ] where: µ 0 permeability constant in vacuum: µ 0 = 4π10 -7 H/m s center-to-center distance of the conductors in triangular formation (mm) or
√2 = 1.26 | √2 = 1.26 | (Heinhold, 1999): [ 8.10 ] where: µ 0 permeability constant in vacuum: µ 0 = 4π10 -7 H/m s center-to-center distance of the conductors in triangular formation (mm) or 3
maal de hartafstand van de geleiders in plat vlak | times the center-to-center distance of the conductors in a flat plane | 8.10 ] where: µ 0 permeability constant in vacuum: µ 0 = 4π10 -7 H/m s center-to-center distance of the conductors in triangular formation (mm) or 3 √2 = 1.26
ρ | ρ
geometrisch gemiddelde straal van de geleider: | geometric mean radius of the conductor: | 4π10 -7 H/m s center-to-center distance of the conductors in triangular formation (mm) or 3 √2 = 1.26 times the center-to-center distance of the conductors in a flat plane ρ
ρ | ρ | of the conductors in triangular formation (mm) or 3 √2 = 1.26 times the center-to-center distance of the conductors in a flat plane ρ geometric mean radius of the conductor:
the conductors in triangular formation (mm) or 3 √2 = 1.26 times the center-to-center distance of the conductors in a flat plane ρ geometric mean radius of the conductor: ρ
-1/4 | -1/4 | in triangular formation (mm) or 3 √2 = 1.26 times the center-to-center distance of the conductors in a flat plane ρ geometric mean radius of the conductor: ρ = e
d | d | triangular formation (mm) or 3 √2 = 1.26 times the center-to-center distance of the conductors in a flat plane ρ geometric mean radius of the conductor: ρ = e -1/4
c | c | formation (mm) or 3 √2 = 1.26 times the center-to-center distance of the conductors in a flat plane ρ geometric mean radius of the conductor: ρ = e -1/4 d
/2 ≅ 0,779 d | /2 ≅ 0.779 d | (mm) or 3 √2 = 1.26 times the center-to-center distance of the conductors in a flat plane ρ geometric mean radius of the conductor: ρ = e -1/4 d c
c | c
/2 mm | /2 mm | 1.26 times the center-to-center distance of the conductors in a flat plane ρ geometric mean radius of the conductor: ρ = e -1/4 d c /2 ≅ 0.779 d c
d | d | the center-to-center distance of the conductors in a flat plane ρ geometric mean radius of the conductor: ρ = e -1/4 d c /2 ≅ 0.779 d c /2 mm
c | c | center-to-center distance of the conductors in a flat plane ρ geometric mean radius of the conductor: ρ = e -1/4 d c /2 ≅ 0.779 d c /2 mm d
geleiderdiameter (mm) | conductor diameter (mm) | distance of the conductors in a flat plane ρ geometric mean radius of the conductor: ρ = e -1/4 d c /2 ≅ 0.779 d c /2 mm d c
Invullen van de permeabiliteitsconstante en de factor voor de geometrisch gemiddelde diameter van de geleider levert de vereenvoudigde formule: | Substituting the permeability constant and the factor for the geometric mean diameter of the conductor yields the simplified formula: | conductors in a flat plane ρ geometric mean radius of the conductor: ρ = e -1/4 d c /2 ≅ 0.779 d c /2 mm d c conductor diameter (mm)
mH/km | mH/km | ≅ 0.779 d c /2 mm d c conductor diameter (mm) Substituting the permeability constant and the factor for the geometric mean diameter of the conductor yields the simplified formula:
[ | [ | 0.779 d c /2 mm d c conductor diameter (mm) Substituting the permeability constant and the factor for the geometric mean diameter of the conductor yields the simplified formula: mH/km
8.11 | 8.11 | d c /2 mm d c conductor diameter (mm) Substituting the permeability constant and the factor for the geometric mean diameter of the conductor yields the simplified formula: mH/km [
] | ] | c /2 mm d c conductor diameter (mm) Substituting the permeability constant and the factor for the geometric mean diameter of the conductor yields the simplified formula: mH/km [ 8.11
Uiteindelijk wordt de normale reactantie berekend door de inductie te vermenigvuldigen met de hoekfrequentie: | Ultimately, the normal reactance is calculated by multiplying the inductance by the angular frequency: | /2 mm d c conductor diameter (mm) Substituting the permeability constant and the factor for the geometric mean diameter of the conductor yields the simplified formula: mH/km [ 8.11 ]
Ω/km | Ω/km | for the geometric mean diameter of the conductor yields the simplified formula: mH/km [ 8.11 ] Ultimately, the normal reactance is calculated by multiplying the inductance by the angular frequency:
[ | [ | the geometric mean diameter of the conductor yields the simplified formula: mH/km [ 8.11 ] Ultimately, the normal reactance is calculated by multiplying the inductance by the angular frequency: Ω/km
8.12 | 8.12 | geometric mean diameter of the conductor yields the simplified formula: mH/km [ 8.11 ] Ultimately, the normal reactance is calculated by multiplying the inductance by the angular frequency: Ω/km [
] | ] | mean diameter of the conductor yields the simplified formula: mH/km [ 8.11 ] Ultimately, the normal reactance is calculated by multiplying the inductance by the angular frequency: Ω/km [ 8.12
Dit geldt ook voor kabels met scherm en voor kabels waarvan de geleiderdoorsnede niet rond is. De normale impedantie kan ook worden berekend met behulp van een op finite-elementberekening gebaseerd elektromagnetisch veldsterkteprogramma. | This also applies to shielded cables and cables with non-circular conductor cross-sections. The normal impedance can also be calculated using an electromagnetic field strength program based on finite element analysis. | diameter of the conductor yields the simplified formula: mH/km [ 8.11 ] Ultimately, the normal reactance is calculated by multiplying the inductance by the angular frequency: Ω/km [ 8.12 ]
Normale capaciteit | Normal capacitance | This also applies to shielded cables and cables with non-circular conductor cross-sections. The normal impedance can also be calculated using an electromagnetic field strength program based on finite element analysis.
De capaciteit speelt voornamelijk een rol in de blindvermogenshuishouding. Hoe hoger het spanningsniveau, des te groter is de invloed. Ook bepaalt de capaciteit het diëlektrische verlies dat in verband met de warmteontwikkeling een beperkende factor is voor de maximale stroombelastbaarheid van kabels voor spanningsniveaus van 50 kV en hoger. In geval van zwevende MS-netten met een geïsoleerd sterpunt speelt de capaciteit een rol bij de grootte van de stroom in geval van een fase-aardsluiting. Bij LS-kabels is de capaciteit voor de meeste loadflow- en kortsluitberekeningen niet belangrijk. | The capacitance mainly plays a role in reactive power management. The higher the voltage level, the greater the influence. Capacitance also determines the dielectric loss, which, due to heat development, is a limiting factor for the maximum current-carrying capacity of cables at voltage levels of 50 kV and higher. In the case of floating medium voltage networks with an isolated neutral point, capacitance affects the magnitude of the current in the event of a phase-to-ground fault. For low voltage cables, capacitance is not important for most load flow and short-circuit calculations. | applies to shielded cables and cables with non-circular conductor cross-sections. The normal impedance can also be calculated using an electromagnetic field strength program based on finite element analysis. Normal capacitance
De normale capaciteit van kabels is doorgaans gespecificeerd door de kabelfabrikanten. Deze kan ook berekend worden met behulp van onderstaande formule voor enkeladerige kabels en meeraderige kabels met afzonderlijke schermen (Happoldt, 1978): | The normal capacitance of cables is typically specified by the cable manufacturers. It can also be calculated using the formula below for single-core cables and multi-core cables with separate screens (Happoldt, 1978): | point, capacitance affects the magnitude of the current in the event of a phase-to-ground fault. For low voltage cables, capacitance is not important for most load flow and short-circuit calculations.
μF/km | μF/km | capacitance of cables is typically specified by the cable manufacturers. It can also be calculated using the formula below for single-core cables and multi-core cables with separate screens (Happoldt, 1978):
[ | [ | of cables is typically specified by the cable manufacturers. It can also be calculated using the formula below for single-core cables and multi-core cables with separate screens (Happoldt, 1978): μF/km
8.13 | 8.13 | cables is typically specified by the cable manufacturers. It can also be calculated using the formula below for single-core cables and multi-core cables with separate screens (Happoldt, 1978): μF/km [
] | ] | is typically specified by the cable manufacturers. It can also be calculated using the formula below for single-core cables and multi-core cables with separate screens (Happoldt, 1978): μF/km [ 8.13
met: | with: | typically specified by the cable manufacturers. It can also be calculated using the formula below for single-core cables and multi-core cables with separate screens (Happoldt, 1978): μF/km [ 8.13 ]
ε | ε | specified by the cable manufacturers. It can also be calculated using the formula below for single-core cables and multi-core cables with separate screens (Happoldt, 1978): μF/km [ 8.13 ] with:
0 | 0 | by the cable manufacturers. It can also be calculated using the formula below for single-core cables and multi-core cables with separate screens (Happoldt, 1978): μF/km [ 8.13 ] with: ε
absolute permittiviteit: 8.854 · 10 | absolute permittivity: 8.854 · 10 | the cable manufacturers. It can also be calculated using the formula below for single-core cables and multi-core cables with separate screens (Happoldt, 1978): μF/km [ 8.13 ] with: ε 0
-12 | -12 | also be calculated using the formula below for single-core cables and multi-core cables with separate screens (Happoldt, 1978): μF/km [ 8.13 ] with: ε 0 absolute permittivity: 8.854 · 10
F/m | F/m | be calculated using the formula below for single-core cables and multi-core cables with separate screens (Happoldt, 1978): μF/km [ 8.13 ] with: ε 0 absolute permittivity: 8.854 · 10 -12
ε | ε | calculated using the formula below for single-core cables and multi-core cables with separate screens (Happoldt, 1978): μF/km [ 8.13 ] with: ε 0 absolute permittivity: 8.854 · 10 -12 F/m
r | r | using the formula below for single-core cables and multi-core cables with separate screens (Happoldt, 1978): μF/km [ 8.13 ] with: ε 0 absolute permittivity: 8.854 · 10 -12 F/m ε
relatieve permittiviteit van de isolatie (2,5 voor XLPE; 3,6 voor massa-geïmpregneerd papier) | relative permittivity of the insulation (2.5 for XLPE; 3.6 for mass-impregnated paper) | the formula below for single-core cables and multi-core cables with separate screens (Happoldt, 1978): μF/km [ 8.13 ] with: ε 0 absolute permittivity: 8.854 · 10 -12 F/m ε r
D | D | (Happoldt, 1978): μF/km [ 8.13 ] with: ε 0 absolute permittivity: 8.854 · 10 -12 F/m ε r relative permittivity of the insulation (2.5 for XLPE; 3.6 for mass-impregnated paper)
i | i | 1978): μF/km [ 8.13 ] with: ε 0 absolute permittivity: 8.854 · 10 -12 F/m ε r relative permittivity of the insulation (2.5 for XLPE; 3.6 for mass-impregnated paper) D
diameter over de isolatie, exclusief isolatiescherm (mm) | diameter over the insulation, excluding the insulation screen (mm) | μF/km [ 8.13 ] with: ε 0 absolute permittivity: 8.854 · 10 -12 F/m ε r relative permittivity of the insulation (2.5 for XLPE; 3.6 for mass-impregnated paper) D i
d | d | 8.854 · 10 -12 F/m ε r relative permittivity of the insulation (2.5 for XLPE; 3.6 for mass-impregnated paper) D i diameter over the insulation, excluding the insulation screen (mm)
c | c | · 10 -12 F/m ε r relative permittivity of the insulation (2.5 for XLPE; 3.6 for mass-impregnated paper) D i diameter over the insulation, excluding the insulation screen (mm) d
diameter over de geleider, inclusief geleiderscherm (mm) | diameter over the conductor, including the conductor screen (mm) | 10 -12 F/m ε r relative permittivity of the insulation (2.5 for XLPE; 3.6 for mass-impregnated paper) D i diameter over the insulation, excluding the insulation screen (mm) d c
De berekening voor kabels met gemeenschappelijk scherm en voor gordelkabels is vrij lastig. De literatuur (Heinhold, 1999) geeft een formule waar hier verder niet op ingegaan wordt. | The calculation for cables with a common screen and for belt cables is quite difficult. The literature (Heinhold, 1999) provides a formula that will not be further discussed here. | insulation (2.5 for XLPE; 3.6 for mass-impregnated paper) D i diameter over the insulation, excluding the insulation screen (mm) d c diameter over the conductor, including the conductor screen (mm)
8.2.2 Inverse impedantie | 8.2.2 Inverse Impedance | (mm) The calculation for cables with a common screen and for belt cables is quite difficult. The literature (Heinhold, 1999) provides a formula that will not be further discussed here.
De drieaderige kabels die in middenspanningsnetten worden toegepast zijn altijd driefasensymmetrisch opgebouwd. Dat heeft tot gevolg dat de inverse impedantie ( | The three-core cables used in medium voltage networks are always constructed in a three-phase symmetrical manner. As a result, the inverse impedance | for cables with a common screen and for belt cables is quite difficult. The literature (Heinhold, 1999) provides a formula that will not be further discussed here. 8.2.2 Inverse Impedance
Z | Z | not be further discussed here. 8.2.2 Inverse Impedance The three-core cables used in medium voltage networks are always constructed in a three-phase symmetrical manner. As a result, the inverse impedance
2 | 2 | be further discussed here. 8.2.2 Inverse Impedance The three-core cables used in medium voltage networks are always constructed in a three-phase symmetrical manner. As a result, the inverse impedance Z
) gelijk is aan de normale impedantie ( | ) is equal to the normal impedance ( | further discussed here. 8.2.2 Inverse Impedance The three-core cables used in medium voltage networks are always constructed in a three-phase symmetrical manner. As a result, the inverse impedance Z 2
Z | Z | cables used in medium voltage networks are always constructed in a three-phase symmetrical manner. As a result, the inverse impedance Z 2 ) is equal to the normal impedance (
1 | 1 | used in medium voltage networks are always constructed in a three-phase symmetrical manner. As a result, the inverse impedance Z 2 ) is equal to the normal impedance ( Z
). Een circuit met drie enkelfasige kabels die in driehoekformatie zijn gelegd is ook altijd driefasensymmetrisch. Indien het circuit bestaat uit drie enkelfasige kabels in plat vlak is dat niet het geval. Ook laagspanningskabels met drie fasegeleiders en een nulgeleider zijn niet zuiver driefasensymmetrisch. De afwijkingen van het ideale beeld zijn gering en voldoende klein om aan te nemen dat voor de meeste toepassingen, zoals loadflow- en kortsluitberekeningen, de inverse impedantie gelijk genomen mag worden aan de normale impedantie. Bij alle kabelverbindingen wordt daar dan ook van uit gegaan. | ). A circuit with three single-phase cables laid in a triangular formation is also always three-phase symmetrical. If the circuit consists of three single-phase cables laid flat, this is not the case. Low-voltage cables with three phase conductors and a neutral conductor are also not purely three-phase symmetrical. The deviations from the ideal scenario are minor and small enough to assume that for most applications, such as load flow and short-circuit calculations, the inverse impedance can be considered equal to the normal impedance. This assumption is made for all cable connections. | in medium voltage networks are always constructed in a three-phase symmetrical manner. As a result, the inverse impedance Z 2 ) is equal to the normal impedance ( Z 1
8.2.3 Verlies | 8.2.3 Loss | that for most applications, such as load flow and short-circuit calculations, the inverse impedance can be considered equal to the normal impedance. This assumption is made for all cable connections.
Het verlies in een kabel is opgebouwd uit twee componenten. Het grootste deel wordt veroorzaakt door het stroomtransport en is recht evenredig met de weerstand van de kabel: | The loss in a cable is composed of two components. The majority is caused by the current transport and is directly proportional to the resistance of the cable: | most applications, such as load flow and short-circuit calculations, the inverse impedance can be considered equal to the normal impedance. This assumption is made for all cable connections. 8.2.3 Loss
[ | [ | 8.2.3 Loss The loss in a cable is composed of two components. The majority is caused by the current transport and is directly proportional to the resistance of the cable:
8.14 | 8.14 | Loss The loss in a cable is composed of two components. The majority is caused by the current transport and is directly proportional to the resistance of the cable: [
] | ] | The loss in a cable is composed of two components. The majority is caused by the current transport and is directly proportional to the resistance of the cable: [ 8.14
Het tweede deel is het diëlektrische verlies en wordt veroorzaakt door het wisselende elektrische veld in de isolatie. Het verlies wordt alleen berekend voor afgeschermde kabels en is recht evenredig met de capaciteit: | The second part is the dielectric loss and is caused by the alternating electric field in the insulation. The loss is only calculated for shielded cables and is directly proportional to the capacitance: | loss in a cable is composed of two components. The majority is caused by the current transport and is directly proportional to the resistance of the cable: [ 8.14 ]
[ | [ | is the dielectric loss and is caused by the alternating electric field in the insulation. The loss is only calculated for shielded cables and is directly proportional to the capacitance:
8.15 | 8.15 | the dielectric loss and is caused by the alternating electric field in the insulation. The loss is only calculated for shielded cables and is directly proportional to the capacitance: [
] | ] | dielectric loss and is caused by the alternating electric field in the insulation. The loss is only calculated for shielded cables and is directly proportional to the capacitance: [ 8.15
Hierin is tan(δ) de verliesfactor van de isolatie. Waardes voor veel voorkomende isolatiematerialen zijn opgenomen in de norm IEC 60287. | Here, tan(δ) is the loss factor of the insulation. Values for common insulation materials are included in the IEC 60287 standard. | loss and is caused by the alternating electric field in the insulation. The loss is only calculated for shielded cables and is directly proportional to the capacitance: [ 8.15 ]
Het diëlektrische verlies wordt bij netberekeningen meestal verwaarloosd. Voor hoogspanningskabels heeft het invloed op de temperatuur en daarmee op de stroombelastbaarheid. | Dielectric loss is usually neglected in network calculations. For high-voltage cables, it affects the temperature and thereby the current-carrying capacity. | is directly proportional to the capacitance: [ 8.15 ] Here, tan(δ) is the loss factor of the insulation. Values for common insulation materials are included in the IEC 60287 standard.
8.2.4 Maximale stroombelastbaarheid | 8.2.4 Maximum current-carrying capacity | common insulation materials are included in the IEC 60287 standard. Dielectric loss is usually neglected in network calculations. For high-voltage cables, it affects the temperature and thereby the current-carrying capacity.
De maximale stroombelastbaarheid van kabels is sterk afhankelijk van een aantal omgevingsfactoren (zie paragraaf 4.1.5). De belangrijkste invloed hebben de specifieke warmteweerstand van de bodem, de bodemtemperatuur en de opwarming door parallelle kabelcircuits en warme leidingen. Ook wegboringen hebben slechte thermische eigenschappen en moeten apart worden bekeken. De methode om de maximale stroombelastbaarheid te berekenen is vastgelegd in de internationale norm IEC 60287. Bij het gebruik van deze berekening moet rekening worden gehouden met de 'hot spot', dat wil zeggen die plek in de totale kabelverbinding met de hoogste specifieke warmteweerstand en de hoogste bodemtemperatuur. | The maximum current-carrying capacity of cables is highly dependent on several environmental factors (see paragraph 4.1.5). The most significant influences are the specific thermal resistivity of the soil, the soil temperature, and the heating caused by parallel cable circuits and hot pipes. Additionally, road crossings have poor thermal properties and must be considered separately. The method for calculating the maximum current-carrying capacity is established in the international standard IEC 60287. When using this calculation, the 'hot spot' must be taken into account, which is the location in the entire cable connection with the highest specific thermal resistivity and the highest soil temperature. | included in the IEC 60287 standard. Dielectric loss is usually neglected in network calculations. For high-voltage cables, it affects the temperature and thereby the current-carrying capacity. 8.2.4 Maximum current-carrying capacity
Indien de constructiegegevens van de kabel niet bekend zijn en men genoegen neemt met een vlottere benadering, kan uitgegaan worden van de door de fabrikant (of in een norm) gespecificeerde nominale belastbaarheid. Hierop kan in geval van afwijkende liggingomstandigheid een aantal correctiefactoren worden toegepast. De correctiefactoren worden vaak in de brochure van de fabrikant vermeld. Ook kunnen deze aan een norm, zoals NEN 1010 worden ontleend. | If the construction data of the cable is not known and a quicker approximation is acceptable, the nominal load capacity specified by the manufacturer (or in a standard) can be used. In the case of different laying conditions, several correction factors can be applied to this. The correction factors are often listed in the manufacturer's brochure. They can also be derived from a standard, such as NEN 1010. | this calculation, the 'hot spot' must be taken into account, which is the location in the entire cable connection with the highest specific thermal resistivity and the highest soil temperature.
Er zijn correctiefactoren voor afwijkende omstandigheden bij ondergrondse en bovengrondse installatie. Voor ondergrondse installatie zijn er correctiefactoren voor afwijkingen in: | There are correction factors for abnormal conditions in underground and above-ground installations. For underground installations, there are correction factors for deviations in: | several correction factors can be applied to this. The correction factors are often listed in the manufacturer's brochure. They can also be derived from a standard, such as NEN 1010.
bodemtemperatuur | bodemtemperatuur | derived from a standard, such as NEN 1010. There are correction factors for abnormal conditions in underground and above-ground installations. For underground installations, there are correction factors for deviations in:
liggingdiepte | liggingdiepte | from a standard, such as NEN 1010. There are correction factors for abnormal conditions in underground and above-ground installations. For underground installations, there are correction factors for deviations in: bodemtemperatuur
ligging is een buis of direct in de grond | location is a pipe or directly in the ground | a standard, such as NEN 1010. There are correction factors for abnormal conditions in underground and above-ground installations. For underground installations, there are correction factors for deviations in: bodemtemperatuur liggingdiepte
specifieke thermische weerstand van de grond | specific thermal resistivity of the soil | factors for abnormal conditions in underground and above-ground installations. For underground installations, there are correction factors for deviations in: bodemtemperatuur liggingdiepte location is a pipe or directly in the ground
meerdere parallelle circuits in hetzelfde vlak | multiple parallel circuits in the same plane | and above-ground installations. For underground installations, there are correction factors for deviations in: bodemtemperatuur liggingdiepte location is a pipe or directly in the ground specific thermal resistivity of the soil
Voor bovengrondse installatie zijn er correctiefactoren voor afwijkingen in: | For above-ground installation, there are correction factors for deviations in: | are correction factors for deviations in: bodemtemperatuur liggingdiepte location is a pipe or directly in the ground specific thermal resistivity of the soil multiple parallel circuits in the same plane
luchttemperatuur | luchttemperatuur | a pipe or directly in the ground specific thermal resistivity of the soil multiple parallel circuits in the same plane For above-ground installation, there are correction factors for deviations in:
zoninstraling en kleur van de buitenmantel | solar radiation and color of the outer sheath | pipe or directly in the ground specific thermal resistivity of the soil multiple parallel circuits in the same plane For above-ground installation, there are correction factors for deviations in: luchttemperatuur
installatiemethode en meerdere parallelle circuits | installation method and multiple parallel circuits | resistivity of the soil multiple parallel circuits in the same plane For above-ground installation, there are correction factors for deviations in: luchttemperatuur solar radiation and color of the outer sheath
Voor andere afwijkingen moet een specifieke berekening volgens IEC 60287 worden uitgevoerd. De correctiefactoren uit de NEN 1010 zijn toepasbaar voor de genoemde situaties en geven een voldoende nauwkeurig resultaat. Hoewel de norm NEN 1010 is geschreven voor laagspanningskabels, zijn de correctiefactoren uit die norm ook toepasbaar voor midden- en hoogspanningskabels, want warmtetechnisch bekeken heeft het spanningsniveau geen invloed. | For other deviations, a specific calculation according to IEC 60287 must be performed. The correction factors from NEN 1010 are applicable to the mentioned situations and provide a sufficiently accurate result. Although the NEN 1010 standard is written for low-voltage cables, the correction factors from that standard are also applicable to medium- and high-voltage cables, as the voltage level has no influence from a thermal perspective. | circuits in the same plane For above-ground installation, there are correction factors for deviations in: luchttemperatuur solar radiation and color of the outer sheath installation method and multiple parallel circuits
De correctiefactor voor ondergrondse kabels is samengesteld uit separate factoren: | The correction factor for underground cables is composed of separate factors: | is written for low-voltage cables, the correction factors from that standard are also applicable to medium- and high-voltage cables, as the voltage level has no influence from a thermal perspective.
f = fT • fL • fG • fc | f = fT • fL • fG • fc | are also applicable to medium- and high-voltage cables, as the voltage level has no influence from a thermal perspective. The correction factor for underground cables is composed of separate factors:
[ | [ | the voltage level has no influence from a thermal perspective. The correction factor for underground cables is composed of separate factors: f = fT • fL • fG • fc
8.16 | 8.16 | voltage level has no influence from a thermal perspective. The correction factor for underground cables is composed of separate factors: f = fT • fL • fG • fc [
] | ] | level has no influence from a thermal perspective. The correction factor for underground cables is composed of separate factors: f = fT • fL • fG • fc [ 8.16
Hierin zijn: | These are: | has no influence from a thermal perspective. The correction factor for underground cables is composed of separate factors: f = fT • fL • fG • fc [ 8.16 ]
f | f | influence from a thermal perspective. The correction factor for underground cables is composed of separate factors: f = fT • fL • fG • fc [ 8.16 ] These are:
T | T | from a thermal perspective. The correction factor for underground cables is composed of separate factors: f = fT • fL • fG • fc [ 8.16 ] These are: f
correctiefactor voor afwijkende bodemtemperatuur | correction factor for deviating soil temperature | a thermal perspective. The correction factor for underground cables is composed of separate factors: f = fT • fL • fG • fc [ 8.16 ] These are: f T
f | f | for underground cables is composed of separate factors: f = fT • fL • fG • fc [ 8.16 ] These are: f T correction factor for deviating soil temperature
L | L | underground cables is composed of separate factors: f = fT • fL • fG • fc [ 8.16 ] These are: f T correction factor for deviating soil temperature f
correctiefactor voor afwijkende liggingdiepte | correction factor for deviating burial depth | cables is composed of separate factors: f = fT • fL • fG • fc [ 8.16 ] These are: f T correction factor for deviating soil temperature f L
f | f | f = fT • fL • fG • fc [ 8.16 ] These are: f T correction factor for deviating soil temperature f L correction factor for deviating burial depth
G | G
correctiefactor voor afwijkende thermische weerstand | correction factor for deviating thermal resistance | fT • fL • fG • fc [ 8.16 ] These are: f T correction factor for deviating soil temperature f L correction factor for deviating burial depth f G
f | f | fc [ 8.16 ] These are: f T correction factor for deviating soil temperature f L correction factor for deviating burial depth f G correction factor for deviating thermal resistance
c | c | [ 8.16 ] These are: f T correction factor for deviating soil temperature f L correction factor for deviating burial depth f G correction factor for deviating thermal resistance f
correctiefactor voor meerdere parallelle circuits | correction factor for multiple parallel circuits | 8.16 ] These are: f T correction factor for deviating soil temperature f L correction factor for deviating burial depth f G correction factor for deviating thermal resistance f c
Het gebruik van de correctiefactoren wordt toegelicht aan de hand van een enkele ondergronds geïnstalleerde drieaderige Cu XLPE geïsoleerde kabel met een buitendiameter van 57 mm. De totale correctiefactor voor het omrekenen van de maximale stroombelastbaarheid, zoals opgegeven door de fabrikant, naar de maximale stroombelastbaarheid, die hoort bij afwijkende liggingomstandigheid, kan berekend worden met de correctiefactoren van de NEN 1010: | The use of the correction factors is explained using a single underground installed three-core Cu XLPE insulated cable with an outer diameter of 57 mm. The total correction factor for converting the maximum current-carrying capacity, as specified by the manufacturer, to the maximum current-carrying capacity that corresponds to deviating installation conditions, can be calculated using the correction factors from NEN 1010: | correction factor for deviating soil temperature f L correction factor for deviating burial depth f G correction factor for deviating thermal resistance f c correction factor for multiple parallel circuits
Tabel 8.3 Correctiefactoren voor afwijkende liggingsomstandigheden | Table 8.3 Correction Factors for Deviating Installation Conditions | the maximum current-carrying capacity, as specified by the manufacturer, to the maximum current-carrying capacity that corresponds to deviating installation conditions, can be calculated using the correction factors from NEN 1010:
Liggingomstandigheden | Liggingomstandigheden | manufacturer, to the maximum current-carrying capacity that corresponds to deviating installation conditions, can be calculated using the correction factors from NEN 1010: Table 8.3 Correction Factors for Deviating Installation Conditions
Fabrikant | Fabrikant | to the maximum current-carrying capacity that corresponds to deviating installation conditions, can be calculated using the correction factors from NEN 1010: Table 8.3 Correction Factors for Deviating Installation Conditions Liggingomstandigheden
Afwijkend | Afwijkend | the maximum current-carrying capacity that corresponds to deviating installation conditions, can be calculated using the correction factors from NEN 1010: Table 8.3 Correction Factors for Deviating Installation Conditions Liggingomstandigheden Fabrikant
Correctiefactor | Correctiefactor | maximum current-carrying capacity that corresponds to deviating installation conditions, can be calculated using the correction factors from NEN 1010: Table 8.3 Correction Factors for Deviating Installation Conditions Liggingomstandigheden Fabrikant Afwijkend
Bodemtemperatuur: | Soil temperature: | current-carrying capacity that corresponds to deviating installation conditions, can be calculated using the correction factors from NEN 1010: Table 8.3 Correction Factors for Deviating Installation Conditions Liggingomstandigheden Fabrikant Afwijkend Correctiefactor
20 °C | 68 °F | that corresponds to deviating installation conditions, can be calculated using the correction factors from NEN 1010: Table 8.3 Correction Factors for Deviating Installation Conditions Liggingomstandigheden Fabrikant Afwijkend Correctiefactor Soil temperature:
25 °C | 77 °F | to deviating installation conditions, can be calculated using the correction factors from NEN 1010: Table 8.3 Correction Factors for Deviating Installation Conditions Liggingomstandigheden Fabrikant Afwijkend Correctiefactor Soil temperature: 68 °F
f | f | installation conditions, can be calculated using the correction factors from NEN 1010: Table 8.3 Correction Factors for Deviating Installation Conditions Liggingomstandigheden Fabrikant Afwijkend Correctiefactor Soil temperature: 68 °F 77 °F
T | T | conditions, can be calculated using the correction factors from NEN 1010: Table 8.3 Correction Factors for Deviating Installation Conditions Liggingomstandigheden Fabrikant Afwijkend Correctiefactor Soil temperature: 68 °F 77 °F f
can be calculated using the correction factors from NEN 1010: Table 8.3 Correction Factors for Deviating Installation Conditions Liggingomstandigheden Fabrikant Afwijkend Correctiefactor Soil temperature: 68 °F 77 °F f T
Installatiediepte: | Installation depth: | calculated using the correction factors from NEN 1010: Table 8.3 Correction Factors for Deviating Installation Conditions Liggingomstandigheden Fabrikant Afwijkend Correctiefactor Soil temperature: 68 °F 77 °F f T = 0.9632
1 m | 1 m | the correction factors from NEN 1010: Table 8.3 Correction Factors for Deviating Installation Conditions Liggingomstandigheden Fabrikant Afwijkend Correctiefactor Soil temperature: 68 °F 77 °F f T = 0.9632 Installation depth:
0,7 m | 0.7 m | factors from NEN 1010: Table 8.3 Correction Factors for Deviating Installation Conditions Liggingomstandigheden Fabrikant Afwijkend Correctiefactor Soil temperature: 68 °F 77 °F f T = 0.9632 Installation depth: 1 m
f | f | NEN 1010: Table 8.3 Correction Factors for Deviating Installation Conditions Liggingomstandigheden Fabrikant Afwijkend Correctiefactor Soil temperature: 68 °F 77 °F f T = 0.9632 Installation depth: 1 m 0.7 m
L | L | 1010: Table 8.3 Correction Factors for Deviating Installation Conditions Liggingomstandigheden Fabrikant Afwijkend Correctiefactor Soil temperature: 68 °F 77 °F f T = 0.9632 Installation depth: 1 m 0.7 m f
Table 8.3 Correction Factors for Deviating Installation Conditions Liggingomstandigheden Fabrikant Afwijkend Correctiefactor Soil temperature: 68 °F 77 °F f T = 0.9632 Installation depth: 1 m 0.7 m f L
Specifieke thermische grondweerstand: | Specific thermal soil resistance: | Correction Factors for Deviating Installation Conditions Liggingomstandigheden Fabrikant Afwijkend Correctiefactor Soil temperature: 68 °F 77 °F f T = 0.9632 Installation depth: 1 m 0.7 m f L = 1.0479
1 K·m/W | 1 K·m/W | Installation Conditions Liggingomstandigheden Fabrikant Afwijkend Correctiefactor Soil temperature: 68 °F 77 °F f T = 0.9632 Installation depth: 1 m 0.7 m f L = 1.0479 Specific thermal soil resistance:
2,5 K·m/W | 2.5 K·m/W | Liggingomstandigheden Fabrikant Afwijkend Correctiefactor Soil temperature: 68 °F 77 °F f T = 0.9632 Installation depth: 1 m 0.7 m f L = 1.0479 Specific thermal soil resistance: 1 K·m/W
f | f | Afwijkend Correctiefactor Soil temperature: 68 °F 77 °F f T = 0.9632 Installation depth: 1 m 0.7 m f L = 1.0479 Specific thermal soil resistance: 1 K·m/W 2.5 K·m/W
G | G | Correctiefactor Soil temperature: 68 °F 77 °F f T = 0.9632 Installation depth: 1 m 0.7 m f L = 1.0479 Specific thermal soil resistance: 1 K·m/W 2.5 K·m/W f
Soil temperature: 68 °F 77 °F f T = 0.9632 Installation depth: 1 m 0.7 m f L = 1.0479 Specific thermal soil resistance: 1 K·m/W 2.5 K·m/W f G
De totale correctiefactor wordt dan: | The total correction factor then becomes: | 68 °F 77 °F f T = 0.9632 Installation depth: 1 m 0.7 m f L = 1.0479 Specific thermal soil resistance: 1 K·m/W 2.5 K·m/W f G = 0.6662
f = f | f = f
T | T | depth: 1 m 0.7 m f L = 1.0479 Specific thermal soil resistance: 1 K·m/W 2.5 K·m/W f G = 0.6662 The total correction factor then becomes: f = f
• | • | 1 m 0.7 m f L = 1.0479 Specific thermal soil resistance: 1 K·m/W 2.5 K·m/W f G = 0.6662 The total correction factor then becomes: f = f T
f | f | m 0.7 m f L = 1.0479 Specific thermal soil resistance: 1 K·m/W 2.5 K·m/W f G = 0.6662 The total correction factor then becomes: f = f T •
L | L | 0.7 m f L = 1.0479 Specific thermal soil resistance: 1 K·m/W 2.5 K·m/W f G = 0.6662 The total correction factor then becomes: f = f T • f
• | • | m f L = 1.0479 Specific thermal soil resistance: 1 K·m/W 2.5 K·m/W f G = 0.6662 The total correction factor then becomes: f = f T • f L
f | f | f L = 1.0479 Specific thermal soil resistance: 1 K·m/W 2.5 K·m/W f G = 0.6662 The total correction factor then becomes: f = f T • f L •
G | G | L = 1.0479 Specific thermal soil resistance: 1 K·m/W 2.5 K·m/W f G = 0.6662 The total correction factor then becomes: f = f T • f L • f
• | •
f | f | 1.0479 Specific thermal soil resistance: 1 K·m/W 2.5 K·m/W f G = 0.6662 The total correction factor then becomes: f = f T • f L • f G •
c | c | Specific thermal soil resistance: 1 K·m/W 2.5 K·m/W f G = 0.6662 The total correction factor then becomes: f = f T • f L • f G • f
thermal soil resistance: 1 K·m/W 2.5 K·m/W f G = 0.6662 The total correction factor then becomes: f = f T • f L • f G • f c
• | • | resistance: 1 K·m/W 2.5 K·m/W f G = 0.6662 The total correction factor then becomes: f = f T • f L • f G • f c = 0.96
1,05 | 1.05 | 1 K·m/W 2.5 K·m/W f G = 0.6662 The total correction factor then becomes: f = f T • f L • f G • f c = 0.96 •
• | • | K·m/W 2.5 K·m/W f G = 0.6662 The total correction factor then becomes: f = f T • f L • f G • f c = 0.96 • 1.05
0,67 | 0.67 | 2.5 K·m/W f G = 0.6662 The total correction factor then becomes: f = f T • f L • f G • f c = 0.96 • 1.05 •
• | • | K·m/W f G = 0.6662 The total correction factor then becomes: f = f T • f L • f G • f c = 0.96 • 1.05 • 0.67
1,00 = 0,67 | 1.00 = 0.67 | f G = 0.6662 The total correction factor then becomes: f = f T • f L • f G • f c = 0.96 • 1.05 • 0.67 •
Bij een nominale continue stroom volgens de fabrikant van 380 A, wordt dan de nominale continue stroom voor de afwijkende liggingomstandigheid: 255 A. | With a nominal continuous current according to the manufacturer of 380 A, the nominal continuous current for the deviating location condition then becomes: 255 A. | 0.6662 The total correction factor then becomes: f = f T • f L • f G • f c = 0.96 • 1.05 • 0.67 • 1.00 = 0.67
8.2.5 Homopolaire impedantie | 8.2.5 Homopolar impedance | 0.67 • 1.00 = 0.67 With a nominal continuous current according to the manufacturer of 380 A, the nominal continuous current for the deviating location condition then becomes: 255 A.
De impedantie voor de homopolaire component bestaat uit de homopolaire weerstand en de homopolaire reactantie. De homopolaire impedantie wordt gebruikt voor alle berekeningen waar een retourstroom langs andere weg vloeit dan de fasengeleiders, zoals nulgeleiders, afscherming en aarde. De homopolaire impedantie van een circuit wordt bepaald door enerzijds de impedantie van de kabel zelf en anderzijds door de impedantie van het retourcircuit. In deze paragraaf wordt eerst ingegaan op de homopolaire impedantie van de kabel zelf. | The impedance for the homopolar component consists of the homopolar resistance and the homopolar reactance. The homopolar impedance is used for all calculations where a return current flows through paths other than the phase conductors, such as neutral conductors, shielding, and ground. The homopolar impedance of a circuit is determined by both the impedance of the cable itself and the impedance of the return circuit. This paragraph will first address the homopolar impedance of the cable itself.
Homopolaire weerstand | Homopolar resistance | circuit is determined by both the impedance of the cable itself and the impedance of the return circuit. This paragraph will first address the homopolar impedance of the cable itself.
In het algemeen geldt voor een kabel dat de homopolaire weerstand per fase gelijk is aan de wissel­stroom­weer­stand van de fasegeleider, zonder de invloed van het proximity-effect maar met de invloed van het skin-effect, waarbij de invloed van de retourgeleider wordt opgeteld (BICC, 1990): | In general, for a cable, the homopolar resistance per phase is equal to the alternating current resistance of the phase conductor, without the influence of the proximity effect but with the influence of the skin effect, with the influence of the return conductor added (BICC, 1990): | determined by both the impedance of the cable itself and the impedance of the return circuit. This paragraph will first address the homopolar impedance of the cable itself. Homopolar resistance
drieaderige kabels: drie maal de weerstand van de metalen afscherming, eventueel parallel aan de weerstand van de armering | three-core cables: three times the resistance of the metal shielding, possibly in parallel with the resistance of the armor | resistance of the phase conductor, without the influence of the proximity effect but with the influence of the skin effect, with the influence of the return conductor added (BICC, 1990):
SL-type kabels (elke ader separaat afgeschermd): de weerstand van een metalen afscherming, parallel met drie maal de weerstand van de armering. | SL-type cables (each conductor separately shielded): the resistance of a metal shielding, in parallel with three times the resistance of the armor. | effect, with the influence of the return conductor added (BICC, 1990): three-core cables: three times the resistance of the metal shielding, possibly in parallel with the resistance of the armor
enkeladerige kabels: de weerstand van de metalen afscherming (meestal geen armering). | single-core cables: the resistance of the metal shielding (usually no armor). | in parallel with the resistance of the armor SL-type cables (each conductor separately shielded): the resistance of a metal shielding, in parallel with three times the resistance of the armor.
Voor in Nederland veelvuldig gebruikte kabels betekent dit: | For cables frequently used in the Netherlands, this means: | conductor separately shielded): the resistance of a metal shielding, in parallel with three times the resistance of the armor. single-core cables: the resistance of the metal shielding (usually no armor).
LS drieaderige kabel met gezamenlijk scherm: | LS three-core cable with common shielding: | in parallel with three times the resistance of the armor. single-core cables: the resistance of the metal shielding (usually no armor). For cables frequently used in the Netherlands, this means:
R | R | resistance of the armor. single-core cables: the resistance of the metal shielding (usually no armor). For cables frequently used in the Netherlands, this means: LS three-core cable with common shielding:
0 | 0 | of the armor. single-core cables: the resistance of the metal shielding (usually no armor). For cables frequently used in the Netherlands, this means: LS three-core cable with common shielding: R
the armor. single-core cables: the resistance of the metal shielding (usually no armor). For cables frequently used in the Netherlands, this means: LS three-core cable with common shielding: R 0
F | F | single-core cables: the resistance of the metal shielding (usually no armor). For cables frequently used in the Netherlands, this means: LS three-core cable with common shielding: R 0 = R
+ 3(R | + 3(R | cables: the resistance of the metal shielding (usually no armor). For cables frequently used in the Netherlands, this means: LS three-core cable with common shielding: R 0 = R F
S | S | resistance of the metal shielding (usually no armor). For cables frequently used in the Netherlands, this means: LS three-core cable with common shielding: R 0 = R F + 3(R
//R | //R | of the metal shielding (usually no armor). For cables frequently used in the Netherlands, this means: LS three-core cable with common shielding: R 0 = R F + 3(R S
A | A | the metal shielding (usually no armor). For cables frequently used in the Netherlands, this means: LS three-core cable with common shielding: R 0 = R F + 3(R S //R
) | ) | metal shielding (usually no armor). For cables frequently used in the Netherlands, this means: LS three-core cable with common shielding: R 0 = R F + 3(R S //R A
LS vieraderige kabel met gezamenlijk scherm: | LS four-core cable with common shielding: | shielding (usually no armor). For cables frequently used in the Netherlands, this means: LS three-core cable with common shielding: R 0 = R F + 3(R S //R A )
R | R | frequently used in the Netherlands, this means: LS three-core cable with common shielding: R 0 = R F + 3(R S //R A ) LS four-core cable with common shielding:
0 | 0 | used in the Netherlands, this means: LS three-core cable with common shielding: R 0 = R F + 3(R S //R A ) LS four-core cable with common shielding: R
in the Netherlands, this means: LS three-core cable with common shielding: R 0 = R F + 3(R S //R A ) LS four-core cable with common shielding: R 0
F | F | Netherlands, this means: LS three-core cable with common shielding: R 0 = R F + 3(R S //R A ) LS four-core cable with common shielding: R 0 = R
+ 3(R | + 3(R | this means: LS three-core cable with common shielding: R 0 = R F + 3(R S //R A ) LS four-core cable with common shielding: R 0 = R F
S | S | LS three-core cable with common shielding: R 0 = R F + 3(R S //R A ) LS four-core cable with common shielding: R 0 = R F + 3(R
//R | //R | three-core cable with common shielding: R 0 = R F + 3(R S //R A ) LS four-core cable with common shielding: R 0 = R F + 3(R S
N | N | cable with common shielding: R 0 = R F + 3(R S //R A ) LS four-core cable with common shielding: R 0 = R F + 3(R S //R
//R | //R | with common shielding: R 0 = R F + 3(R S //R A ) LS four-core cable with common shielding: R 0 = R F + 3(R S //R N
A | A | common shielding: R 0 = R F + 3(R S //R A ) LS four-core cable with common shielding: R 0 = R F + 3(R S //R N //R
) | ) | shielding: R 0 = R F + 3(R S //R A ) LS four-core cable with common shielding: R 0 = R F + 3(R S //R N //R A
MS GPLK drieaderige kabel met gezamenlijk scherm: | MS GPLK three-core cable with common shielding: | R 0 = R F + 3(R S //R A ) LS four-core cable with common shielding: R 0 = R F + 3(R S //R N //R A )
R | R | S //R A ) LS four-core cable with common shielding: R 0 = R F + 3(R S //R N //R A ) MS GPLK three-core cable with common shielding:
0 | 0 | //R A ) LS four-core cable with common shielding: R 0 = R F + 3(R S //R N //R A ) MS GPLK three-core cable with common shielding: R
A ) LS four-core cable with common shielding: R 0 = R F + 3(R S //R N //R A ) MS GPLK three-core cable with common shielding: R 0
F | F | LS four-core cable with common shielding: R 0 = R F + 3(R S //R N //R A ) MS GPLK three-core cable with common shielding: R 0 = R
+ 3(R | + 3(R | four-core cable with common shielding: R 0 = R F + 3(R S //R N //R A ) MS GPLK three-core cable with common shielding: R 0 = R F
S | S | with common shielding: R 0 = R F + 3(R S //R N //R A ) MS GPLK three-core cable with common shielding: R 0 = R F + 3(R
//R | //R | common shielding: R 0 = R F + 3(R S //R N //R A ) MS GPLK three-core cable with common shielding: R 0 = R F + 3(R S
A | A | shielding: R 0 = R F + 3(R S //R N //R A ) MS GPLK three-core cable with common shielding: R 0 = R F + 3(R S //R
) | ) | R 0 = R F + 3(R S //R N //R A ) MS GPLK three-core cable with common shielding: R 0 = R F + 3(R S //R A
MS XLPE drieaderige kabel met gezamenlijk scherm: | MS XLPE three-core cable with common shielding: | 0 = R F + 3(R S //R N //R A ) MS GPLK three-core cable with common shielding: R 0 = R F + 3(R S //R A )
R | R | //R N //R A ) MS GPLK three-core cable with common shielding: R 0 = R F + 3(R S //R A ) MS XLPE three-core cable with common shielding:
0 | 0 | N //R A ) MS GPLK three-core cable with common shielding: R 0 = R F + 3(R S //R A ) MS XLPE three-core cable with common shielding: R
//R A ) MS GPLK three-core cable with common shielding: R 0 = R F + 3(R S //R A ) MS XLPE three-core cable with common shielding: R 0
F | F | ) MS GPLK three-core cable with common shielding: R 0 = R F + 3(R S //R A ) MS XLPE three-core cable with common shielding: R 0 = R
+ 3(R | + 3(R | MS GPLK three-core cable with common shielding: R 0 = R F + 3(R S //R A ) MS XLPE three-core cable with common shielding: R 0 = R F
S | S | three-core cable with common shielding: R 0 = R F + 3(R S //R A ) MS XLPE three-core cable with common shielding: R 0 = R F + 3(R
//R | //R | cable with common shielding: R 0 = R F + 3(R S //R A ) MS XLPE three-core cable with common shielding: R 0 = R F + 3(R S
A | A | with common shielding: R 0 = R F + 3(R S //R A ) MS XLPE three-core cable with common shielding: R 0 = R F + 3(R S //R
) | ) | common shielding: R 0 = R F + 3(R S //R A ) MS XLPE three-core cable with common shielding: R 0 = R F + 3(R S //R A
MS XLPE drieaderige kabel met afzonderlijke schermen: | MS XLPE three-core cable with separate shields: | shielding: R 0 = R F + 3(R S //R A ) MS XLPE three-core cable with common shielding: R 0 = R F + 3(R S //R A )
R | R | 3(R S //R A ) MS XLPE three-core cable with common shielding: R 0 = R F + 3(R S //R A ) MS XLPE three-core cable with separate shields:
0 | 0 | S //R A ) MS XLPE three-core cable with common shielding: R 0 = R F + 3(R S //R A ) MS XLPE three-core cable with separate shields: R
//R A ) MS XLPE three-core cable with common shielding: R 0 = R F + 3(R S //R A ) MS XLPE three-core cable with separate shields: R 0
F | F | ) MS XLPE three-core cable with common shielding: R 0 = R F + 3(R S //R A ) MS XLPE three-core cable with separate shields: R 0 = R
+ (R | + (R | MS XLPE three-core cable with common shielding: R 0 = R F + 3(R S //R A ) MS XLPE three-core cable with separate shields: R 0 = R F
S | S | three-core cable with common shielding: R 0 = R F + 3(R S //R A ) MS XLPE three-core cable with separate shields: R 0 = R F + (R
//3R | //3R | cable with common shielding: R 0 = R F + 3(R S //R A ) MS XLPE three-core cable with separate shields: R 0 = R F + (R S
A | A | with common shielding: R 0 = R F + 3(R S //R A ) MS XLPE three-core cable with separate shields: R 0 = R F + (R S //3R
) | ) | common shielding: R 0 = R F + 3(R S //R A ) MS XLPE three-core cable with separate shields: R 0 = R F + (R S //3R A
MS XLPE enkeladerige kabel met scherm: | MS XLPE single-core cable with shield: | shielding: R 0 = R F + 3(R S //R A ) MS XLPE three-core cable with separate shields: R 0 = R F + (R S //3R A )
R | R | + 3(R S //R A ) MS XLPE three-core cable with separate shields: R 0 = R F + (R S //3R A ) MS XLPE single-core cable with shield:
0 | 0 | 3(R S //R A ) MS XLPE three-core cable with separate shields: R 0 = R F + (R S //3R A ) MS XLPE single-core cable with shield: R
S //R A ) MS XLPE three-core cable with separate shields: R 0 = R F + (R S //3R A ) MS XLPE single-core cable with shield: R 0
F | F | A ) MS XLPE three-core cable with separate shields: R 0 = R F + (R S //3R A ) MS XLPE single-core cable with shield: R 0 = R
+ R | + R | ) MS XLPE three-core cable with separate shields: R 0 = R F + (R S //3R A ) MS XLPE single-core cable with shield: R 0 = R F
S | S | XLPE three-core cable with separate shields: R 0 = R F + (R S //3R A ) MS XLPE single-core cable with shield: R 0 = R F + R
waarin: | where: | three-core cable with separate shields: R 0 = R F + (R S //3R A ) MS XLPE single-core cable with shield: R 0 = R F + R S
R | R | cable with separate shields: R 0 = R F + (R S //3R A ) MS XLPE single-core cable with shield: R 0 = R F + R S where:
F | F | with separate shields: R 0 = R F + (R S //3R A ) MS XLPE single-core cable with shield: R 0 = R F + R S where: R
weerstand van de fasegeleider, gelijk aan: R'(1+y | resistance of the phase conductor, equal to: R'(1+y) | separate shields: R 0 = R F + (R S //3R A ) MS XLPE single-core cable with shield: R 0 = R F + R S where: R F
s | s | (R S //3R A ) MS XLPE single-core cable with shield: R 0 = R F + R S where: R F resistance of the phase conductor, equal to: R'(1+y)
) | ) | S //3R A ) MS XLPE single-core cable with shield: R 0 = R F + R S where: R F resistance of the phase conductor, equal to: R'(1+y) s
R | R | //3R A ) MS XLPE single-core cable with shield: R 0 = R F + R S where: R F resistance of the phase conductor, equal to: R'(1+y) s )
N | N | A ) MS XLPE single-core cable with shield: R 0 = R F + R S where: R F resistance of the phase conductor, equal to: R'(1+y) s ) R
weerstand van de nulgeleider | resistance of the neutral conductor | ) MS XLPE single-core cable with shield: R 0 = R F + R S where: R F resistance of the phase conductor, equal to: R'(1+y) s ) R N
R | R | with shield: R 0 = R F + R S where: R F resistance of the phase conductor, equal to: R'(1+y) s ) R N resistance of the neutral conductor
S | S | shield: R 0 = R F + R S where: R F resistance of the phase conductor, equal to: R'(1+y) s ) R N resistance of the neutral conductor R
weerstand van het scherm | resistance of the shield | R 0 = R F + R S where: R F resistance of the phase conductor, equal to: R'(1+y) s ) R N resistance of the neutral conductor R S
R | R | F + R S where: R F resistance of the phase conductor, equal to: R'(1+y) s ) R N resistance of the neutral conductor R S resistance of the shield
A | A | + R S where: R F resistance of the phase conductor, equal to: R'(1+y) s ) R N resistance of the neutral conductor R S resistance of the shield R
weerstand van de armering | resistance of the armor | R S where: R F resistance of the phase conductor, equal to: R'(1+y) s ) R N resistance of the neutral conductor R S resistance of the shield R A
In het algemeen geldt het volgende. Sommige drieaderige kabels zijn per fase uitgerust met een afzonderlijke afscherming die in staat is een éénfase kortsluit­stroom te geleiden. In dat geval moet de weerstand van die afscherming worden gebruikt. Wanneer er sprake is van één afscherming, gezamenlijk voor de drie geleiders, moet drie maal de weerstand van die afscherming worden gebruikt. Indien beide typen gecombineerd voorkomen, zoals een afscherming per fase en een gezamenlijke armering moet het voorbeeld van de SL-type kabel worden gebruikt. In principe moeten de weerstanden | In general, the following applies. Some three-core cables are equipped per phase with a separate shield capable of conducting a single-phase short-circuit current. In that case, the resistance of that shield must be used. When there is a single shield common to the three conductors, three times the resistance of that shield must be used. If both types are combined, such as a shield per phase and a common armor, the example of the SL-type cable should be used. In principle, the resistances must | F resistance of the phase conductor, equal to: R'(1+y) s ) R N resistance of the neutral conductor R S resistance of the shield R A resistance of the armor
R | R | used. If both types are combined, such as a shield per phase and a common armor, the example of the SL-type cable should be used. In principle, the resistances must
i | i | If both types are combined, such as a shield per phase and a common armor, the example of the SL-type cable should be used. In principle, the resistances must R
van alle individuele retourpaden separaat worden berekend en moet de equivalente weerstand van al deze parallel geschakelde retourpaden worden bepaald. De homopolaire weerstand is dan | calculated separately for all individual return paths, and the equivalent resistance of all these parallel-connected return paths must be determined. The homopolar resistance is then | both types are combined, such as a shield per phase and a common armor, the example of the SL-type cable should be used. In principle, the resistances must R i
R | R | the resistances must R i calculated separately for all individual return paths, and the equivalent resistance of all these parallel-connected return paths must be determined. The homopolar resistance is then
F | F | resistances must R i calculated separately for all individual return paths, and the equivalent resistance of all these parallel-connected return paths must be determined. The homopolar resistance is then R
plus deze waarde, vermenigvuldigd met 3. | plus this value, multiplied by 3. | must R i calculated separately for all individual return paths, and the equivalent resistance of all these parallel-connected return paths must be determined. The homopolar resistance is then R F
[ | [ | all individual return paths, and the equivalent resistance of all these parallel-connected return paths must be determined. The homopolar resistance is then R F plus this value, multiplied by 3.
8.17 | 8.17 | individual return paths, and the equivalent resistance of all these parallel-connected return paths must be determined. The homopolar resistance is then R F plus this value, multiplied by 3. [
] | ] | return paths, and the equivalent resistance of all these parallel-connected return paths must be determined. The homopolar resistance is then R F plus this value, multiplied by 3. [ 8.17
Hieruit blijkt dat de homopolaire weerstand nooit kleiner is dan de normale weerstand. | From this, it appears that the homopolar resistance is never smaller than the normal resistance. | paths, and the equivalent resistance of all these parallel-connected return paths must be determined. The homopolar resistance is then R F plus this value, multiplied by 3. [ 8.17 ]
Bijvoorbeeld, een MS XLPE drieaderige kabel met afzonderlijke schermen, kent de drie schermen en de armering als retourpaden. Invullen in bovenstaande vergelijking levert: | For example, an MS XLPE three-core cable with separate screens uses the three screens and the armor as return paths. Substituting into the above equation yields: | homopolar resistance is then R F plus this value, multiplied by 3. [ 8.17 ] From this, it appears that the homopolar resistance is never smaller than the normal resistance.
[ | [ | than the normal resistance. For example, an MS XLPE three-core cable with separate screens uses the three screens and the armor as return paths. Substituting into the above equation yields:
8.18 | 8.18 | the normal resistance. For example, an MS XLPE three-core cable with separate screens uses the three screens and the armor as return paths. Substituting into the above equation yields: [
] | ] | normal resistance. For example, an MS XLPE three-core cable with separate screens uses the three screens and the armor as return paths. Substituting into the above equation yields: [ 8.18
De weerstanden worden berekend uit het geleidende oppervlak van de doorsnede en de specifieke weerstand van de betreffende geleiders. Voor een scherm wordt het geleidende oppervlak berekend uit de diameter en de dikte. Voor afzonderlijke draden wordt de weerstand bepaald uit die van een enkele draad, gedeeld door het aantal draden en gecorrigeerd voor de spoed. Bij kabels met een meanderend scherm is de lengte van het scherm groter dan die van de totale kabel. | The resistances are calculated from the conductive cross-sectional area and the specific resistance of the respective conductors. For a screen, the conductive area is calculated from the diameter and thickness. For individual wires, the resistance is determined from that of a single wire, divided by the number of wires and corrected for the pitch. In cables with a meandering screen, the length of the screen is greater than that of the entire cable. | resistance. For example, an MS XLPE three-core cable with separate screens uses the three screens and the armor as return paths. Substituting into the above equation yields: [ 8.18 ]
De homopolaire weerstand is, net als de normale weerstand, afhankelijk van de kabeltemperatuur en kan berekend worden zoals aangegeven in paragraaf 8.2.1. | The homopolar resistance, like the normal resistance, depends on the cable temperature and can be calculated as indicated in paragraph 8.2.1. | divided by the number of wires and corrected for the pitch. In cables with a meandering screen, the length of the screen is greater than that of the entire cable.
Homopolaire inductie en reactantie | Homopolar induction and reactance | screen is greater than that of the entire cable. The homopolar resistance, like the normal resistance, depends on the cable temperature and can be calculated as indicated in paragraph 8.2.1.
De homopolaire reactantie van een kabel kan meestal niet uit de brochure van de fabrikant worden herleid. Dit komt doordat de homopolaire impedantie van een circuit in grote mate wordt beïnvloed door de impedantie van het retourpad. In dit geval kan de homopolaire impedantie worden bepaald met een op finite-elementberekening gebaseerd elektromagnetisch veldsterkteprogramma. | The homopolar reactance of a cable usually cannot be derived from the manufacturer's brochure. This is because the homopolar impedance of a circuit is greatly influenced by the impedance of the return path. In this case, the homopolar impedance can be determined using an electromagnetic field strength program based on finite element calculation. | that of the entire cable. The homopolar resistance, like the normal resistance, depends on the cable temperature and can be calculated as indicated in paragraph 8.2.1. Homopolar induction and reactance
Voor het geval dat het retourcircuit bestaat uit alleen de eigen nul, scherm en armering kan de homopolaire reactantie per fase van een enkeladerige kabel redelijk eenvoudig berekend worden. Door in de formule voor de berekening van de normale inductie twee maal de geleiderafstand te vervangen door de diameter van de metalen afscherming, ontstaat de formule voor de homopolaire inductie per fase. | In the case where the return circuit consists solely of the neutral, shield, and armor, the homopolar reactance per phase of a single-core cable can be calculated fairly easily. By replacing twice the conductor spacing in the formula for calculating normal inductance with the diameter of the metallic shielding, the formula for homopolar inductance per phase is obtained. | is greatly influenced by the impedance of the return path. In this case, the homopolar impedance can be determined using an electromagnetic field strength program based on finite element calculation.
[ | [ | easily. By replacing twice the conductor spacing in the formula for calculating normal inductance with the diameter of the metallic shielding, the formula for homopolar inductance per phase is obtained.
8.19 | 8.19 | By replacing twice the conductor spacing in the formula for calculating normal inductance with the diameter of the metallic shielding, the formula for homopolar inductance per phase is obtained. [
] | ] | replacing twice the conductor spacing in the formula for calculating normal inductance with the diameter of the metallic shielding, the formula for homopolar inductance per phase is obtained. [ 8.19
waarin: | in which: | twice the conductor spacing in the formula for calculating normal inductance with the diameter of the metallic shielding, the formula for homopolar inductance per phase is obtained. [ 8.19 ]
µ | µ | conductor spacing in the formula for calculating normal inductance with the diameter of the metallic shielding, the formula for homopolar inductance per phase is obtained. [ 8.19 ] in which:
0 | 0 | spacing in the formula for calculating normal inductance with the diameter of the metallic shielding, the formula for homopolar inductance per phase is obtained. [ 8.19 ] in which: µ
permeabiliteitconstante in vacuüm: | permeability constant in a vacuum: | in the formula for calculating normal inductance with the diameter of the metallic shielding, the formula for homopolar inductance per phase is obtained. [ 8.19 ] in which: µ 0
µ | µ | normal inductance with the diameter of the metallic shielding, the formula for homopolar inductance per phase is obtained. [ 8.19 ] in which: µ 0 permeability constant in a vacuum:
0 | 0 | inductance with the diameter of the metallic shielding, the formula for homopolar inductance per phase is obtained. [ 8.19 ] in which: µ 0 permeability constant in a vacuum: µ
with the diameter of the metallic shielding, the formula for homopolar inductance per phase is obtained. [ 8.19 ] in which: µ 0 permeability constant in a vacuum: µ 0
-7 | -7 | diameter of the metallic shielding, the formula for homopolar inductance per phase is obtained. [ 8.19 ] in which: µ 0 permeability constant in a vacuum: µ 0 = 4π10
H/m | H/m | of the metallic shielding, the formula for homopolar inductance per phase is obtained. [ 8.19 ] in which: µ 0 permeability constant in a vacuum: µ 0 = 4π10 -7
D | D | the metallic shielding, the formula for homopolar inductance per phase is obtained. [ 8.19 ] in which: µ 0 permeability constant in a vacuum: µ 0 = 4π10 -7 H/m
s | s | metallic shielding, the formula for homopolar inductance per phase is obtained. [ 8.19 ] in which: µ 0 permeability constant in a vacuum: µ 0 = 4π10 -7 H/m D
gemiddelde diameter van de metalen afscherming (mm) | average diameter of the metal shielding (mm) | shielding, the formula for homopolar inductance per phase is obtained. [ 8.19 ] in which: µ 0 permeability constant in a vacuum: µ 0 = 4π10 -7 H/m D s
ρ | ρ | phase is obtained. [ 8.19 ] in which: µ 0 permeability constant in a vacuum: µ 0 = 4π10 -7 H/m D s average diameter of the metal shielding (mm)
geometrisch gemiddelde straal van de geleider: | geometric mean radius of the conductor: | is obtained. [ 8.19 ] in which: µ 0 permeability constant in a vacuum: µ 0 = 4π10 -7 H/m D s average diameter of the metal shielding (mm) ρ
ρ = e | ρ = e | which: µ 0 permeability constant in a vacuum: µ 0 = 4π10 -7 H/m D s average diameter of the metal shielding (mm) ρ geometric mean radius of the conductor:
-1/4 | -1/4 | permeability constant in a vacuum: µ 0 = 4π10 -7 H/m D s average diameter of the metal shielding (mm) ρ geometric mean radius of the conductor: ρ = e
d | d | constant in a vacuum: µ 0 = 4π10 -7 H/m D s average diameter of the metal shielding (mm) ρ geometric mean radius of the conductor: ρ = e -1/4
c | c | in a vacuum: µ 0 = 4π10 -7 H/m D s average diameter of the metal shielding (mm) ρ geometric mean radius of the conductor: ρ = e -1/4 d
/2 | /2 | a vacuum: µ 0 = 4π10 -7 H/m D s average diameter of the metal shielding (mm) ρ geometric mean radius of the conductor: ρ = e -1/4 d c
≅ | ≅ | vacuum: µ 0 = 4π10 -7 H/m D s average diameter of the metal shielding (mm) ρ geometric mean radius of the conductor: ρ = e -1/4 d c /2
0,779 d | 0.779 d | µ 0 = 4π10 -7 H/m D s average diameter of the metal shielding (mm) ρ geometric mean radius of the conductor: ρ = e -1/4 d c /2 ≅
c | c
/2 | /2 | 4π10 -7 H/m D s average diameter of the metal shielding (mm) ρ geometric mean radius of the conductor: ρ = e -1/4 d c /2 ≅ 0.779 d c
mm | mm | -7 H/m D s average diameter of the metal shielding (mm) ρ geometric mean radius of the conductor: ρ = e -1/4 d c /2 ≅ 0.779 d c /2
d | d | H/m D s average diameter of the metal shielding (mm) ρ geometric mean radius of the conductor: ρ = e -1/4 d c /2 ≅ 0.779 d c /2 mm
c | c | D s average diameter of the metal shielding (mm) ρ geometric mean radius of the conductor: ρ = e -1/4 d c /2 ≅ 0.779 d c /2 mm d
geleiderdiameter (mm) | conductor diameter (mm) | s average diameter of the metal shielding (mm) ρ geometric mean radius of the conductor: ρ = e -1/4 d c /2 ≅ 0.779 d c /2 mm d c
Invullen van de permeabiliteitconstante en de factor voor de geometrisch gemiddelde diameter van de geleider levert de homopolaire inductie per fase van een enkeladerige kabel (BICC, 1990): | Substituting the permeability constant and the factor for the geometric mean diameter of the conductor yields the homopolar inductance per phase of a single-core cable (BICC, 1990): | of the metal shielding (mm) ρ geometric mean radius of the conductor: ρ = e -1/4 d c /2 ≅ 0.779 d c /2 mm d c conductor diameter (mm)
[ | [ | conductor diameter (mm) Substituting the permeability constant and the factor for the geometric mean diameter of the conductor yields the homopolar inductance per phase of a single-core cable (BICC, 1990):
8.20 | 8.20 | diameter (mm) Substituting the permeability constant and the factor for the geometric mean diameter of the conductor yields the homopolar inductance per phase of a single-core cable (BICC, 1990): [
] | ] | (mm) Substituting the permeability constant and the factor for the geometric mean diameter of the conductor yields the homopolar inductance per phase of a single-core cable (BICC, 1990): [ 8.20
Voor drieaderige kabels met een gezamenlijke afscherming kan de homopolaire inductie per fase berekend worden met behulp van onderstaande vergelijking. Hierin komt een factor 3 voor om de reactantie van het gezamenlijke scherm om te rekenen naar reactantie per fase. | For three-core cables with a common shielding, the homopolar inductance per phase can be calculated using the equation below. A factor of 3 is included to convert the reactance of the common shield to the reactance per phase. | Substituting the permeability constant and the factor for the geometric mean diameter of the conductor yields the homopolar inductance per phase of a single-core cable (BICC, 1990): [ 8.20 ]
[ | [ | homopolar inductance per phase can be calculated using the equation below. A factor of 3 is included to convert the reactance of the common shield to the reactance per phase.
8.21 | 8.21 | inductance per phase can be calculated using the equation below. A factor of 3 is included to convert the reactance of the common shield to the reactance per phase. [
] | ] | per phase can be calculated using the equation below. A factor of 3 is included to convert the reactance of the common shield to the reactance per phase. [ 8.21
waarin: | in which: | phase can be calculated using the equation below. A factor of 3 is included to convert the reactance of the common shield to the reactance per phase. [ 8.21 ]
D | D | be calculated using the equation below. A factor of 3 is included to convert the reactance of the common shield to the reactance per phase. [ 8.21 ] in which:
s | s | calculated using the equation below. A factor of 3 is included to convert the reactance of the common shield to the reactance per phase. [ 8.21 ] in which: D
gemiddelde diameter van de metalen afscherming over de gezamenlijke aders (mm) | average diameter of the metal shielding over the combined conductors (mm) | using the equation below. A factor of 3 is included to convert the reactance of the common shield to the reactance per phase. [ 8.21 ] in which: D s
gmd | gmd | convert the reactance of the common shield to the reactance per phase. [ 8.21 ] in which: D s average diameter of the metal shielding over the combined conductors (mm)
geometrische gemiddelde diameter van de geleiders in de kabel (mm). | geometric mean diameter of the conductors in the cable (mm). | the reactance of the common shield to the reactance per phase. [ 8.21 ] in which: D s average diameter of the metal shielding over the combined conductors (mm) gmd
De waarde van | The value of | phase. [ 8.21 ] in which: D s average diameter of the metal shielding over the combined conductors (mm) gmd geometric mean diameter of the conductors in the cable (mm).
gmd | gmd | ] in which: D s average diameter of the metal shielding over the combined conductors (mm) gmd geometric mean diameter of the conductors in the cable (mm). The value of
mag gelijk genomen worden aan 0,75 maal | may be taken as 0.75 times | in which: D s average diameter of the metal shielding over the combined conductors (mm) gmd geometric mean diameter of the conductors in the cable (mm). The value of gmd
D | D | of the metal shielding over the combined conductors (mm) gmd geometric mean diameter of the conductors in the cable (mm). The value of gmd may be taken as 0.75 times
ogg | ogg | the metal shielding over the combined conductors (mm) gmd geometric mean diameter of the conductors in the cable (mm). The value of gmd may be taken as 0.75 times D
, de diameter van de cirkel die raakt aan de drie gezamenlijke geleiders in de kabel, ervan uitgaande dat de geleiders cirkelvormig zijn (BICC, 1990). De diameter van de cirkel over de samengeslagen geleiders kan als volgt berekend worden uit de diameter over de geïsoleerde geleider (D | , the diameter of the circle that touches the three combined conductors in the cable, assuming the conductors are circular (BICC, 1990). The diameter of the circle over the bundled conductors can be calculated as follows from the diameter over the insulated conductor (D | metal shielding over the combined conductors (mm) gmd geometric mean diameter of the conductors in the cable (mm). The value of gmd may be taken as 0.75 times D ogg
i | i | cable, assuming the conductors are circular (BICC, 1990). The diameter of the circle over the bundled conductors can be calculated as follows from the diameter over the insulated conductor (D
) en de geleiderdiameter (d | ) and the conductor diameter (d | assuming the conductors are circular (BICC, 1990). The diameter of the circle over the bundled conductors can be calculated as follows from the diameter over the insulated conductor (D i
c | c | 1990). The diameter of the circle over the bundled conductors can be calculated as follows from the diameter over the insulated conductor (D i ) and the conductor diameter (d
): | ): | The diameter of the circle over the bundled conductors can be calculated as follows from the diameter over the insulated conductor (D i ) and the conductor diameter (d c
mm | mm | diameter of the circle over the bundled conductors can be calculated as follows from the diameter over the insulated conductor (D i ) and the conductor diameter (d c ):
[ | [ | of the circle over the bundled conductors can be calculated as follows from the diameter over the insulated conductor (D i ) and the conductor diameter (d c ): mm
8.22 | 8.22 | the circle over the bundled conductors can be calculated as follows from the diameter over the insulated conductor (D i ) and the conductor diameter (d c ): mm [
] | ] | circle over the bundled conductors can be calculated as follows from the diameter over the insulated conductor (D i ) and the conductor diameter (d c ): mm [ 8.22
Uiteindelijk wordt de normale reactantie berekend door de inductie te vermenigvuldigen met de hoekfrequentie: | Ultimately, the normal reactance is calculated by multiplying the inductance by the angular frequency: | over the bundled conductors can be calculated as follows from the diameter over the insulated conductor (D i ) and the conductor diameter (d c ): mm [ 8.22 ]
Ω/km | Ω/km | insulated conductor (D i ) and the conductor diameter (d c ): mm [ 8.22 ] Ultimately, the normal reactance is calculated by multiplying the inductance by the angular frequency:
[ | [ | conductor (D i ) and the conductor diameter (d c ): mm [ 8.22 ] Ultimately, the normal reactance is calculated by multiplying the inductance by the angular frequency: Ω/km
8.23 | 8.23 | (D i ) and the conductor diameter (d c ): mm [ 8.22 ] Ultimately, the normal reactance is calculated by multiplying the inductance by the angular frequency: Ω/km [
] | ] | i ) and the conductor diameter (d c ): mm [ 8.22 ] Ultimately, the normal reactance is calculated by multiplying the inductance by the angular frequency: Ω/km [ 8.23
Indien de kabel geen scherm heeft, zoals bij sommige LS-kabels, kan de homopolaire impedantie worden berekend vanuit de resultaten van een finite-elementberekening met een elektromagnetisch veldsterkteprogramma. Dit geldt ook voor kabels waarvan de geleiderdoorsnede niet rond is. | If the cable does not have a shield, as is the case with some low-voltage cables, the homopolar impedance can be calculated from the results of a finite element analysis using an electromagnetic field strength program. This also applies to cables whose conductor cross-section is not round. | ) and the conductor diameter (d c ): mm [ 8.22 ] Ultimately, the normal reactance is calculated by multiplying the inductance by the angular frequency: Ω/km [ 8.23 ]
Homopolaire capaciteit | Homopolar capacitance | homopolar impedance can be calculated from the results of a finite element analysis using an electromagnetic field strength program. This also applies to cables whose conductor cross-section is not round.
De kleine afstanden tussen de geleiders onderling in een kabel en tussen geleiders en afscherming en de diëlektrische constante van het isolatiemedium zorgen ervoor dat de capaciteit groter is dan bij bovengrondse lijnen. De kabelcapaciteiten liggen in de grootte van 0,1 tot 1,2 µF/km. De homopolaire capaciteit is afhankelijk van de constructie van de kabel. | The small distances between the conductors within a cable and between the conductors and shielding, as well as the dielectric constant of the insulating medium, result in a higher capacitance compared to overhead lines. Cable capacitance ranges from 0.1 to 1.2 µF/km. The homopolar capacitance depends on the construction of the cable. | can be calculated from the results of a finite element analysis using an electromagnetic field strength program. This also applies to cables whose conductor cross-section is not round. Homopolar capacitance
Figuur 8.1 Capaciteiten in diverse kabelsoorten | Figure 8.1 Capacitances in various types of cables | the insulating medium, result in a higher capacitance compared to overhead lines. Cable capacitance ranges from 0.1 to 1.2 µF/km. The homopolar capacitance depends on the construction of the cable.
Tabel 8.4 geeft een benadering van de normale capaciteit ( | Table 8.4 provides an approximation of the normal capacitance | compared to overhead lines. Cable capacitance ranges from 0.1 to 1.2 µF/km. The homopolar capacitance depends on the construction of the cable. Figure 8.1 Capacitances in various types of cables
C | C | to 1.2 µF/km. The homopolar capacitance depends on the construction of the cable. Figure 8.1 Capacitances in various types of cables Table 8.4 provides an approximation of the normal capacitance
1 | 1 | 1.2 µF/km. The homopolar capacitance depends on the construction of the cable. Figure 8.1 Capacitances in various types of cables Table 8.4 provides an approximation of the normal capacitance C
) en de homopolaire capaciteit ( | ) and the homopolar capacitance ( | µF/km. The homopolar capacitance depends on the construction of the cable. Figure 8.1 Capacitances in various types of cables Table 8.4 provides an approximation of the normal capacitance C 1
C | C | the construction of the cable. Figure 8.1 Capacitances in various types of cables Table 8.4 provides an approximation of the normal capacitance C 1 ) and the homopolar capacitance (
0 | 0 | construction of the cable. Figure 8.1 Capacitances in various types of cables Table 8.4 provides an approximation of the normal capacitance C 1 ) and the homopolar capacitance ( C
) voor de kabelsoorten van figuur 8.1 (Happoldt, 1978). In deze tabel is | ) for the cable types in figure 8.1 (Happoldt, 1978). In this table, | of the cable. Figure 8.1 Capacitances in various types of cables Table 8.4 provides an approximation of the normal capacitance C 1 ) and the homopolar capacitance ( C 0
C | C | provides an approximation of the normal capacitance C 1 ) and the homopolar capacitance ( C 0 ) for the cable types in figure 8.1 (Happoldt, 1978). In this table,
E | E | an approximation of the normal capacitance C 1 ) and the homopolar capacitance ( C 0 ) for the cable types in figure 8.1 (Happoldt, 1978). In this table, C
de capaciteit tussen een geleider en het scherm en is | the capacitance between a conductor and the shield and is | approximation of the normal capacitance C 1 ) and the homopolar capacitance ( C 0 ) for the cable types in figure 8.1 (Happoldt, 1978). In this table, C E
C | C | homopolar capacitance ( C 0 ) for the cable types in figure 8.1 (Happoldt, 1978). In this table, C E the capacitance between a conductor and the shield and is
de capaciteit tussen twee geleiders. | the capacitance between two conductors. | capacitance ( C 0 ) for the cable types in figure 8.1 (Happoldt, 1978). In this table, C E the capacitance between a conductor and the shield and is C
Tabel 8.4 Normale en homopolaire capaciteiten | Table 8.4 Normal and Homopolar Capacitances | for the cable types in figure 8.1 (Happoldt, 1978). In this table, C E the capacitance between a conductor and the shield and is C the capacitance between two conductors.
Type kabel | Type of cable | 8.1 (Happoldt, 1978). In this table, C E the capacitance between a conductor and the shield and is C the capacitance between two conductors. Table 8.4 Normal and Homopolar Capacitances
C | C | In this table, C E the capacitance between a conductor and the shield and is C the capacitance between two conductors. Table 8.4 Normal and Homopolar Capacitances Type of cable
1 | 1 | this table, C E the capacitance between a conductor and the shield and is C the capacitance between two conductors. Table 8.4 Normal and Homopolar Capacitances Type of cable C
C | C | table, C E the capacitance between a conductor and the shield and is C the capacitance between two conductors. Table 8.4 Normal and Homopolar Capacitances Type of cable C 1
0 | 0 | C E the capacitance between a conductor and the shield and is C the capacitance between two conductors. Table 8.4 Normal and Homopolar Capacitances Type of cable C 1 C
Gordelkabel | Gordelkabel | E the capacitance between a conductor and the shield and is C the capacitance between two conductors. Table 8.4 Normal and Homopolar Capacitances Type of cable C 1 C 0
C | C | the capacitance between a conductor and the shield and is C the capacitance between two conductors. Table 8.4 Normal and Homopolar Capacitances Type of cable C 1 C 0 Gordelkabel
E | E | capacitance between a conductor and the shield and is C the capacitance between two conductors. Table 8.4 Normal and Homopolar Capacitances Type of cable C 1 C 0 Gordelkabel C
+ 3 C | + 3 C | between a conductor and the shield and is C the capacitance between two conductors. Table 8.4 Normal and Homopolar Capacitances Type of cable C 1 C 0 Gordelkabel C E
0,6 C | 0.6 C | and the shield and is C the capacitance between two conductors. Table 8.4 Normal and Homopolar Capacitances Type of cable C 1 C 0 Gordelkabel C E + 3 C
1 | 1 | shield and is C the capacitance between two conductors. Table 8.4 Normal and Homopolar Capacitances Type of cable C 1 C 0 Gordelkabel C E + 3 C 0.6 C
Gescheiden afschermingen | Separated shields | and is C the capacitance between two conductors. Table 8.4 Normal and Homopolar Capacitances Type of cable C 1 C 0 Gordelkabel C E + 3 C 0.6 C 1
C | C | C the capacitance between two conductors. Table 8.4 Normal and Homopolar Capacitances Type of cable C 1 C 0 Gordelkabel C E + 3 C 0.6 C 1 Separated shields
E | E | the capacitance between two conductors. Table 8.4 Normal and Homopolar Capacitances Type of cable C 1 C 0 Gordelkabel C E + 3 C 0.6 C 1 Separated shields C
C | C | capacitance between two conductors. Table 8.4 Normal and Homopolar Capacitances Type of cable C 1 C 0 Gordelkabel C E + 3 C 0.6 C 1 Separated shields C E
1 | 1 | between two conductors. Table 8.4 Normal and Homopolar Capacitances Type of cable C 1 C 0 Gordelkabel C E + 3 C 0.6 C 1 Separated shields C E C
Enkeladerige kabel | Single-core cable | two conductors. Table 8.4 Normal and Homopolar Capacitances Type of cable C 1 C 0 Gordelkabel C E + 3 C 0.6 C 1 Separated shields C E C 1
C | C | Table 8.4 Normal and Homopolar Capacitances Type of cable C 1 C 0 Gordelkabel C E + 3 C 0.6 C 1 Separated shields C E C 1 Single-core cable
E | E | 8.4 Normal and Homopolar Capacitances Type of cable C 1 C 0 Gordelkabel C E + 3 C 0.6 C 1 Separated shields C E C 1 Single-core cable C
C | C | Normal and Homopolar Capacitances Type of cable C 1 C 0 Gordelkabel C E + 3 C 0.6 C 1 Separated shields C E C 1 Single-core cable C E
1 | 1 | and Homopolar Capacitances Type of cable C 1 C 0 Gordelkabel C E + 3 C 0.6 C 1 Separated shields C E C 1 Single-core cable C E C
Hieruit volgt dat de homopolaire capaciteit eenvoudig uit te drukken is in de capaciteit van het normale systeem. | From this, it follows that the homopolar capacitance can be easily expressed in terms of the capacitance of the normal system. | Homopolar Capacitances Type of cable C 1 C 0 Gordelkabel C E + 3 C 0.6 C 1 Separated shields C E C 1 Single-core cable C E C 1
8.2.6 Invloed aardelektrode en aarde | 8.2.6 Influence of Ground Electrode and Earth | E C 1 Single-core cable C E C 1 From this, it follows that the homopolar capacitance can be easily expressed in terms of the capacitance of the normal system.
De homopolaire impedantie wordt in belangrijke mate beïnvloed door het retourpad. Het retourpad bestaat uit het pad door de kabel zelf (onder andere de afscherming) met parallel daaraan het pad door de aarde. Het pad door de aarde bestaat uit de aardelektrodes (minimaal twee) en het pad door de aarde zelf. Het retourpad door de aarde loopt zo dicht mogelijk langs de betreffende kabel. Hierdoor is de weerstand van het pad door de aarde meestal anders dan puur theoretisch berekend. Bovendien heeft het retourpad door aarde een reactieve component, die bepaald wordt door de omvatte flux en de elektromagnetische koppeling met andere geleidende voorwerpen in de bodem. Het is hierdoor niet eenvoudig te voorspellen hoe groot de invloed van de parallelschakeling van het retourpad door de aarde op de totale homopolaire impedantie is. In zijn algemeenheid geldt wel dat parallelschakeling van de aarde de homopolaire weerstand verkleint en de homopolaire reactantie vergroot. | The homopolar impedance is significantly influenced by the return path. The return path consists of the path through the cable itself (including the shielding) and, in parallel, the path through the earth. The path through the earth consists of the ground electrodes (at least two) and the path through the earth itself. The return path through the earth runs as close as possible to the respective cable. As a result, the resistance of the path through the earth is usually different from purely theoretical calculations. Additionally, the return path through the earth has a reactive component, determined by the enclosed flux and the electromagnetic coupling with other conductive objects in the ground. Therefore, it is not easy to predict the extent of the influence of the parallel connection of the return path through the earth on the total homopolar impedance. Generally, it is true that the parallel connection of the earth reduces the homopolar resistance and increases the homopolar reactance. | C 1 From this, it follows that the homopolar capacitance can be easily expressed in terms of the capacitance of the normal system. 8.2.6 Influence of Ground Electrode and Earth
De aardelektrode wordt gemodelleerd met een weerstand naar de 'verre aarde'. De weerstand van de aardelektrode is afhankelijk van de specifieke bodemweerstand | The ground electrode is modeled with a resistance to the 'remote earth'. The resistance of the ground electrode depends on the specific soil resistivity. | return path through the earth on the total homopolar impedance. Generally, it is true that the parallel connection of the earth reduces the homopolar resistance and increases the homopolar reactance.
ρ | ρ | resistance and increases the homopolar reactance. The ground electrode is modeled with a resistance to the 'remote earth'. The resistance of the ground electrode depends on the specific soil resistivity.
en de fysische afmetingen van de aardelektrode. Voor een enkele ronde penvormige aardelektrode geldt onderstaande formule voor berekening van de aardverspreidingsweerstand (Happoldt, 1978): | and the physical dimensions of the ground electrode. For a single round rod-shaped ground electrode, the following formula applies for calculating the ground spreading resistance (Happoldt, 1978): | and increases the homopolar reactance. The ground electrode is modeled with a resistance to the 'remote earth'. The resistance of the ground electrode depends on the specific soil resistivity. ρ
Ω | Ohms | soil resistivity. ρ and the physical dimensions of the ground electrode. For a single round rod-shaped ground electrode, the following formula applies for calculating the ground spreading resistance (Happoldt, 1978):
[ | [ | resistivity. ρ and the physical dimensions of the ground electrode. For a single round rod-shaped ground electrode, the following formula applies for calculating the ground spreading resistance (Happoldt, 1978): Ohms
8.24 | 8.24 | ρ and the physical dimensions of the ground electrode. For a single round rod-shaped ground electrode, the following formula applies for calculating the ground spreading resistance (Happoldt, 1978): Ohms [
] | ] | and the physical dimensions of the ground electrode. For a single round rod-shaped ground electrode, the following formula applies for calculating the ground spreading resistance (Happoldt, 1978): Ohms [ 8.24
met: | with: | the physical dimensions of the ground electrode. For a single round rod-shaped ground electrode, the following formula applies for calculating the ground spreading resistance (Happoldt, 1978): Ohms [ 8.24 ]
ρ | ρ | physical dimensions of the ground electrode. For a single round rod-shaped ground electrode, the following formula applies for calculating the ground spreading resistance (Happoldt, 1978): Ohms [ 8.24 ] with:
specifieke bodemweerstand (Ωm) | specific soil resistivity (Ωm) | dimensions of the ground electrode. For a single round rod-shaped ground electrode, the following formula applies for calculating the ground spreading resistance (Happoldt, 1978): Ohms [ 8.24 ] with: ρ
L | L | electrode. For a single round rod-shaped ground electrode, the following formula applies for calculating the ground spreading resistance (Happoldt, 1978): Ohms [ 8.24 ] with: ρ specific soil resistivity (Ωm)
lengte van de verticale elektrode in de grond (m) | length of the vertical electrode in the ground (m) | For a single round rod-shaped ground electrode, the following formula applies for calculating the ground spreading resistance (Happoldt, 1978): Ohms [ 8.24 ] with: ρ specific soil resistivity (Ωm) L
d | d | formula applies for calculating the ground spreading resistance (Happoldt, 1978): Ohms [ 8.24 ] with: ρ specific soil resistivity (Ωm) L length of the vertical electrode in the ground (m)
diameter van de aardelektrode (m) | diameter of the ground electrode (m) | applies for calculating the ground spreading resistance (Happoldt, 1978): Ohms [ 8.24 ] with: ρ specific soil resistivity (Ωm) L length of the vertical electrode in the ground (m) d
De specifieke bodemweerstand is afhankelijk van het bodemmateriaal en de hoeveelheid vocht in en temperatuur van de bodem. Tabel 8.5 geeft een overzicht voor de materialen. | The specific soil resistivity depends on the soil material and the amount of moisture and temperature of the soil. Table 8.5 provides an overview for the materials. | resistance (Happoldt, 1978): Ohms [ 8.24 ] with: ρ specific soil resistivity (Ωm) L length of the vertical electrode in the ground (m) d diameter of the ground electrode (m)
Tabel 8.5 Specifieke bodemweerstand | Table 8.5 Specific Soil Resistivity | ground electrode (m) The specific soil resistivity depends on the soil material and the amount of moisture and temperature of the soil. Table 8.5 provides an overview for the materials.
Bodemsoort | Bodemsoort | soil resistivity depends on the soil material and the amount of moisture and temperature of the soil. Table 8.5 provides an overview for the materials. Table 8.5 Specific Soil Resistivity
ρ minimaal [Ωm] | ρ minimum [Ωm] | resistivity depends on the soil material and the amount of moisture and temperature of the soil. Table 8.5 provides an overview for the materials. Table 8.5 Specific Soil Resistivity Bodemsoort
ρ maximaal [Ωm] | ρ maximum [Ωm] | the soil material and the amount of moisture and temperature of the soil. Table 8.5 provides an overview for the materials. Table 8.5 Specific Soil Resistivity Bodemsoort ρ minimum [Ωm]
Veen | Veen | and the amount of moisture and temperature of the soil. Table 8.5 provides an overview for the materials. Table 8.5 Specific Soil Resistivity Bodemsoort ρ minimum [Ωm] ρ maximum [Ωm]
5 | 5 | the amount of moisture and temperature of the soil. Table 8.5 provides an overview for the materials. Table 8.5 Specific Soil Resistivity Bodemsoort ρ minimum [Ωm] ρ maximum [Ωm] Veen
40 | 40 | amount of moisture and temperature of the soil. Table 8.5 provides an overview for the materials. Table 8.5 Specific Soil Resistivity Bodemsoort ρ minimum [Ωm] ρ maximum [Ωm] Veen 5
Klei | Klei | of moisture and temperature of the soil. Table 8.5 provides an overview for the materials. Table 8.5 Specific Soil Resistivity Bodemsoort ρ minimum [Ωm] ρ maximum [Ωm] Veen 5 40
20 | 20 | moisture and temperature of the soil. Table 8.5 provides an overview for the materials. Table 8.5 Specific Soil Resistivity Bodemsoort ρ minimum [Ωm] ρ maximum [Ωm] Veen 5 40 Klei
200 | 200 | and temperature of the soil. Table 8.5 provides an overview for the materials. Table 8.5 Specific Soil Resistivity Bodemsoort ρ minimum [Ωm] ρ maximum [Ωm] Veen 5 40 Klei 20
Zand | Zand | temperature of the soil. Table 8.5 provides an overview for the materials. Table 8.5 Specific Soil Resistivity Bodemsoort ρ minimum [Ωm] ρ maximum [Ωm] Veen 5 40 Klei 20 200
200 | 200 | of the soil. Table 8.5 provides an overview for the materials. Table 8.5 Specific Soil Resistivity Bodemsoort ρ minimum [Ωm] ρ maximum [Ωm] Veen 5 40 Klei 20 200 Zand
2500 | 2500 | the soil. Table 8.5 provides an overview for the materials. Table 8.5 Specific Soil Resistivity Bodemsoort ρ minimum [Ωm] ρ maximum [Ωm] Veen 5 40 Klei 20 200 Zand 200
Kiezel | Kiezel | soil. Table 8.5 provides an overview for the materials. Table 8.5 Specific Soil Resistivity Bodemsoort ρ minimum [Ωm] ρ maximum [Ωm] Veen 5 40 Klei 20 200 Zand 200 2500
2000 | 2000 | Table 8.5 provides an overview for the materials. Table 8.5 Specific Soil Resistivity Bodemsoort ρ minimum [Ωm] ρ maximum [Ωm] Veen 5 40 Klei 20 200 Zand 200 2500 Kiezel
3000 | 3000 | 8.5 provides an overview for the materials. Table 8.5 Specific Soil Resistivity Bodemsoort ρ minimum [Ωm] ρ maximum [Ωm] Veen 5 40 Klei 20 200 Zand 200 2500 Kiezel 2000
Het verschil tussen de minimale en maximale waarden van de specifieke bodemweerstand wordt bepaald door het gewichtspercentage van het in het materiaal aanwezige vocht. Dit kan gemeten worden tijdens het slaan van de elektrode, ervan uitgaande dat de meting representatief is voor de laagste vochtigheid van de bodem gedurende het hele jaar. | The difference between the minimum and maximum values of the specific soil resistivity is determined by the weight percentage of the moisture present in the material. This can be measured during the driving of the electrode, assuming that the measurement is representative of the lowest moisture content of the soil throughout the year. | provides an overview for the materials. Table 8.5 Specific Soil Resistivity Bodemsoort ρ minimum [Ωm] ρ maximum [Ωm] Veen 5 40 Klei 20 200 Zand 200 2500 Kiezel 2000 3000
In Nederland is de aardelektrode vaak een geslagen elektrode van rond koperdraad met een doorsnede van 50 mm | In the Netherlands, the grounding electrode is often a driven electrode made of round copper wire with a diameter of 50 mm. | in the material. This can be measured during the driving of the electrode, assuming that the measurement is representative of the lowest moisture content of the soil throughout the year.
2 | 2 | moisture content of the soil throughout the year. In the Netherlands, the grounding electrode is often a driven electrode made of round copper wire with a diameter of 50 mm.
( | ( | content of the soil throughout the year. In the Netherlands, the grounding electrode is often a driven electrode made of round copper wire with a diameter of 50 mm. 2
d | d | of the soil throughout the year. In the Netherlands, the grounding electrode is often a driven electrode made of round copper wire with a diameter of 50 mm. 2 (
the soil throughout the year. In the Netherlands, the grounding electrode is often a driven electrode made of round copper wire with a diameter of 50 mm. 2 ( d
Voor het maken van een aardelektrode met een aardverspreidingsweerstand kleiner dan 1 Ω moeten er vaak meerdere parallel elektroden geslagen worden, op ruime afstand van elkaar. Volgens bovenstaande formule is de aardverspreidingsweerstand voor een aardelektrode van 10 m en een diameter van 7,5 mm in bodem met een specifieke weerstand van 100 Ωm gelijk aan 13,7 Ω. De literatuur (Happoldt, 1978) geeft formules voor het berekenen van parallelle of andere vormen van aardelektroden. | To create a grounding electrode with a ground resistance of less than 1 Ω, multiple parallel electrodes often need to be driven into the ground at a considerable distance from each other. According to the above formula, the ground resistance for a 10 m grounding electrode with a diameter of 7.5 mm in soil with a specific resistance of 100 Ωm is 13.7 Ω. The literature (Happoldt, 1978) provides formulas for calculating parallel or other forms of grounding electrodes. | 0.0075 m). Several other types are also used, such as solid steel (round, star-shaped, or cross-shaped) with a well-adhering copper layer on the surface and a galvanized round steel variant.
8.2.7 Meting van de homopolaire impedantie | 8.2.7 Measurement of the homopolar impedance | of 7.5 mm in soil with a specific resistance of 100 Ωm is 13.7 Ω. The literature (Happoldt, 1978) provides formulas for calculating parallel or other forms of grounding electrodes.
Aangezien de homopolaire impedantie van sterkstroomkabels niet met grote nauwkeurigheid berekend kan worden, zijn metingen noodzakelijk. Met behulp van deze metingen uit de praktijk kan een schatting gedaan worden voor waarden die bij de planning van een nieuw tracé bruikbaar zijn. Overigens laten talrijke praktijkmetingen zien dat de spreiding in de meetresultaten aanzienlijk is. | Since the homopolar impedance of high-voltage cables cannot be calculated with great accuracy, measurements are necessary. Using these practical measurements, an estimate can be made for values that are useful in the planning of a new route. Moreover, numerous practical measurements show that the variation in the measurement results is considerable. | a specific resistance of 100 Ωm is 13.7 Ω. The literature (Happoldt, 1978) provides formulas for calculating parallel or other forms of grounding electrodes. 8.2.7 Measurement of the homopolar impedance
De symmetrische componenten transformatie beschrijft de relatie tussen de stromen in het componentnetwerk en het fysieke stelsel (paragraaf 7.5). | The symmetrical components transformation describes the relationship between the currents in the component network and the physical system (paragraph 7.5). | estimate can be made for values that are useful in the planning of a new route. Moreover, numerous practical measurements show that the variation in the measurement results is considerable.
[ | [ | show that the variation in the measurement results is considerable. The symmetrical components transformation describes the relationship between the currents in the component network and the physical system (paragraph 7.5).
8.25 | 8.25 | that the variation in the measurement results is considerable. The symmetrical components transformation describes the relationship between the currents in the component network and the physical system (paragraph 7.5). [
] | ] | the variation in the measurement results is considerable. The symmetrical components transformation describes the relationship between the currents in the component network and the physical system (paragraph 7.5). [ 8.25
Hieruit blijkt dat de homopolaire stroom gelijk is aan éénderde van de som van de drie fasenstromen. In geval van een driefasensymmetrisch systeem met driefasensymmetrische stromen, zal de homopolaire stroom nul zijn. Indien de drie fasestromen niet driefasensymmetrisch zijn, is de stroom, die over het retourpad vloeit, gelijk aan de som van de drie fasenstromen en volgens vergelijking 8.25 gelijk aan | From this, it appears that the homopolar current is equal to one-third of the sum of the three phase currents. In the case of a three-phase symmetrical system with three-phase symmetrical currents, the homopolar current will be zero. If the three phase currents are not three-phase symmetrical, the current flowing through the return path is equal to the sum of the three phase currents and, according to equation 8.25, is equal to | variation in the measurement results is considerable. The symmetrical components transformation describes the relationship between the currents in the component network and the physical system (paragraph 7.5). [ 8.25 ]
3I | 3I | currents are not three-phase symmetrical, the current flowing through the return path is equal to the sum of the three phase currents and, according to equation 8.25, is equal to
0 | 0 | are not three-phase symmetrical, the current flowing through the return path is equal to the sum of the three phase currents and, according to equation 8.25, is equal to 3I
. Hieruit volgt de manier om de homopolaire impedantie te meten, door middel van het aanbrengen van een homopolaire spanning, zoals aangegeven in figuur 8.2. | From this follows the method to measure the homopolar impedance, by applying a homopolar voltage, as indicated in figure 8.2. | not three-phase symmetrical, the current flowing through the return path is equal to the sum of the three phase currents and, according to equation 8.25, is equal to 3I 0
De homopolaire impedantie wordt gemeten met behulp van een voeding met een homopolair stelsel. Dit wordt bereikt door de fasen aan beide uiteinden parallel te schakelen. Aan het uiteinde wordt deze parallelschakeling met de retourleiding verbonden en eventueel geaard. De retourimpedantie, bestaande uit de parallelschakeling van de retourleiding van de kabel en het retourpad door de aarde, wordt in figuur 8.2 voorgesteld door | The homopolar impedance is measured using a power supply with a homopolar system. This is achieved by connecting the phases in parallel at both ends. At the end, this parallel connection is linked to the return conductor and possibly grounded. The return impedance, consisting of the parallel connection of the cable's return conductor and the return path through the ground, is represented in figure 8.2 by | and, according to equation 8.25, is equal to 3I 0 From this follows the method to measure the homopolar impedance, by applying a homopolar voltage, as indicated in figure 8.2.
Z | Z | conductor and possibly grounded. The return impedance, consisting of the parallel connection of the cable's return conductor and the return path through the ground, is represented in figure 8.2 by
E | E | and possibly grounded. The return impedance, consisting of the parallel connection of the cable's return conductor and the return path through the ground, is represented in figure 8.2 by Z
. Aan het begin van het circuit wordt de parallelschakeling éénfasig tegen aarde gevoed. De homopolaire impedantie is dan het quotiënt van spanning en stroom. Indien de kabelmantels aan beide uiteinden geaard zijn, vindt een stroomopdeling plaats tussen de mantels en de aarde. Bij éénzijdige aarding (op de andere zijde zijn de mantels zwevend en niet doorverbonden met mantels van andere kabels) gaat de retourstroom alleen door de aarde. De stroom door de aarde wordt sterk beïnvloed door andere geleidende voorwerpen in of op de aarde, zoals andere kabelmantels, metalen gas- en waterleidingen en dergelijke. Omdat de homopolaire impedantie dus mede afhankelijk is van de omgeving van de kabel kan voor een bepaald kabeltype een algemeen geldige homopolaire impedantie niet worden aangegeven. Soms wordt een homopolaire impedantie aangegeven onder de voorwaarde dat de retourstroom alleen door de mantels vloeit. Bij drie éénfase-kabels zijn deze mantelstromen gelijk. | At the beginning of the circuit, the parallel connection is fed single-phase to ground. The homopolar impedance is then the quotient of voltage and current. If the cable sheaths are grounded at both ends, the current is divided between the sheaths and the ground. With single-sided grounding (where the sheaths on the other side are floating and not connected to the sheaths of other cables), the return current flows only through the ground. The current through the ground is significantly influenced by other conductive objects in or on the ground, such as other cable sheaths, metal gas, and water pipes, and the like. Because the homopolar impedance is thus also dependent on the cable's surroundings, a universally valid homopolar impedance cannot be specified for a particular cable type. Sometimes a homopolar impedance is specified under the condition that the return current flows only through the sheaths. With three single-phase cables, these sheath currents are equal. | possibly grounded. The return impedance, consisting of the parallel connection of the cable's return conductor and the return path through the ground, is represented in figure 8.2 by Z E
Figuur 8.2 Meting van de homopolaire impedantie | Figure 8.2 Measurement of the homopolar impedance | particular cable type. Sometimes a homopolar impedance is specified under the condition that the return current flows only through the sheaths. With three single-phase cables, these sheath currents are equal.
In een driefasensymmetrisch net is | In a three-phase symmetrical network, | is specified under the condition that the return current flows only through the sheaths. With three single-phase cables, these sheath currents are equal. Figure 8.2 Measurement of the homopolar impedance
Z | Z | that the return current flows only through the sheaths. With three single-phase cables, these sheath currents are equal. Figure 8.2 Measurement of the homopolar impedance In a three-phase symmetrical network,
A | A | the return current flows only through the sheaths. With three single-phase cables, these sheath currents are equal. Figure 8.2 Measurement of the homopolar impedance In a three-phase symmetrical network, Z
return current flows only through the sheaths. With three single-phase cables, these sheath currents are equal. Figure 8.2 Measurement of the homopolar impedance In a three-phase symmetrical network, Z A
B | B | flows only through the sheaths. With three single-phase cables, these sheath currents are equal. Figure 8.2 Measurement of the homopolar impedance In a three-phase symmetrical network, Z A = Z
only through the sheaths. With three single-phase cables, these sheath currents are equal. Figure 8.2 Measurement of the homopolar impedance In a three-phase symmetrical network, Z A = Z B
C | C | the sheaths. With three single-phase cables, these sheath currents are equal. Figure 8.2 Measurement of the homopolar impedance In a three-phase symmetrical network, Z A = Z B = Z
sheaths. With three single-phase cables, these sheath currents are equal. Figure 8.2 Measurement of the homopolar impedance In a three-phase symmetrical network, Z A = Z B = Z C
L | L | three single-phase cables, these sheath currents are equal. Figure 8.2 Measurement of the homopolar impedance In a three-phase symmetrical network, Z A = Z B = Z C = Z
, | , | single-phase cables, these sheath currents are equal. Figure 8.2 Measurement of the homopolar impedance In a three-phase symmetrical network, Z A = Z B = Z C = Z L
zodat | zodat | cables, these sheath currents are equal. Figure 8.2 Measurement of the homopolar impedance In a three-phase symmetrical network, Z A = Z B = Z C = Z L ,
I | I | these sheath currents are equal. Figure 8.2 Measurement of the homopolar impedance In a three-phase symmetrical network, Z A = Z B = Z C = Z L , zodat
A | A | sheath currents are equal. Figure 8.2 Measurement of the homopolar impedance In a three-phase symmetrical network, Z A = Z B = Z C = Z L , zodat I
currents are equal. Figure 8.2 Measurement of the homopolar impedance In a three-phase symmetrical network, Z A = Z B = Z C = Z L , zodat I A
B | B | equal. Figure 8.2 Measurement of the homopolar impedance In a three-phase symmetrical network, Z A = Z B = Z C = Z L , zodat I A = I
Figure 8.2 Measurement of the homopolar impedance In a three-phase symmetrical network, Z A = Z B = Z C = Z L , zodat I A = I B
C | C | Measurement of the homopolar impedance In a three-phase symmetrical network, Z A = Z B = Z C = Z L , zodat I A = I B = I
of the homopolar impedance In a three-phase symmetrical network, Z A = Z B = Z C = Z L , zodat I A = I B = I C
0 | 0 | homopolar impedance In a three-phase symmetrical network, Z A = Z B = Z C = Z L , zodat I A = I B = I C = I
. Dan volgt voor de meting: | . Then follows for the measurement: | impedance In a three-phase symmetrical network, Z A = Z B = Z C = Z L , zodat I A = I B = I C = I 0
[ | [ | Z A = Z B = Z C = Z L , zodat I A = I B = I C = I 0 . Then follows for the measurement:
8.26 | 8.26 | A = Z B = Z C = Z L , zodat I A = I B = I C = I 0 . Then follows for the measurement: [
] | ]
Hieruit volgt voor de homopolaire impedantie: | From this follows for the homopolar impedance: | Z B = Z C = Z L , zodat I A = I B = I C = I 0 . Then follows for the measurement: [ 8.26 ]
[ | [ | L , zodat I A = I B = I C = I 0 . Then follows for the measurement: [ 8.26 ] From this follows for the homopolar impedance:
8.27 | 8.27 | , zodat I A = I B = I C = I 0 . Then follows for the measurement: [ 8.26 ] From this follows for the homopolar impedance: [
] | ] | zodat I A = I B = I C = I 0 . Then follows for the measurement: [ 8.26 ] From this follows for the homopolar impedance: [ 8.27
en voor de meting: | and for the measurement: | I A = I B = I C = I 0 . Then follows for the measurement: [ 8.26 ] From this follows for the homopolar impedance: [ 8.27 ]
[ | [ | B = I C = I 0 . Then follows for the measurement: [ 8.26 ] From this follows for the homopolar impedance: [ 8.27 ] and for the measurement:
8.28 | 8.28
] | ] | I C = I 0 . Then follows for the measurement: [ 8.26 ] From this follows for the homopolar impedance: [ 8.27 ] and for the measurement: [ 8.28
Voor planningsdoeleinden kan de homopolaire impedantie geschat worden, afhankelijk van de situatie als een constante waarde of als een factor van de normale impedantie. | For planning purposes, the homopolar impedance can be estimated, depending on the situation, as a constant value or as a factor of the normal impedance. | C = I 0 . Then follows for the measurement: [ 8.26 ] From this follows for the homopolar impedance: [ 8.27 ] and for the measurement: [ 8.28 ]
Samenvattend wordt de homopolaire impedantie van een kabelverbinding bepaald door het totale circuit van de homopolaire stroom. Het totale circuit bestaat uit de heenweg (de fasegeleiders) en de terugweg (de nulgeleiders, de afscherming en armering van de kabel plus de aarde via de aardelektrodes (onder andere in middenspanningsruimten) en eventueel ander contact met aarde. In de aarde aanwezige geleidende materialen (andere kabels, metalen pijpen en spoorrails) kunnen de homopolaire impedantie sterk beïnvloeden. | In summary, the homopolar impedance of a cable connection is determined by the total circuit of the homopolar current. The total circuit consists of the forward path (the phase conductors) and the return path (the neutral conductors, the shielding and armor of the cable, plus the ground via the ground electrodes (including in medium voltage spaces) and any other contact with the ground. Conductive materials present in the ground (other cables, metal pipes, and railroad tracks) can significantly influence the homopolar impedance. | the measurement: [ 8.28 ] For planning purposes, the homopolar impedance can be estimated, depending on the situation, as a constant value or as a factor of the normal impedance.
Het is mogelijk de homopolaire impedantie van een kabel te berekenen voor het geval dat het retourcircuit bestaat uit mantel en eventueel nulgeleider. Dit is ook de waarde die de fabrikant in de meeste gevallen opgeeft. Indien de retourstroom echter (zoals in de meeste praktische gevallen) ook door de aarde vloeit, zal de homopolaire weerstand afnemen en de homopolaire reactantie toenemen. De waarde is voor die gevallen zeer moeilijk te berekenen en de berekening is meestal onnauwkeurig. | It is possible to calculate the homopolar impedance of a cable for cases where the return circuit consists of the sheath and possibly a neutral conductor. This is also the value that the manufacturer usually provides. However, if the return current (as in most practical cases) also flows through the ground, the homopolar resistance will decrease and the homopolar reactance will increase. The value in those cases is very difficult to calculate, and the calculation is usually inaccurate. | in medium voltage spaces) and any other contact with the ground. Conductive materials present in the ground (other cables, metal pipes, and railroad tracks) can significantly influence the homopolar impedance.
Voor enkele kabeltypen en situaties zijn de homopolaire impedanties berekend voor het geval het retourpad alleen via de kabel zelf loopt. Alle gegeven waarden dienen alleen ter informatie. De verhoudingen van de homopolaire tot de normale impedanties zijn hieronder samengevat. De resultaten variëren voor kabels van kleine naar grote geleiderdiameter. | For certain cable types and situations, the homopolar impedances have been calculated for the case where the return path runs only through the cable itself. All provided values are for informational purposes only. The ratios of the homopolar to the normal impedances are summarized below. The results vary for cables with small to large conductor diameters. | through the ground, the homopolar resistance will decrease and the homopolar reactance will increase. The value in those cases is very difficult to calculate, and the calculation is usually inaccurate.
Tabel 8.6 Homopolaire impedantie bij retourpad alleen door de kabel zelf | Table 8.6 Homopolar impedance with return path only through the cable itself | provided values are for informational purposes only. The ratios of the homopolar to the normal impedances are summarized below. The results vary for cables with small to large conductor diameters.
Type kabel | Cable type | to the normal impedances are summarized below. The results vary for cables with small to large conductor diameters. Table 8.6 Homopolar impedance with return path only through the cable itself
Retour nul | Zero return | normal impedances are summarized below. The results vary for cables with small to large conductor diameters. Table 8.6 Homopolar impedance with return path only through the cable itself Cable type
Retour nul + mantel | Zero return + sheath | are summarized below. The results vary for cables with small to large conductor diameters. Table 8.6 Homopolar impedance with return path only through the cable itself Cable type Zero return
R | R | results vary for cables with small to large conductor diameters. Table 8.6 Homopolar impedance with return path only through the cable itself Cable type Zero return Zero return + sheath
0 | 0 | vary for cables with small to large conductor diameters. Table 8.6 Homopolar impedance with return path only through the cable itself Cable type Zero return Zero return + sheath R
/R | /R | for cables with small to large conductor diameters. Table 8.6 Homopolar impedance with return path only through the cable itself Cable type Zero return Zero return + sheath R 0
1 | 1 | cables with small to large conductor diameters. Table 8.6 Homopolar impedance with return path only through the cable itself Cable type Zero return Zero return + sheath R 0 /R
X | X | with small to large conductor diameters. Table 8.6 Homopolar impedance with return path only through the cable itself Cable type Zero return Zero return + sheath R 0 /R 1
0 | 0 | small to large conductor diameters. Table 8.6 Homopolar impedance with return path only through the cable itself Cable type Zero return Zero return + sheath R 0 /R 1 X
/X | /X | to large conductor diameters. Table 8.6 Homopolar impedance with return path only through the cable itself Cable type Zero return Zero return + sheath R 0 /R 1 X 0
1 | 1 | large conductor diameters. Table 8.6 Homopolar impedance with return path only through the cable itself Cable type Zero return Zero return + sheath R 0 /R 1 X 0 /X
R | R | conductor diameters. Table 8.6 Homopolar impedance with return path only through the cable itself Cable type Zero return Zero return + sheath R 0 /R 1 X 0 /X 1
0 | 0 | diameters. Table 8.6 Homopolar impedance with return path only through the cable itself Cable type Zero return Zero return + sheath R 0 /R 1 X 0 /X 1 R
/R | /R | Table 8.6 Homopolar impedance with return path only through the cable itself Cable type Zero return Zero return + sheath R 0 /R 1 X 0 /X 1 R 0
1 | 1 | 8.6 Homopolar impedance with return path only through the cable itself Cable type Zero return Zero return + sheath R 0 /R 1 X 0 /X 1 R 0 /R
X | X | Homopolar impedance with return path only through the cable itself Cable type Zero return Zero return + sheath R 0 /R 1 X 0 /X 1 R 0 /R 1
0 | 0 | impedance with return path only through the cable itself Cable type Zero return Zero return + sheath R 0 /R 1 X 0 /X 1 R 0 /R 1 X
/X | /X | with return path only through the cable itself Cable type Zero return Zero return + sheath R 0 /R 1 X 0 /X 1 R 0 /R 1 X 0
1 | 1 | return path only through the cable itself Cable type Zero return Zero return + sheath R 0 /R 1 X 0 /X 1 R 0 /R 1 X 0 /X
LS 4-ad kabel (25..300 mm) | LS 4-core cable (25..300 mm) | path only through the cable itself Cable type Zero return Zero return + sheath R 0 /R 1 X 0 /X 1 R 0 /R 1 X 0 /X 1
4,0 | 4.0 | itself Cable type Zero return Zero return + sheath R 0 /R 1 X 0 /X 1 R 0 /R 1 X 0 /X 1 LS 4-core cable (25..300 mm)
3,5..4,0 | 3.5..4.0 | Cable type Zero return Zero return + sheath R 0 /R 1 X 0 /X 1 R 0 /R 1 X 0 /X 1 LS 4-core cable (25..300 mm) 4.0
2,5..3,0 | 2.5..3.0 | type Zero return Zero return + sheath R 0 /R 1 X 0 /X 1 R 0 /R 1 X 0 /X 1 LS 4-core cable (25..300 mm) 4.0 3.5..4.0
1,5..2,0 | 1.5..2.0 | Zero return Zero return + sheath R 0 /R 1 X 0 /X 1 R 0 /R 1 X 0 /X 1 LS 4-core cable (25..300 mm) 4.0 3.5..4.0 2.5..3.0
Type kabel | Type of cable | return Zero return + sheath R 0 /R 1 X 0 /X 1 R 0 /R 1 X 0 /X 1 LS 4-core cable (25..300 mm) 4.0 3.5..4.0 2.5..3.0 1.5..2.0
Retour mantel | Return sheath | + sheath R 0 /R 1 X 0 /X 1 R 0 /R 1 X 0 /X 1 LS 4-core cable (25..300 mm) 4.0 3.5..4.0 2.5..3.0 1.5..2.0 Type of cable
R | R | R 0 /R 1 X 0 /X 1 R 0 /R 1 X 0 /X 1 LS 4-core cable (25..300 mm) 4.0 3.5..4.0 2.5..3.0 1.5..2.0 Type of cable Return sheath
0 | 0 | 0 /R 1 X 0 /X 1 R 0 /R 1 X 0 /X 1 LS 4-core cable (25..300 mm) 4.0 3.5..4.0 2.5..3.0 1.5..2.0 Type of cable Return sheath R
/R | /R | /R 1 X 0 /X 1 R 0 /R 1 X 0 /X 1 LS 4-core cable (25..300 mm) 4.0 3.5..4.0 2.5..3.0 1.5..2.0 Type of cable Return sheath R 0
1 | 1 | 1 X 0 /X 1 R 0 /R 1 X 0 /X 1 LS 4-core cable (25..300 mm) 4.0 3.5..4.0 2.5..3.0 1.5..2.0 Type of cable Return sheath R 0 /R
X | X | X 0 /X 1 R 0 /R 1 X 0 /X 1 LS 4-core cable (25..300 mm) 4.0 3.5..4.0 2.5..3.0 1.5..2.0 Type of cable Return sheath R 0 /R 1
0 | 0 | 0 /X 1 R 0 /R 1 X 0 /X 1 LS 4-core cable (25..300 mm) 4.0 3.5..4.0 2.5..3.0 1.5..2.0 Type of cable Return sheath R 0 /R 1 X
/X | /X | /X 1 R 0 /R 1 X 0 /X 1 LS 4-core cable (25..300 mm) 4.0 3.5..4.0 2.5..3.0 1.5..2.0 Type of cable Return sheath R 0 /R 1 X 0
1 | 1 | 1 R 0 /R 1 X 0 /X 1 LS 4-core cable (25..300 mm) 4.0 3.5..4.0 2.5..3.0 1.5..2.0 Type of cable Return sheath R 0 /R 1 X 0 /X
MS gordelkabel (25..300 mm) | MS belt cable (25..300 mm) | R 0 /R 1 X 0 /X 1 LS 4-core cable (25..300 mm) 4.0 3.5..4.0 2.5..3.0 1.5..2.0 Type of cable Return sheath R 0 /R 1 X 0 /X 1
4..15 | 4..15 | 0 /X 1 LS 4-core cable (25..300 mm) 4.0 3.5..4.0 2.5..3.0 1.5..2.0 Type of cable Return sheath R 0 /R 1 X 0 /X 1 MS belt cable (25..300 mm)
1,7..1,4 | 1.7..1.4 | /X 1 LS 4-core cable (25..300 mm) 4.0 3.5..4.0 2.5..3.0 1.5..2.0 Type of cable Return sheath R 0 /R 1 X 0 /X 1 MS belt cable (25..300 mm) 4..15
MS 3-ad XLPE (50..300 mm) | MS 3-core XLPE (50..300 mm) | 1 LS 4-core cable (25..300 mm) 4.0 3.5..4.0 2.5..3.0 1.5..2.0 Type of cable Return sheath R 0 /R 1 X 0 /X 1 MS belt cable (25..300 mm) 4..15 1.7..1.4
7..20 | 7..20 | mm) 4.0 3.5..4.0 2.5..3.0 1.5..2.0 Type of cable Return sheath R 0 /R 1 X 0 /X 1 MS belt cable (25..300 mm) 4..15 1.7..1.4 MS 3-core XLPE (50..300 mm)
1 | 1 | 4.0 3.5..4.0 2.5..3.0 1.5..2.0 Type of cable Return sheath R 0 /R 1 X 0 /X 1 MS belt cable (25..300 mm) 4..15 1.7..1.4 MS 3-core XLPE (50..300 mm) 7..20
MS 1-ad XLPE (95..400 mm) | MS 1-core XLPE (95..400 mm) | 3.5..4.0 2.5..3.0 1.5..2.0 Type of cable Return sheath R 0 /R 1 X 0 /X 1 MS belt cable (25..300 mm) 4..15 1.7..1.4 MS 3-core XLPE (50..300 mm) 7..20 1
7..18 | 7..18 | cable Return sheath R 0 /R 1 X 0 /X 1 MS belt cable (25..300 mm) 4..15 1.7..1.4 MS 3-core XLPE (50..300 mm) 7..20 1 MS 1-core XLPE (95..400 mm)
0,4..0,3 | 0.4..0.3 | Return sheath R 0 /R 1 X 0 /X 1 MS belt cable (25..300 mm) 4..15 1.7..1.4 MS 3-core XLPE (50..300 mm) 7..20 1 MS 1-core XLPE (95..400 mm) 7..18
8.2.8 Uitgebreid model voor de laagspanningskabel | 8.2.8 Extended model for the low voltage cable | sheath R 0 /R 1 X 0 /X 1 MS belt cable (25..300 mm) 4..15 1.7..1.4 MS 3-core XLPE (50..300 mm) 7..20 1 MS 1-core XLPE (95..400 mm) 7..18 0.4..0.3
Voor berekeningen aan de aanrakingsveiligheid zijn specifieke kabelgegevens nodig, die niet zonder meer uit tabellen van de kabelfabrikanten af te leiden zijn. Die tabellen bevatten alleen gegevens betreffende het gebruik van de kabel in normale omstandigheden en het gedrag bij kortsluiting. Bij een éénfase aardsluiting echter, heeft de kortsluitstroom door inductie invloed op de spanning in de overige geleiders. De elektromagnetische koppelingen tussen de geleiders van de kabel onderling en tussen de geleiders en het aardscherm zijn niet gedocumenteerd en moeten berekend worden. Het betreft PVC en GPLK kabels met sectorvormige en ronde geleiders, zowel koper als aluminium, zowel met als zonder hulpaders. In deze paragraaf worden de impedanties van de kabels berekend met een programma voor analyse van elektrische en magnetische velden in rotatiesymmetrische doorsneden. | For calculations regarding touch safety, specific cable data is required, which cannot be directly derived from the tables provided by cable manufacturers. These tables only contain information about the use of the cable under normal conditions and its behavior during a short circuit. However, in the case of a single-phase ground fault, the short-circuit current influences the voltage in the other conductors through induction. The electromagnetic couplings between the conductors of the cable and between the conductors and the ground shield are not documented and must be calculated. This concerns PVC and GPLK cables with sector-shaped and round conductors, both copper and aluminum, with and without auxiliary cores. In this section, the impedances of the cables are calculated using a program for analyzing electric and magnetic fields in rotationally symmetric cross-sections. | 1 MS belt cable (25..300 mm) 4..15 1.7..1.4 MS 3-core XLPE (50..300 mm) 7..20 1 MS 1-core XLPE (95..400 mm) 7..18 0.4..0.3 8.2.8 Extended model for the low voltage cable
De laagspanningskabel is opgebouwd uit: | The low-voltage cable is composed of: | and aluminum, with and without auxiliary cores. In this section, the impedances of the cables are calculated using a program for analyzing electric and magnetic fields in rotationally symmetric cross-sections.
geleiders en hulpaders, | conductors and auxiliary cores, | cores. In this section, the impedances of the cables are calculated using a program for analyzing electric and magnetic fields in rotationally symmetric cross-sections. The low-voltage cable is composed of:
meestal geïsoleerd met kunststof, | usually insulated with plastic, | the impedances of the cables are calculated using a program for analyzing electric and magnetic fields in rotationally symmetric cross-sections. The low-voltage cable is composed of: conductors and auxiliary cores,
bijeengehouden door een binnenmantel, | held together by an inner sheath, | cables are calculated using a program for analyzing electric and magnetic fields in rotationally symmetric cross-sections. The low-voltage cable is composed of: conductors and auxiliary cores, usually insulated with plastic,
vaak omgeven door een aardscherm, | often surrounded by a grounding shield, | for analyzing electric and magnetic fields in rotationally symmetric cross-sections. The low-voltage cable is composed of: conductors and auxiliary cores, usually insulated with plastic, held together by an inner sheath,
beschermd door een buitenmantel, | protected by an outer sheath, | in rotationally symmetric cross-sections. The low-voltage cable is composed of: conductors and auxiliary cores, usually insulated with plastic, held together by an inner sheath, often surrounded by a grounding shield,
waarbij soms nog armering is aangebracht. | where sometimes additional armoring is applied. | low-voltage cable is composed of: conductors and auxiliary cores, usually insulated with plastic, held together by an inner sheath, often surrounded by a grounding shield, protected by an outer sheath,
Een typische doorsnede van de geleidende onderdelen van een LS-kabel met cirkelvormige en met sectorvormige geleiders toont figuur 8.3 voor een kabel van het type GPLKh 4x35 Cu rond + 4x2,5 Cu en van het type GPLKh 4x95 Cu sector + 4x6 Cu. Van binnen naar buiten zijn zichtbaar: hoofdaders en hulpaders met isolatie, scherm, vulling, wapening en buitenmantel. | A typical cross-section of the conductive parts of an LS cable with circular and sector-shaped conductors is shown in figure 8.3 for a cable of the type GPLKh 4x35 Cu round + 4x2.5 Cu and of the type GPLKh 4x95 Cu sector + 4x6 Cu. From the inside out, the following are visible: main cores and auxiliary cores with insulation, shield, filling, armoring, and outer sheath. | and auxiliary cores, usually insulated with plastic, held together by an inner sheath, often surrounded by a grounding shield, protected by an outer sheath, where sometimes additional armoring is applied.
Figuur 8.3 Kabelopbouw van LS-kabels met ronde en sectorvormige geleiders | Figure 8.3 Cable construction of low-voltage cables with round and sector-shaped conductors | the type GPLKh 4x95 Cu sector + 4x6 Cu. From the inside out, the following are visible: main cores and auxiliary cores with insulation, shield, filling, armoring, and outer sheath.
Duidelijk zichtbaar is dat de raakvlakken tussen de geleiders onderling en tussen geleiders en mantel in het geval van de sectorvormige geleiders veel groter zijn dan bij de ronde geleiders. Als gevolg is bij de sectorvormige geleiders de mutuele koppeling sterker. | It is clearly visible that the contact surfaces between the conductors themselves and between the conductors and the sheath are much larger in the case of sector-shaped conductors than with round conductors. As a result, the mutual coupling is stronger in sector-shaped conductors. | out, the following are visible: main cores and auxiliary cores with insulation, shield, filling, armoring, and outer sheath. Figure 8.3 Cable construction of low-voltage cables with round and sector-shaped conductors
Bij onderscheid van fasegeleiders, nulgeleider, hulpgeleiders en scherm zijn in de laagspanningskabel maximaal 11 verschillende impedanties te onderscheiden: | When distinguishing between phase conductors, neutral conductor, auxiliary conductors, and shield, up to 11 different impedances can be identified in the low-voltage cable: | between the conductors and the sheath are much larger in the case of sector-shaped conductors than with round conductors. As a result, the mutual coupling is stronger in sector-shaped conductors.
Z | Z | mutual coupling is stronger in sector-shaped conductors. When distinguishing between phase conductors, neutral conductor, auxiliary conductors, and shield, up to 11 different impedances can be identified in the low-voltage cable:
c | c | coupling is stronger in sector-shaped conductors. When distinguishing between phase conductors, neutral conductor, auxiliary conductors, and shield, up to 11 different impedances can be identified in the low-voltage cable: Z
langsimpedantie hoofdgeleidercircuit (fase en nul) | longitudinal impedance of the main conductor circuit (phase and neutral) | is stronger in sector-shaped conductors. When distinguishing between phase conductors, neutral conductor, auxiliary conductors, and shield, up to 11 different impedances can be identified in the low-voltage cable: Z c
Z | Z | neutral conductor, auxiliary conductors, and shield, up to 11 different impedances can be identified in the low-voltage cable: Z c longitudinal impedance of the main conductor circuit (phase and neutral)
cc,n | cc,n | conductor, auxiliary conductors, and shield, up to 11 different impedances can be identified in the low-voltage cable: Z c longitudinal impedance of the main conductor circuit (phase and neutral) Z
mutuele impedantie naast elkaar gelegen hoofdgeleiders | mutual impedance of adjacent main conductors | auxiliary conductors, and shield, up to 11 different impedances can be identified in the low-voltage cable: Z c longitudinal impedance of the main conductor circuit (phase and neutral) Z cc,n
Z | Z | 11 different impedances can be identified in the low-voltage cable: Z c longitudinal impedance of the main conductor circuit (phase and neutral) Z cc,n mutual impedance of adjacent main conductors
cc,t | cc,t | different impedances can be identified in the low-voltage cable: Z c longitudinal impedance of the main conductor circuit (phase and neutral) Z cc,n mutual impedance of adjacent main conductors Z
mutuele impedantie tegenover elkaar gelegen hoofdgeleiders | mutual impedance of main conductors located opposite each other | impedances can be identified in the low-voltage cable: Z c longitudinal impedance of the main conductor circuit (phase and neutral) Z cc,n mutual impedance of adjacent main conductors Z cc,t
Z | Z | c longitudinal impedance of the main conductor circuit (phase and neutral) Z cc,n mutual impedance of adjacent main conductors Z cc,t mutual impedance of main conductors located opposite each other
e | e | longitudinal impedance of the main conductor circuit (phase and neutral) Z cc,n mutual impedance of adjacent main conductors Z cc,t mutual impedance of main conductors located opposite each other Z
langsimpedantie schermcircuit | longitudinal impedance of the shielding circuit | impedance of the main conductor circuit (phase and neutral) Z cc,n mutual impedance of adjacent main conductors Z cc,t mutual impedance of main conductors located opposite each other Z e
Z | Z | (phase and neutral) Z cc,n mutual impedance of adjacent main conductors Z cc,t mutual impedance of main conductors located opposite each other Z e longitudinal impedance of the shielding circuit
ce | ce | and neutral) Z cc,n mutual impedance of adjacent main conductors Z cc,t mutual impedance of main conductors located opposite each other Z e longitudinal impedance of the shielding circuit Z
mutuele impedantie hoofdgeleider en scherm | mutual impedance of main conductor and shield | neutral) Z cc,n mutual impedance of adjacent main conductors Z cc,t mutual impedance of main conductors located opposite each other Z e longitudinal impedance of the shielding circuit Z ce
Z | Z | main conductors Z cc,t mutual impedance of main conductors located opposite each other Z e longitudinal impedance of the shielding circuit Z ce mutual impedance of main conductor and shield
h | h | conductors Z cc,t mutual impedance of main conductors located opposite each other Z e longitudinal impedance of the shielding circuit Z ce mutual impedance of main conductor and shield Z
langsimpedantie hulpgeleidercircuit | longitudinal impedance of the auxiliary conductor circuit | Z cc,t mutual impedance of main conductors located opposite each other Z e longitudinal impedance of the shielding circuit Z ce mutual impedance of main conductor and shield Z h
Z | Z | located opposite each other Z e longitudinal impedance of the shielding circuit Z ce mutual impedance of main conductor and shield Z h longitudinal impedance of the auxiliary conductor circuit
ch,n | ch,n | opposite each other Z e longitudinal impedance of the shielding circuit Z ce mutual impedance of main conductor and shield Z h longitudinal impedance of the auxiliary conductor circuit Z
mutuele impedantie naast elkaar gelegen hoofd- en hulpgeleiders | mutual impedance of adjacent main and auxiliary conductors | each other Z e longitudinal impedance of the shielding circuit Z ce mutual impedance of main conductor and shield Z h longitudinal impedance of the auxiliary conductor circuit Z ch,n
Z | Z | shielding circuit Z ce mutual impedance of main conductor and shield Z h longitudinal impedance of the auxiliary conductor circuit Z ch,n mutual impedance of adjacent main and auxiliary conductors
ch,t | ch,t | circuit Z ce mutual impedance of main conductor and shield Z h longitudinal impedance of the auxiliary conductor circuit Z ch,n mutual impedance of adjacent main and auxiliary conductors Z
mutuele impedantie tegenover elkaar gelegen hoofd- en hulpgeleiders | mutual impedance of opposing main and auxiliary conductors | Z ce mutual impedance of main conductor and shield Z h longitudinal impedance of the auxiliary conductor circuit Z ch,n mutual impedance of adjacent main and auxiliary conductors Z ch,t
Z | Z | shield Z h longitudinal impedance of the auxiliary conductor circuit Z ch,n mutual impedance of adjacent main and auxiliary conductors Z ch,t mutual impedance of opposing main and auxiliary conductors
hh,n | hh,n | Z h longitudinal impedance of the auxiliary conductor circuit Z ch,n mutual impedance of adjacent main and auxiliary conductors Z ch,t mutual impedance of opposing main and auxiliary conductors Z
mutuele impedantie 'naast elkaar gelegen' hulpgeleiders | mutual impedance of 'adjacent' auxiliary conductors | h longitudinal impedance of the auxiliary conductor circuit Z ch,n mutual impedance of adjacent main and auxiliary conductors Z ch,t mutual impedance of opposing main and auxiliary conductors Z hh,n
Z | Z | conductor circuit Z ch,n mutual impedance of adjacent main and auxiliary conductors Z ch,t mutual impedance of opposing main and auxiliary conductors Z hh,n mutual impedance of 'adjacent' auxiliary conductors
hh,t | mutual impedance of 'opposing' auxiliary conductors | circuit Z ch,n mutual impedance of adjacent main and auxiliary conductors Z ch,t mutual impedance of opposing main and auxiliary conductors Z hh,n mutual impedance of 'adjacent' auxiliary conductors Z
mutuele impedantie 'tegenover elkaar gelegen' hulpgeleiders | mutual impedance of 'opposing' auxiliary conductors | adjacent main and auxiliary conductors Z ch,t mutual impedance of opposing main and auxiliary conductors Z hh,n mutual impedance of 'adjacent' auxiliary conductors Z mutual impedance of 'opposing' auxiliary conductors
Z | Z | ch,t mutual impedance of opposing main and auxiliary conductors Z hh,n mutual impedance of 'adjacent' auxiliary conductors Z mutual impedance of 'opposing' auxiliary conductors mutual impedance of 'opposing' auxiliary conductors
he | he | mutual impedance of opposing main and auxiliary conductors Z hh,n mutual impedance of 'adjacent' auxiliary conductors Z mutual impedance of 'opposing' auxiliary conductors mutual impedance of 'opposing' auxiliary conductors Z
mutuele impedantie hulpgeleider en scherm | mutual impedance of auxiliary conductor and shield | impedance of opposing main and auxiliary conductors Z hh,n mutual impedance of 'adjacent' auxiliary conductors Z mutual impedance of 'opposing' auxiliary conductors mutual impedance of 'opposing' auxiliary conductors Z he
In matrixvorm: | In matrix form: | Z hh,n mutual impedance of 'adjacent' auxiliary conductors Z mutual impedance of 'opposing' auxiliary conductors mutual impedance of 'opposing' auxiliary conductors Z he mutual impedance of auxiliary conductor and shield
De kabel bestaat uit 3 gelijke fasen- en nulgeleiders. Indien de nulgeleider afwijkt van de fasegeleiders wijzigen in de matrix de getallen in kolom 4 en rij 4. Eventueel kunnen 4 gelijke hulpaders aanwezig zijn. Indien de hulpaders of de geleidende mantel ontbreekt, zijn de betreffende impedanties niet in de matrix aanwezig. | The cable consists of 3 identical phase and neutral conductors. If the neutral conductor differs from the phase conductors, the numbers in column 4 and row 4 of the matrix change. Optionally, 4 identical auxiliary conductors may be present. If the auxiliary conductors or the conductive shield are missing, the respective impedances are not present in the matrix. | impedance of 'adjacent' auxiliary conductors Z mutual impedance of 'opposing' auxiliary conductors mutual impedance of 'opposing' auxiliary conductors Z he mutual impedance of auxiliary conductor and shield In matrix form:
De bedrijfsimpedantie van een kabel is niet dezelfde als de langsimpedantie van een hoofdgeleidercircuit, maar wordt berekend uit de individuele impedanties van de gehele kabel als gesloten systeem. Zo is de bedrijfsimpedantie uit te rekenen uit de langsimpedantie van een hoofdgeleidercircuit | The operational impedance of a cable is not the same as the longitudinal impedance of a main conductor circuit, but is calculated from the individual impedances of the entire cable as a closed system. Thus, the operational impedance can be calculated from the longitudinal impedance of a main conductor circuit. | the matrix change. Optionally, 4 identical auxiliary conductors may be present. If the auxiliary conductors or the conductive shield are missing, the respective impedances are not present in the matrix.
Z | Z | is calculated from the individual impedances of the entire cable as a closed system. Thus, the operational impedance can be calculated from the longitudinal impedance of a main conductor circuit.
c | c | calculated from the individual impedances of the entire cable as a closed system. Thus, the operational impedance can be calculated from the longitudinal impedance of a main conductor circuit. Z
en het gemiddelde van de mutuele impedanties van een fasegeleider naar een aanliggende fasegeleider | and the average of the mutual impedances from one phase conductor to an adjacent phase conductor | from the individual impedances of the entire cable as a closed system. Thus, the operational impedance can be calculated from the longitudinal impedance of a main conductor circuit. Z c
Z | Z | can be calculated from the longitudinal impedance of a main conductor circuit. Z c and the average of the mutual impedances from one phase conductor to an adjacent phase conductor
cc,n | cc,n | be calculated from the longitudinal impedance of a main conductor circuit. Z c and the average of the mutual impedances from one phase conductor to an adjacent phase conductor Z
en van een fasegeleider naar een tegenoverliggende fasegeleider | and from one phase conductor to an opposite phase conductor | calculated from the longitudinal impedance of a main conductor circuit. Z c and the average of the mutual impedances from one phase conductor to an adjacent phase conductor Z cc,n
Z | Z | Z c and the average of the mutual impedances from one phase conductor to an adjacent phase conductor Z cc,n and from one phase conductor to an opposite phase conductor
cc,t | cc,t | c and the average of the mutual impedances from one phase conductor to an adjacent phase conductor Z cc,n and from one phase conductor to an opposite phase conductor Z
. | . | and the average of the mutual impedances from one phase conductor to an adjacent phase conductor Z cc,n and from one phase conductor to an opposite phase conductor Z cc,t
[ | [ | the average of the mutual impedances from one phase conductor to an adjacent phase conductor Z cc,n and from one phase conductor to an opposite phase conductor Z cc,t .
8.29 | 8.29 | average of the mutual impedances from one phase conductor to an adjacent phase conductor Z cc,n and from one phase conductor to an opposite phase conductor Z cc,t . [
] | ] | of the mutual impedances from one phase conductor to an adjacent phase conductor Z cc,n and from one phase conductor to an opposite phase conductor Z cc,t . [ 8.29
Evenzo kan de interne homopolaire impedantie van de kabel berekend worden: | Similarly, the internal homopolar impedance of the cable can be calculated: | the mutual impedances from one phase conductor to an adjacent phase conductor Z cc,n and from one phase conductor to an opposite phase conductor Z cc,t . [ 8.29 ]
[ | [ | conductor Z cc,n and from one phase conductor to an opposite phase conductor Z cc,t . [ 8.29 ] Similarly, the internal homopolar impedance of the cable can be calculated:
8.30 | 8.30 | Z cc,n and from one phase conductor to an opposite phase conductor Z cc,t . [ 8.29 ] Similarly, the internal homopolar impedance of the cable can be calculated: [
] | ] | cc,n and from one phase conductor to an opposite phase conductor Z cc,t . [ 8.29 ] Similarly, the internal homopolar impedance of the cable can be calculated: [ 8.30
8.3 Transformatoren | 8.3 Transformers | and from one phase conductor to an opposite phase conductor Z cc,t . [ 8.29 ] Similarly, the internal homopolar impedance of the cable can be calculated: [ 8.30 ]
Transformatoren bestaan in vele soorten en maten. Voor de koppeling tussen HS- en MS-niveau worden voedingstransformatoren met nominale vermogens van 10 tot 70 MVA toegepast. Dit zijn meestal transformatoren met twee wikkelingen, maar in sommige gevallen worden ook driewikkelingstransformatoren (150/50/10 kV) toegepast. De distributietransformatoren tussen MS- en LS-niveau zijn gestandaardiseerd. Deze normtransformatoren zijn er voor vermogens van 50 tot 1600 kVA. Daarnaast worden in uitgestrekte netten ook wel regeltransformatoren toegepast om het spanningsprofiel te verbeteren. | Transformers come in many types and sizes. For the connection between high-voltage (HV) and medium-voltage (MV) levels, power transformers with nominal capacities ranging from 10 to 70 MVA are used. These are usually two-winding transformers, but in some cases, three-winding transformers (150/50/10 kV) are also used. The distribution transformers between MV and low-voltage (LV) levels are standardized. These standard transformers are available for capacities from 50 to 1600 kVA. Additionally, in extensive networks, regulating transformers are sometimes used to improve the voltage profile. | one phase conductor to an opposite phase conductor Z cc,t . [ 8.29 ] Similarly, the internal homopolar impedance of the cable can be calculated: [ 8.30 ] 8.3 Transformers
8.3.1 Wikkelconfiguraties | 8.3.1 Winding Configurations | (LV) levels are standardized. These standard transformers are available for capacities from 50 to 1600 kVA. Additionally, in extensive networks, regulating transformers are sometimes used to improve the voltage profile.
De transformatorwikkelingen worden op drie manieren geschakeld, namelijk in ster-, in driehoek- en in zigzag-configuratie. Daarnaast kunnen de fasen onderling gewisseld worden zodat de fasehoek instelbaar is in stappen van 30 graden. Aangezien hier 12 mogelijkheden voor zijn, wordt dit aangeduid met het klokgetal. Ook de draairichting van het driefasenstelsel kan hierdoor omgekeerd worden. Om misverstanden te voorkomen zijn transformatoren ingedeeld naar wikkelingconfiguratie en klokgetal. | The transformer windings are connected in three ways, namely in star, delta, and zigzag configurations. Additionally, the phases can be interchanged so that the phase angle can be adjusted in steps of 30 degrees. Since there are 12 possibilities for this, it is indicated by the clock number. The rotation direction of the three-phase system can also be reversed by this means. To avoid misunderstandings, transformers are classified according to winding configuration and clock number. | standardized. These standard transformers are available for capacities from 50 to 1600 kVA. Additionally, in extensive networks, regulating transformers are sometimes used to improve the voltage profile. 8.3.1 Winding Configurations
Tabel 8.7 geeft een overzicht van de belangrijkste mogelijkheden voor transformatoren met twee wikkelingen. Hierin geeft de letter aan of de wikkelconfiguratie ster (Y), driehoek (D) of zigzag (Z) is. De hoofdletter geeft de primaire zijde aan en de kleine letter de secundaire zijde. | Table 8.7 provides an overview of the main possibilities for transformers with two windings. In this, the letter indicates whether the winding configuration is star (Y), delta (D), or zigzag (Z). The capital letter indicates the primary side, and the lowercase letter indicates the secondary side. | the clock number. The rotation direction of the three-phase system can also be reversed by this means. To avoid misunderstandings, transformers are classified according to winding configuration and clock number.
Indien bij een van de wikkelingen het sterpunt kan worden aangesloten, wordt dit aangegeven met de letter N voor de primaire wikkeling en n voor de secundaire wikkeling. Een veel gebruikte distributietransformator heeft de schakeling Dyn5. | If the neutral point of one of the windings can be connected, this is indicated by the letter N for the primary winding and n for the secondary winding. A commonly used distribution transformer has the Dyn5 configuration. | the letter indicates whether the winding configuration is star (Y), delta (D), or zigzag (Z). The capital letter indicates the primary side, and the lowercase letter indicates the secondary side.
Tabel 8.7 Wikkelconfiguraties | Table 8.7 Winding Configurations | windings can be connected, this is indicated by the letter N for the primary winding and n for the secondary winding. A commonly used distribution transformer has the Dyn5 configuration.
Klokgetal | Klokgetal | this is indicated by the letter N for the primary winding and n for the secondary winding. A commonly used distribution transformer has the Dyn5 configuration. Table 8.7 Winding Configurations
Schakeling | Schakeling | is indicated by the letter N for the primary winding and n for the secondary winding. A commonly used distribution transformer has the Dyn5 configuration. Table 8.7 Winding Configurations Klokgetal
Primair | Primair | indicated by the letter N for the primary winding and n for the secondary winding. A commonly used distribution transformer has the Dyn5 configuration. Table 8.7 Winding Configurations Klokgetal Schakeling
Secundair | Secundair | by the letter N for the primary winding and n for the secondary winding. A commonly used distribution transformer has the Dyn5 configuration. Table 8.7 Winding Configurations Klokgetal Schakeling Primair
0 | 0 | the letter N for the primary winding and n for the secondary winding. A commonly used distribution transformer has the Dyn5 configuration. Table 8.7 Winding Configurations Klokgetal Schakeling Primair Secundair
Dd0 | Dd0 | letter N for the primary winding and n for the secondary winding. A commonly used distribution transformer has the Dyn5 configuration. Table 8.7 Winding Configurations Klokgetal Schakeling Primair Secundair 0
Yy0 | Yy0 | N for the primary winding and n for the secondary winding. A commonly used distribution transformer has the Dyn5 configuration. Table 8.7 Winding Configurations Klokgetal Schakeling Primair Secundair 0 Dd0
Dz0 | Dz0 | for the primary winding and n for the secondary winding. A commonly used distribution transformer has the Dyn5 configuration. Table 8.7 Winding Configurations Klokgetal Schakeling Primair Secundair 0 Dd0 Yy0
5 | 5 | the primary winding and n for the secondary winding. A commonly used distribution transformer has the Dyn5 configuration. Table 8.7 Winding Configurations Klokgetal Schakeling Primair Secundair 0 Dd0 Yy0 Dz0
Dy5 | Dy5 | primary winding and n for the secondary winding. A commonly used distribution transformer has the Dyn5 configuration. Table 8.7 Winding Configurations Klokgetal Schakeling Primair Secundair 0 Dd0 Yy0 Dz0 5
Yd5 | Yd5 | winding and n for the secondary winding. A commonly used distribution transformer has the Dyn5 configuration. Table 8.7 Winding Configurations Klokgetal Schakeling Primair Secundair 0 Dd0 Yy0 Dz0 5 Dy5
Yz5 | Yz5 | and n for the secondary winding. A commonly used distribution transformer has the Dyn5 configuration. Table 8.7 Winding Configurations Klokgetal Schakeling Primair Secundair 0 Dd0 Yy0 Dz0 5 Dy5 Yd5
6 | 6 | n for the secondary winding. A commonly used distribution transformer has the Dyn5 configuration. Table 8.7 Winding Configurations Klokgetal Schakeling Primair Secundair 0 Dd0 Yy0 Dz0 5 Dy5 Yd5 Yz5
Dd6 | Dd6 | for the secondary winding. A commonly used distribution transformer has the Dyn5 configuration. Table 8.7 Winding Configurations Klokgetal Schakeling Primair Secundair 0 Dd0 Yy0 Dz0 5 Dy5 Yd5 Yz5 6
Yy6 | Yy6 | the secondary winding. A commonly used distribution transformer has the Dyn5 configuration. Table 8.7 Winding Configurations Klokgetal Schakeling Primair Secundair 0 Dd0 Yy0 Dz0 5 Dy5 Yd5 Yz5 6 Dd6
Dz6 | Dz6 | secondary winding. A commonly used distribution transformer has the Dyn5 configuration. Table 8.7 Winding Configurations Klokgetal Schakeling Primair Secundair 0 Dd0 Yy0 Dz0 5 Dy5 Yd5 Yz5 6 Dd6 Yy6
11 | 11 | winding. A commonly used distribution transformer has the Dyn5 configuration. Table 8.7 Winding Configurations Klokgetal Schakeling Primair Secundair 0 Dd0 Yy0 Dz0 5 Dy5 Yd5 Yz5 6 Dd6 Yy6 Dz6
Dy11 | Dy11 | A commonly used distribution transformer has the Dyn5 configuration. Table 8.7 Winding Configurations Klokgetal Schakeling Primair Secundair 0 Dd0 Yy0 Dz0 5 Dy5 Yd5 Yz5 6 Dd6 Yy6 Dz6 11
Yd11 | Yd11 | commonly used distribution transformer has the Dyn5 configuration. Table 8.7 Winding Configurations Klokgetal Schakeling Primair Secundair 0 Dd0 Yy0 Dz0 5 Dy5 Yd5 Yz5 6 Dd6 Yy6 Dz6 11 Dy11
Yz11 | Yz11 | used distribution transformer has the Dyn5 configuration. Table 8.7 Winding Configurations Klokgetal Schakeling Primair Secundair 0 Dd0 Yy0 Dz0 5 Dy5 Yd5 Yz5 6 Dd6 Yy6 Dz6 11 Dy11 Yd11
Aan hoogspanningszijde wordt meestal een sterwikkeling gekozen, omdat in die netten het sterpunt beschikbaar is en de transformator impedantie-geaard kan worden. De middenspanningsnetten hebben vaak een zwevend sterpunt en daarom zal op dit spanningsniveau meestal een driehoekswikkeling gekozen worden. Indien het middenspanningsnet toch geaard moet worden, zal dat met een aparte aardingstransformator worden gedaan. De laagspanningsnetten worden meestal hard geaard, waardoor op dit spanningsniveau voor een sterwikkeling gekozen wordt. De zigzagwikkeling komt minder vaak voor, behoudens in aardingstransformatoren. | On the high voltage side, a star winding is usually chosen because the star point is available in those networks and the transformer can be impedance-grounded. Medium voltage networks often have a floating star point, and therefore a delta winding is usually chosen at this voltage level. If the medium voltage network still needs to be grounded, this will be done with a separate grounding transformer. Low voltage networks are usually solidly grounded, so a star winding is chosen at this voltage level. The zigzag winding is less common, except in grounding transformers. | distribution transformer has the Dyn5 configuration. Table 8.7 Winding Configurations Klokgetal Schakeling Primair Secundair 0 Dd0 Yy0 Dz0 5 Dy5 Yd5 Yz5 6 Dd6 Yy6 Dz6 11 Dy11 Yd11 Yz11
Bij het parallel schakelen van transformatoren moet goed op het klokgetal en de wikkelconfiguratie worden gelet. Het is mogelijk om transformatoren van verschillende wikkelconfiguratie parallel te schakelen. Dit mag echter niet zonder meer plaatsvinden. Hierbij moeten de aansluitklemmen van de verschillende transformatoren op de juiste wijze verwisseld worden om alsnog aan de secundaire zijde van de transformator het juiste klokgetal en fasevolgorde te verkrijgen. Onderstaand diagram geeft als voorbeeld het parallel schakelen van een Dy5 en een Dy11 transformator. De parallelschakeling wordt gerealiseerd door bij de Dy11 transformator aan primaire zijde de aansluiting op klemmen | When paralleling transformers, careful attention must be paid to the clock number and winding configuration. It is possible to parallel transformers with different winding configurations. However, this should not be done without proper consideration. The terminals of the different transformers must be correctly swapped to achieve the correct clock number and phase sequence on the secondary side of the transformer. The diagram below provides an example of paralleling a Dy5 and a Dy11 transformer. The paralleling is achieved by connecting the primary side terminals of the Dy11 transformer. | separate grounding transformer. Low voltage networks are usually solidly grounded, so a star winding is chosen at this voltage level. The zigzag winding is less common, except in grounding transformers.
U | U | the transformer. The diagram below provides an example of paralleling a Dy5 and a Dy11 transformer. The paralleling is achieved by connecting the primary side terminals of the Dy11 transformer.
en | en | transformer. The diagram below provides an example of paralleling a Dy5 and a Dy11 transformer. The paralleling is achieved by connecting the primary side terminals of the Dy11 transformer. U
V | V | The diagram below provides an example of paralleling a Dy5 and a Dy11 transformer. The paralleling is achieved by connecting the primary side terminals of the Dy11 transformer. U en
te verwisselen en aan secundaire zijde de klemmen | to swap and on the secondary side the terminals | diagram below provides an example of paralleling a Dy5 and a Dy11 transformer. The paralleling is achieved by connecting the primary side terminals of the Dy11 transformer. U en V
v | v | and a Dy11 transformer. The paralleling is achieved by connecting the primary side terminals of the Dy11 transformer. U en V to swap and on the secondary side the terminals
en | en | a Dy11 transformer. The paralleling is achieved by connecting the primary side terminals of the Dy11 transformer. U en V to swap and on the secondary side the terminals v
w | w | Dy11 transformer. The paralleling is achieved by connecting the primary side terminals of the Dy11 transformer. U en V to swap and on the secondary side the terminals v en
te verwisselen. | to swap. | transformer. The paralleling is achieved by connecting the primary side terminals of the Dy11 transformer. U en V to swap and on the secondary side the terminals v en w
Figuur 8.4 Parallel schakelen van een Dy5 en een Dy11 transformator | Figure 8.4 Paralleling a Dy5 and a Dy11 transformer | paralleling is achieved by connecting the primary side terminals of the Dy11 transformer. U en V to swap and on the secondary side the terminals v en w to swap.
8.3.2 Overzetverhouding | 8.3.2 Transformation Ratio | of the Dy11 transformer. U en V to swap and on the secondary side the terminals v en w to swap. Figure 8.4 Paralleling a Dy5 and a Dy11 transformer
Naast de wikkelconfiguratie wordt de transformator gekenmerkt door zijn nominale vermogen en de nominale primaire en secundaire spanning. De overzetverhouding is het quotiënt van de primaire en de secundaire spanning: | In addition to the winding configuration, the transformer is characterized by its nominal power and the nominal primary and secondary voltage. The transformation ratio is the quotient of the primary and secondary voltage: | transformer. U en V to swap and on the secondary side the terminals v en w to swap. Figure 8.4 Paralleling a Dy5 and a Dy11 transformer 8.3.2 Transformation Ratio
[ | [ | the winding configuration, the transformer is characterized by its nominal power and the nominal primary and secondary voltage. The transformation ratio is the quotient of the primary and secondary voltage:
8.31 | 8.31 | winding configuration, the transformer is characterized by its nominal power and the nominal primary and secondary voltage. The transformation ratio is the quotient of the primary and secondary voltage: [
] | ] | configuration, the transformer is characterized by its nominal power and the nominal primary and secondary voltage. The transformation ratio is the quotient of the primary and secondary voltage: [ 8.31
De nominale spanningen gelden voor de transformator en niet voor de wikkelingen. De nominale spanningen zijn gekoppelde spanningen. Dat houdt in dat bij een driehoekswikkeling deze spanning ook over elk van de wikkelingen staat. Bij een sterwikkeling is de spanning over een wikkeling √3 maal kleiner dan de nominale spanning. | The nominal voltages apply to the transformer and not to the windings. The nominal voltages are line-to-line voltages. This means that in a delta winding, this voltage is also present across each of the windings. In a star winding, the voltage across a winding is √3 times smaller than the nominal voltage. | the transformer is characterized by its nominal power and the nominal primary and secondary voltage. The transformation ratio is the quotient of the primary and secondary voltage: [ 8.31 ]
De meeste transformatoren zijn voorzien van een trappenschakelaar, waarmee de overzetverhouding in stappen geregeld kan worden. Indien de trappenschakelaar in de neutrale stand staat, heeft de transformator de nominale overzetverhouding. Door een andere trapstand te kiezen verandert de overzetverhouding met het aantal trappen maal de spanning per trap. Indien een enkele trap overeenkomt met een spanning ΔV, is de overzetverhouding voor n trappen ten opzichte van de neutrale stand: | Most transformers are equipped with a tap changer, which allows the turns ratio to be adjusted in steps. If the tap changer is in the neutral position, the transformer has the nominal turns ratio. By selecting a different tap position, the turns ratio changes by the number of steps times the voltage per step. If a single step corresponds to a voltage ΔV, the turns ratio for n steps relative to the neutral position is: | a delta winding, this voltage is also present across each of the windings. In a star winding, the voltage across a winding is √3 times smaller than the nominal voltage.
[ | [ | the number of steps times the voltage per step. If a single step corresponds to a voltage ΔV, the turns ratio for n steps relative to the neutral position is:
8.32 | 8.32 | number of steps times the voltage per step. If a single step corresponds to a voltage ΔV, the turns ratio for n steps relative to the neutral position is: [
] | ] | of steps times the voltage per step. If a single step corresponds to a voltage ΔV, the turns ratio for n steps relative to the neutral position is: [ 8.32
De aftakkingen zijn genummerd en meestal zodanig dat een hoger nummer correspondeert met een hogere secundaire spanning, ook al bevindt de trappenschakelaar zich aan de primaire zijde. De spanningsverandering per regeltrap bedraagt meestal 1,3 tot 2% van de nominale spanning. | The taps are numbered and usually arranged so that a higher number corresponds to a higher secondary voltage, even though the tap changer is on the primary side. The voltage change per step is usually 1.3 to 2% of the nominal voltage. | steps times the voltage per step. If a single step corresponds to a voltage ΔV, the turns ratio for n steps relative to the neutral position is: [ 8.32 ]
Een HS/MS-voedingstransformator wordt meestal uitgerust met een regelbare trappenschakelaar, die wordt aangestuurd door een regeling die de spanning op de MS-zijde meet en binnen grenzen probeert te houden. Het principe is in paragraaf 4.3 toegelicht. Omdat de regeling een discrete trappenschakelaar aanstuurt, is het niet mogelijk de spanning aan de secundaire zijde exact een gewenste waarde te laten zijn. Het is zelfs zo dat twee of meer trapstanden mogelijk zijn, afhankelijk van de trapgrootte ten opzichte van de te regelen spanningsband. | A HV/MV power transformer is usually equipped with an adjustable tap changer, which is controlled by a system that measures the voltage on the MV side and tries to keep it within limits. The principle is explained in paragraph 4.3. Because the system controls a discrete tap changer, it is not possible to set the voltage on the secondary side to an exact desired value. In fact, two or more tap positions may be possible, depending on the step size relative to the voltage regulation band. | corresponds to a higher secondary voltage, even though the tap changer is on the primary side. The voltage change per step is usually 1.3 to 2% of the nominal voltage.
8.3.3 Parameters voor transformatoren met twee wikkelingen | 8.3.3 Parameters for transformers with two windings | on the secondary side to an exact desired value. In fact, two or more tap positions may be possible, depending on the step size relative to the voltage regulation band.
Met het nominale vermogen en de nominale spanningen zijn de nominale stromen aan primaire en secundaire zijde uit te rekenen: | With the nominal power and the nominal voltages, the nominal currents on the primary and secondary sides can be calculated: | desired value. In fact, two or more tap positions may be possible, depending on the step size relative to the voltage regulation band. 8.3.3 Parameters for transformers with two windings
[ | [ | voltage regulation band. 8.3.3 Parameters for transformers with two windings With the nominal power and the nominal voltages, the nominal currents on the primary and secondary sides can be calculated:
8.33 | 8.33 | regulation band. 8.3.3 Parameters for transformers with two windings With the nominal power and the nominal voltages, the nominal currents on the primary and secondary sides can be calculated: [
] | ] | band. 8.3.3 Parameters for transformers with two windings With the nominal power and the nominal voltages, the nominal currents on the primary and secondary sides can be calculated: [ 8.33
Twee andere belangrijk kengetallen zijn de relatieve kortsluitspanning | Two other important parameters are the relative short-circuit voltage | 8.3.3 Parameters for transformers with two windings With the nominal power and the nominal voltages, the nominal currents on the primary and secondary sides can be calculated: [ 8.33 ]
u | u | nominal power and the nominal voltages, the nominal currents on the primary and secondary sides can be calculated: [ 8.33 ] Two other important parameters are the relative short-circuit voltage
k | k | power and the nominal voltages, the nominal currents on the primary and secondary sides can be calculated: [ 8.33 ] Two other important parameters are the relative short-circuit voltage u
en het kortsluitverlies | and the short-circuit loss | and the nominal voltages, the nominal currents on the primary and secondary sides can be calculated: [ 8.33 ] Two other important parameters are the relative short-circuit voltage u k
P | P | the nominal currents on the primary and secondary sides can be calculated: [ 8.33 ] Two other important parameters are the relative short-circuit voltage u k and the short-circuit loss
k | k | nominal currents on the primary and secondary sides can be calculated: [ 8.33 ] Two other important parameters are the relative short-circuit voltage u k and the short-circuit loss P
. De kortsluitspanning is de spanning die op de primaire zijde van de transformator moet worden aangebracht, zodanig dat bij een kortgesloten secundaire zijde de nominale stroom vloeit. De relatieve kortsluitspanning wordt uitgedrukt in procenten van de nominale spanning. Het kortsluitverlies, ook wel koperverlies genoemd, is verantwoordelijk voor de opwarming van de transformator als gevolg van het getransporteerde vermogen. Met deze twee kengetallen wordt de transformatorimpedantie berekend: | The short-circuit voltage is the voltage that must be applied to the primary side of the transformer so that the nominal current flows when the secondary side is short-circuited. The relative short-circuit voltage is expressed as a percentage of the nominal voltage. The short-circuit loss, also known as copper loss, is responsible for the heating of the transformer due to the power being transmitted. These two parameters are used to calculate the transformer impedance: | currents on the primary and secondary sides can be calculated: [ 8.33 ] Two other important parameters are the relative short-circuit voltage u k and the short-circuit loss P k
[ | [ | loss, also known as copper loss, is responsible for the heating of the transformer due to the power being transmitted. These two parameters are used to calculate the transformer impedance:
8.34 | 8.34 | also known as copper loss, is responsible for the heating of the transformer due to the power being transmitted. These two parameters are used to calculate the transformer impedance: [
] | ] | known as copper loss, is responsible for the heating of the transformer due to the power being transmitted. These two parameters are used to calculate the transformer impedance: [ 8.34
In bovenstaande vergelijkingen is de transformatorimpedantie betrokken op de secundaire zijde. Indien de transformatorimpedantie betrokken zou moeten worden op de primaire zijde, wordt dezelfde berekening uitgevoerd met de nominale spanning aan primaire zijde. De relatie tussen de twee waarden is de overzetverhouding in het kwadraat: | In the above equations, the transformer impedance is referred to the secondary side. If the transformer impedance needs to be referred to the primary side, the same calculation is performed using the nominal voltage on the primary side. The relationship between the two values is the square of the turns ratio: | as copper loss, is responsible for the heating of the transformer due to the power being transmitted. These two parameters are used to calculate the transformer impedance: [ 8.34 ]
[ | [ | to the primary side, the same calculation is performed using the nominal voltage on the primary side. The relationship between the two values is the square of the turns ratio:
8.35 | 8.35 | the primary side, the same calculation is performed using the nominal voltage on the primary side. The relationship between the two values is the square of the turns ratio: [
] | ] | primary side, the same calculation is performed using the nominal voltage on the primary side. The relationship between the two values is the square of the turns ratio: [ 8.35
Het koperverlies van de transformator wordt berekend met de weerstand en de actuele stroom, hetzij aan de primaire dan wel aan de secundaire zijde: | The copper loss of the transformer is calculated using the resistance and the actual current, either on the primary or the secondary side: | side, the same calculation is performed using the nominal voltage on the primary side. The relationship between the two values is the square of the turns ratio: [ 8.35 ]
[ | [ | of the turns ratio: [ 8.35 ] The copper loss of the transformer is calculated using the resistance and the actual current, either on the primary or the secondary side:
8.36 | 8.36 | the turns ratio: [ 8.35 ] The copper loss of the transformer is calculated using the resistance and the actual current, either on the primary or the secondary side: [
] | ] | turns ratio: [ 8.35 ] The copper loss of the transformer is calculated using the resistance and the actual current, either on the primary or the secondary side: [ 8.36
De transformator kent ook een nullastverlies. Dit wordt veroorzaakt door het wervelstroomverlies | The transformer also has a no-load loss. This is caused by eddy current loss. | ratio: [ 8.35 ] The copper loss of the transformer is calculated using the resistance and the actual current, either on the primary or the secondary side: [ 8.36 ]
P | P | resistance and the actual current, either on the primary or the secondary side: [ 8.36 ] The transformer also has a no-load loss. This is caused by eddy current loss.
nullast | nullast | and the actual current, either on the primary or the secondary side: [ 8.36 ] The transformer also has a no-load loss. This is caused by eddy current loss. P
in de ijzerkern. Dit wervelstroomverlies wordt gemodelleerd met een hoofdveldweerstand R | in the iron core. This eddy current loss is modeled with a main field resistance R | the actual current, either on the primary or the secondary side: [ 8.36 ] The transformer also has a no-load loss. This is caused by eddy current loss. P nullast
f | f | also has a no-load loss. This is caused by eddy current loss. P nullast in the iron core. This eddy current loss is modeled with a main field resistance R
. Daarnaast bestaat de magnetiseringstroom, die veroorzaakt wordt door de hoofdveldreactantie | . Additionally, there is the magnetizing current, which is caused by the main field reactance | has a no-load loss. This is caused by eddy current loss. P nullast in the iron core. This eddy current loss is modeled with a main field resistance R f
X | X | iron core. This eddy current loss is modeled with a main field resistance R f . Additionally, there is the magnetizing current, which is caused by the main field reactance
μ | μ | core. This eddy current loss is modeled with a main field resistance R f . Additionally, there is the magnetizing current, which is caused by the main field reactance X
. Het wervelstroomverlies en de magnetiseringstroom worden samen bij nullast gemeten in de nullaststroom | The eddy current loss and the magnetizing current are measured together at no load in the no-load current. | This eddy current loss is modeled with a main field resistance R f . Additionally, there is the magnetizing current, which is caused by the main field reactance X μ
I | I | magnetizing current, which is caused by the main field reactance X μ The eddy current loss and the magnetizing current are measured together at no load in the no-load current.
nullast | nullast | current, which is caused by the main field reactance X μ The eddy current loss and the magnetizing current are measured together at no load in the no-load current. I
. Het nullastverlies en de nullaststroom worden gemeten bij nominale spanning. Dit leidt tot het vervangingsschema van figuur 8.5. | The no-load loss and the no-load current are measured at nominal voltage. This leads to the equivalent circuit of figure 8.5. | which is caused by the main field reactance X μ The eddy current loss and the magnetizing current are measured together at no load in the no-load current. I nullast
Figuur 8.5 Vervangingsschema van de transformator | Figure 8.5 Equivalent circuit of the transformer | at no load in the no-load current. I nullast The no-load loss and the no-load current are measured at nominal voltage. This leads to the equivalent circuit of figure 8.5.
De hoofdveldweerstand en de hoofdveldreactantie laten zich berekenen uit hun parallelschakeling en de meting van | The main field resistance and the main field reactance can be calculated from their parallel connection and the measurement of | I nullast The no-load loss and the no-load current are measured at nominal voltage. This leads to the equivalent circuit of figure 8.5. Figure 8.5 Equivalent circuit of the transformer
P | P | of figure 8.5. Figure 8.5 Equivalent circuit of the transformer The main field resistance and the main field reactance can be calculated from their parallel connection and the measurement of
nullast | nullast | figure 8.5. Figure 8.5 Equivalent circuit of the transformer The main field resistance and the main field reactance can be calculated from their parallel connection and the measurement of P
en | en | 8.5. Figure 8.5 Equivalent circuit of the transformer The main field resistance and the main field reactance can be calculated from their parallel connection and the measurement of P nullast
I | I | Figure 8.5 Equivalent circuit of the transformer The main field resistance and the main field reactance can be calculated from their parallel connection and the measurement of P nullast en
nullast | nullast | 8.5 Equivalent circuit of the transformer The main field resistance and the main field reactance can be calculated from their parallel connection and the measurement of P nullast en I
. Indien de nullastmeting aan de secundaire zijde van de transformator wordt uitgevoerd, wordt de nullastimpedantie berekend uit: | If the no-load measurement is performed on the secondary side of the transformer, the no-load impedance is calculated from: | Equivalent circuit of the transformer The main field resistance and the main field reactance can be calculated from their parallel connection and the measurement of P nullast en I nullast
[ | [ | parallel connection and the measurement of P nullast en I nullast If the no-load measurement is performed on the secondary side of the transformer, the no-load impedance is calculated from:
8.37 | 8.37 | connection and the measurement of P nullast en I nullast If the no-load measurement is performed on the secondary side of the transformer, the no-load impedance is calculated from: [
] | ] | and the measurement of P nullast en I nullast If the no-load measurement is performed on the secondary side of the transformer, the no-load impedance is calculated from: [ 8.37
De hoofdveldweerstand | The main field resistance | the measurement of P nullast en I nullast If the no-load measurement is performed on the secondary side of the transformer, the no-load impedance is calculated from: [ 8.37 ]
R | R | nullast en I nullast If the no-load measurement is performed on the secondary side of the transformer, the no-load impedance is calculated from: [ 8.37 ] The main field resistance
f | f | en I nullast If the no-load measurement is performed on the secondary side of the transformer, the no-load impedance is calculated from: [ 8.37 ] The main field resistance R
en de magnetiseringsreactantie | and the magnetizing reactance | I nullast If the no-load measurement is performed on the secondary side of the transformer, the no-load impedance is calculated from: [ 8.37 ] The main field resistance R f
X | X | no-load measurement is performed on the secondary side of the transformer, the no-load impedance is calculated from: [ 8.37 ] The main field resistance R f and the magnetizing reactance
m | m | measurement is performed on the secondary side of the transformer, the no-load impedance is calculated from: [ 8.37 ] The main field resistance R f and the magnetizing reactance X
worden dan berekend met: | are then calculated using: | is performed on the secondary side of the transformer, the no-load impedance is calculated from: [ 8.37 ] The main field resistance R f and the magnetizing reactance X m
[ | [ | secondary side of the transformer, the no-load impedance is calculated from: [ 8.37 ] The main field resistance R f and the magnetizing reactance X m are then calculated using:
8.38 | 8.38 | side of the transformer, the no-load impedance is calculated from: [ 8.37 ] The main field resistance R f and the magnetizing reactance X m are then calculated using: [
] | ] | of the transformer, the no-load impedance is calculated from: [ 8.37 ] The main field resistance R f and the magnetizing reactance X m are then calculated using: [ 8.38
[ | [ | the transformer, the no-load impedance is calculated from: [ 8.37 ] The main field resistance R f and the magnetizing reactance X m are then calculated using: [ 8.38 ]
8.39 | 8.39 | transformer, the no-load impedance is calculated from: [ 8.37 ] The main field resistance R f and the magnetizing reactance X m are then calculated using: [ 8.38 ] [
] | ] | the no-load impedance is calculated from: [ 8.37 ] The main field resistance R f and the magnetizing reactance X m are then calculated using: [ 8.38 ] [ 8.39
Het actuele nullastverlies is dus afhankelijk van de spanning en kan dan eenvoudig berekend worden met: | The actual no-load loss is therefore dependent on the voltage and can then be easily calculated with: | no-load impedance is calculated from: [ 8.37 ] The main field resistance R f and the magnetizing reactance X m are then calculated using: [ 8.38 ] [ 8.39 ]
[ | [ | reactance X m are then calculated using: [ 8.38 ] [ 8.39 ] The actual no-load loss is therefore dependent on the voltage and can then be easily calculated with:
8.40 | 8.40 | X m are then calculated using: [ 8.38 ] [ 8.39 ] The actual no-load loss is therefore dependent on the voltage and can then be easily calculated with: [
] | ] | m are then calculated using: [ 8.38 ] [ 8.39 ] The actual no-load loss is therefore dependent on the voltage and can then be easily calculated with: [ 8.40
Samenvattend bestaat het verlies van de transformator uit twee delen. Een deel, het koperverlies, is kwadratisch afhankelijk van de stroom door de transformator en hangt af van de bedrijfstijd van de transformator. Het andere deel, het nullastverlies, is kwadratisch afhankelijk van de spanning en is altijd aanwezig zolang de transformator in bedrijf is: | In summary, the loss of the transformer consists of two parts. One part, the copper loss, is quadratically dependent on the current through the transformer and depends on the operating time of the transformer. The other part, the no-load loss, is quadratically dependent on the voltage and is always present as long as the transformer is in operation: | are then calculated using: [ 8.38 ] [ 8.39 ] The actual no-load loss is therefore dependent on the voltage and can then be easily calculated with: [ 8.40 ]
[ | [ | the operating time of the transformer. The other part, the no-load loss, is quadratically dependent on the voltage and is always present as long as the transformer is in operation:
8.41 | 8.41 | operating time of the transformer. The other part, the no-load loss, is quadratically dependent on the voltage and is always present as long as the transformer is in operation: [
] | ] | time of the transformer. The other part, the no-load loss, is quadratically dependent on the voltage and is always present as long as the transformer is in operation: [ 8.41
8.3.4 Parameters voor transformatoren met drie wikkelingen | 8.3.4 Parameters for transformers with three windings | of the transformer. The other part, the no-load loss, is quadratically dependent on the voltage and is always present as long as the transformer is in operation: [ 8.41 ]
De meeste transformatoren zijn geconstrueerd met twee wikkelingen. Veel voedingstransformatoren en industriële transformatoren die converters en gelijkrichters voeden zijn uitgevoerd met drie wikkelingen. Een voedingstransformator is vaak van het type YNynd, waarbij de primaire wikkeling en de secundaire wikkeling een sterschakeling met uitgevoerd sterpunt hebben en de tertiaire wikkeling een driehoekschakeling heeft met zwevend sterpunt. Deze transformator is eventueel regelbaar met een trappenschakelaar op hoogspanningsniveau op de primaire wikkeling. De secundaire wikkeling kan een instelbare trappenschakelaar hebben die niet tijdens bedrijf versteld wordt. Een transformator die een converter of een gelijkrichter voedt is in distributienetten meestal niet regelbaar. | Most transformers are constructed with two windings. Many power transformers and industrial transformers that supply converters and rectifiers are equipped with three windings. A power transformer is often of the YNynd type, where the primary winding and the secondary winding have a star connection with a grounded neutral point, and the tertiary winding has a delta connection with a floating neutral point. This transformer can be adjustable with a tap changer at the high voltage level on the primary winding. The secondary winding can have an adjustable tap changer that is not adjusted during operation. A transformer that supplies a converter or a rectifier is usually not adjustable in distribution networks. | no-load loss, is quadratically dependent on the voltage and is always present as long as the transformer is in operation: [ 8.41 ] 8.3.4 Parameters for transformers with three windings
De vermogens die de drie wikkelingen kunnen voeren zijn meestal niet gelijk aan elkaar. Vaak heeft de tertiaire wikkeling een lager vermogen. Hierom wordt van elke wikkeling het nominale vermogen aangegeven. Als gevolg zijn de doorgaande vermogens telkens gelijk aan het minimum van de twee betreffende wikkelingen: | The power that the three windings can handle is usually not equal. Often, the tertiary winding has a lower power rating. Therefore, the nominal power of each winding is specified. As a result, the through powers are always equal to the minimum of the two respective windings: | secondary winding can have an adjustable tap changer that is not adjusted during operation. A transformer that supplies a converter or a rectifier is usually not adjustable in distribution networks.
[ | [ | a lower power rating. Therefore, the nominal power of each winding is specified. As a result, the through powers are always equal to the minimum of the two respective windings:
8.42 | 8.42 | lower power rating. Therefore, the nominal power of each winding is specified. As a result, the through powers are always equal to the minimum of the two respective windings: [
] | ] | power rating. Therefore, the nominal power of each winding is specified. As a result, the through powers are always equal to the minimum of the two respective windings: [ 8.42
Terwijl bij de transformator met twee wikkelingen maar één meting nodig is voor het vaststellen van de kortsluitspanning, zijn bij de driewikkelingstransformator drie metingen nodig. De kortsluitspanning wordt gemeten aan twee van de drie wikkelingen, waarbij de wikkeling met het laagste vermogen wordt kortgesloten. De derde wikkeling blijft open. Op de wikkeling met het hoogste vermogen wordt dan een zodanige spanning aangesloten dat in de wikkeling met het laagste vermogen de nominale stroom vloeit. Kortsluitspanning en kortsluitvermogen zijn steeds gedefinieerd in een vaste richting: primair - secundair (1-2), primair - tertiair (1-3) en secundair - tertiair (2-3). Vaak hebben | While only one measurement is needed to determine the short-circuit voltage in a two-winding transformer, three measurements are required for a three-winding transformer. The short-circuit voltage is measured on two of the three windings, with the winding having the lowest power being short-circuited. The third winding remains open. A voltage is then applied to the winding with the highest power such that the nominal current flows in the winding with the lowest power. Short-circuit voltage and short-circuit power are always defined in a fixed direction: primary - secondary (1-2), primary - tertiary (1-3), and secondary - tertiary (2-3). Often, | rating. Therefore, the nominal power of each winding is specified. As a result, the through powers are always equal to the minimum of the two respective windings: [ 8.42 ]
u | u | with the lowest power. Short-circuit voltage and short-circuit power are always defined in a fixed direction: primary - secondary (1-2), primary - tertiary (1-3), and secondary - tertiary (2-3). Often,
k,ij | k,ij | the lowest power. Short-circuit voltage and short-circuit power are always defined in a fixed direction: primary - secondary (1-2), primary - tertiary (1-3), and secondary - tertiary (2-3). Often, u
en | en | lowest power. Short-circuit voltage and short-circuit power are always defined in a fixed direction: primary - secondary (1-2), primary - tertiary (1-3), and secondary - tertiary (2-3). Often, u k,ij
P | P | power. Short-circuit voltage and short-circuit power are always defined in a fixed direction: primary - secondary (1-2), primary - tertiary (1-3), and secondary - tertiary (2-3). Often, u k,ij en
k,ij | k,ij | Short-circuit voltage and short-circuit power are always defined in a fixed direction: primary - secondary (1-2), primary - tertiary (1-3), and secondary - tertiary (2-3). Often, u k,ij en P
betrekking op het (kleinere)doorgaande vermogen van wikkeling | refers to the (smaller) continuous power of the winding | voltage and short-circuit power are always defined in a fixed direction: primary - secondary (1-2), primary - tertiary (1-3), and secondary - tertiary (2-3). Often, u k,ij en P k,ij
i | i | fixed direction: primary - secondary (1-2), primary - tertiary (1-3), and secondary - tertiary (2-3). Often, u k,ij en P k,ij refers to the (smaller) continuous power of the winding
naar wikkeling | to winding | direction: primary - secondary (1-2), primary - tertiary (1-3), and secondary - tertiary (2-3). Often, u k,ij en P k,ij refers to the (smaller) continuous power of the winding i
j | j | - secondary (1-2), primary - tertiary (1-3), and secondary - tertiary (2-3). Often, u k,ij en P k,ij refers to the (smaller) continuous power of the winding i to winding
. Het komt voor dat in beproevingsrapporten | . It happens that in test reports | secondary (1-2), primary - tertiary (1-3), and secondary - tertiary (2-3). Often, u k,ij en P k,ij refers to the (smaller) continuous power of the winding i to winding j
u | u | secondary - tertiary (2-3). Often, u k,ij en P k,ij refers to the (smaller) continuous power of the winding i to winding j . It happens that in test reports
k,ij | k,ij | - tertiary (2-3). Often, u k,ij en P k,ij refers to the (smaller) continuous power of the winding i to winding j . It happens that in test reports u
en | en | tertiary (2-3). Often, u k,ij en P k,ij refers to the (smaller) continuous power of the winding i to winding j . It happens that in test reports u k,ij
P | P | (2-3). Often, u k,ij en P k,ij refers to the (smaller) continuous power of the winding i to winding j . It happens that in test reports u k,ij en
k,ij | k,ij | Often, u k,ij en P k,ij refers to the (smaller) continuous power of the winding i to winding j . It happens that in test reports u k,ij en P
niet op het (kleinere) doorgaande vermogen zijn betrokken, maar op het vermogen van de wikkeling met het grootste vermogen, bijvoorbeeld | are not related to the (smaller) continuous power, but to the power of the winding with the highest power, for example | u k,ij en P k,ij refers to the (smaller) continuous power of the winding i to winding j . It happens that in test reports u k,ij en P k,ij
u | u | that in test reports u k,ij en P k,ij are not related to the (smaller) continuous power, but to the power of the winding with the highest power, for example
k,ij,groot | k,ij,large | in test reports u k,ij en P k,ij are not related to the (smaller) continuous power, but to the power of the winding with the highest power, for example u
en | en | test reports u k,ij en P k,ij are not related to the (smaller) continuous power, but to the power of the winding with the highest power, for example u k,ij,large
P | P | reports u k,ij en P k,ij are not related to the (smaller) continuous power, but to the power of the winding with the highest power, for example u k,ij,large en
k,ij,groot | k,ij,large | u k,ij en P k,ij are not related to the (smaller) continuous power, but to the power of the winding with the highest power, for example u k,ij,large en P
. In dat geval moeten | . In that case, must | k,ij en P k,ij are not related to the (smaller) continuous power, but to the power of the winding with the highest power, for example u k,ij,large en P k,ij,large
u | u | not related to the (smaller) continuous power, but to the power of the winding with the highest power, for example u k,ij,large en P k,ij,large . In that case, must
k,ij,groot | k,ij,large | related to the (smaller) continuous power, but to the power of the winding with the highest power, for example u k,ij,large en P k,ij,large . In that case, must u
en | en | to the (smaller) continuous power, but to the power of the winding with the highest power, for example u k,ij,large en P k,ij,large . In that case, must u k,ij,large
P | P | the (smaller) continuous power, but to the power of the winding with the highest power, for example u k,ij,large en P k,ij,large . In that case, must u k,ij,large en
k,ij,groot | k,ij,large | (smaller) continuous power, but to the power of the winding with the highest power, for example u k,ij,large en P k,ij,large . In that case, must u k,ij,large en P
worden omgerekend naar het betreffende (kleinere) doorgaande vermogen volgens onderstaande formules. De spanning komt in deze omzetting niet voor. | must be converted to the corresponding (smaller) continuous power according to the formulas below. The voltage does not appear in this conversion. | continuous power, but to the power of the winding with the highest power, for example u k,ij,large en P k,ij,large . In that case, must u k,ij,large en P k,ij,large
[ | [ | that case, must u k,ij,large en P k,ij,large must be converted to the corresponding (smaller) continuous power according to the formulas below. The voltage does not appear in this conversion.
8.43 | 8.43 | case, must u k,ij,large en P k,ij,large must be converted to the corresponding (smaller) continuous power according to the formulas below. The voltage does not appear in this conversion. [
] | ] | must u k,ij,large en P k,ij,large must be converted to the corresponding (smaller) continuous power according to the formulas below. The voltage does not appear in this conversion. [ 8.43
De transformatorimpedanties worden afgeleid uit de kortsluitspanning en het kortsluitverlies. Eerst worden de groottes van de impedanties bepaald. Vervolgens de weerstanden en daaruit de reactanties. Ten behoeve van de berekeningen worden de transformatorimpedanties meestal op eenzelfde spanningsniveau betrokken. Onderstaande formules geven de berekening voor | The transformer impedances are derived from the short-circuit voltage and the short-circuit loss. First, the magnitudes of the impedances are determined. Next, the resistances are calculated, and from those, the reactances. For the purpose of the calculations, the transformer impedances are usually referenced to the same voltage level. The formulas below provide the calculation for | u k,ij,large en P k,ij,large must be converted to the corresponding (smaller) continuous power according to the formulas below. The voltage does not appear in this conversion. [ 8.43 ]
Z | Z | calculated, and from those, the reactances. For the purpose of the calculations, the transformer impedances are usually referenced to the same voltage level. The formulas below provide the calculation for
T | T | and from those, the reactances. For the purpose of the calculations, the transformer impedances are usually referenced to the same voltage level. The formulas below provide the calculation for Z
en | en | from those, the reactances. For the purpose of the calculations, the transformer impedances are usually referenced to the same voltage level. The formulas below provide the calculation for Z T
R | R | those, the reactances. For the purpose of the calculations, the transformer impedances are usually referenced to the same voltage level. The formulas below provide the calculation for Z T en
T | T | the reactances. For the purpose of the calculations, the transformer impedances are usually referenced to the same voltage level. The formulas below provide the calculation for Z T en R
, betrokken op de primaire zijde (1). | , referred to the primary side (1). | reactances. For the purpose of the calculations, the transformer impedances are usually referenced to the same voltage level. The formulas below provide the calculation for Z T en R T
[ | [ | the transformer impedances are usually referenced to the same voltage level. The formulas below provide the calculation for Z T en R T , referred to the primary side (1).
8.44 | 8.44 | transformer impedances are usually referenced to the same voltage level. The formulas below provide the calculation for Z T en R T , referred to the primary side (1). [
] | ] | impedances are usually referenced to the same voltage level. The formulas below provide the calculation for Z T en R T , referred to the primary side (1). [ 8.44
Tenslotte worden de reactantie uit | Finally, the reactance is | are usually referenced to the same voltage level. The formulas below provide the calculation for Z T en R T , referred to the primary side (1). [ 8.44 ]
Z | Z | the same voltage level. The formulas below provide the calculation for Z T en R T , referred to the primary side (1). [ 8.44 ] Finally, the reactance is
T,ij | T,ij | same voltage level. The formulas below provide the calculation for Z T en R T , referred to the primary side (1). [ 8.44 ] Finally, the reactance is Z
en | en | voltage level. The formulas below provide the calculation for Z T en R T , referred to the primary side (1). [ 8.44 ] Finally, the reactance is Z T,ij
R | R | level. The formulas below provide the calculation for Z T en R T , referred to the primary side (1). [ 8.44 ] Finally, the reactance is Z T,ij en
T,ij | T,ij | The formulas below provide the calculation for Z T en R T , referred to the primary side (1). [ 8.44 ] Finally, the reactance is Z T,ij en R
bepaald: | determined: | formulas below provide the calculation for Z T en R T , referred to the primary side (1). [ 8.44 ] Finally, the reactance is Z T,ij en R T,ij
[ | [ | below provide the calculation for Z T en R T , referred to the primary side (1). [ 8.44 ] Finally, the reactance is Z T,ij en R T,ij determined:
8.45 | 8.45 | provide the calculation for Z T en R T , referred to the primary side (1). [ 8.44 ] Finally, the reactance is Z T,ij en R T,ij determined: [
] | ] | the calculation for Z T en R T , referred to the primary side (1). [ 8.44 ] Finally, the reactance is Z T,ij en R T,ij determined: [ 8.45
Figuur 8.6 geeft het vervangingsschema voor de driewikkelingstransformator, waarbij de impedanties betrokken zijn op de primaire zijde. In dit schema is de overzetverhouding weggelaten. Dit schema is dan ook bruikbaar voor berekeningen die betrokken zijn op een enkel spanningsniveau, bijvoorbeeld aan de primaire zijde. Voor toepassing van dit vervangingsschema moeten alle impedanties op dat zelfde spanningsniveau betrokken zijn. Het vervangingsschema is ook toepasbaar voor een ander spanningsniveau, maar dan moeten de impedanties op de bij dat spanningsniveau behorende zijde betrokken zijn. De impedanties worden dan berekend door in de bovenstaande formules in plaats van | Figure 8.6 provides the equivalent circuit for the three-winding transformer, with the impedances referred to the primary side. In this diagram, the turns ratio is omitted. This diagram is therefore useful for calculations that are referred to a single voltage level, for example, on the primary side. For the application of this equivalent circuit, all impedances must be referred to that same voltage level. The equivalent circuit is also applicable for another voltage level, but then the impedances must be referred to the side corresponding to that voltage level. The impedances are then calculated by using the above formulas instead of | calculation for Z T en R T , referred to the primary side (1). [ 8.44 ] Finally, the reactance is Z T,ij en R T,ij determined: [ 8.45 ]
U | U | another voltage level, but then the impedances must be referred to the side corresponding to that voltage level. The impedances are then calculated by using the above formulas instead of
nom,1 | nom,1 | voltage level, but then the impedances must be referred to the side corresponding to that voltage level. The impedances are then calculated by using the above formulas instead of U
het andere gewenste spanningsniveau te gebruiken. | to use the other desired voltage level. | level, but then the impedances must be referred to the side corresponding to that voltage level. The impedances are then calculated by using the above formulas instead of U nom,1
Figuur 8.6 Vervangingsschema van de driewikkelingstransformator | Figure 8.6 Replacement diagram of the three-winding transformer | referred to the side corresponding to that voltage level. The impedances are then calculated by using the above formulas instead of U nom,1 to use the other desired voltage level.
In het vervangingsschema van de driewikkelingstransformator is eenvoudig de relatie tussen de interne impedanties | In the replacement diagram of the three-winding transformer, the relationship between the internal impedances is straightforward. | level. The impedances are then calculated by using the above formulas instead of U nom,1 to use the other desired voltage level. Figure 8.6 Replacement diagram of the three-winding transformer
Z | Z | use the other desired voltage level. Figure 8.6 Replacement diagram of the three-winding transformer In the replacement diagram of the three-winding transformer, the relationship between the internal impedances is straightforward.
1 | 1 | the other desired voltage level. Figure 8.6 Replacement diagram of the three-winding transformer In the replacement diagram of the three-winding transformer, the relationship between the internal impedances is straightforward. Z
, | , | other desired voltage level. Figure 8.6 Replacement diagram of the three-winding transformer In the replacement diagram of the three-winding transformer, the relationship between the internal impedances is straightforward. Z 1
Z | Z | desired voltage level. Figure 8.6 Replacement diagram of the three-winding transformer In the replacement diagram of the three-winding transformer, the relationship between the internal impedances is straightforward. Z 1 ,
2 | 2 | voltage level. Figure 8.6 Replacement diagram of the three-winding transformer In the replacement diagram of the three-winding transformer, the relationship between the internal impedances is straightforward. Z 1 , Z
en | en | level. Figure 8.6 Replacement diagram of the three-winding transformer In the replacement diagram of the three-winding transformer, the relationship between the internal impedances is straightforward. Z 1 , Z 2
Z | Z | Figure 8.6 Replacement diagram of the three-winding transformer In the replacement diagram of the three-winding transformer, the relationship between the internal impedances is straightforward. Z 1 , Z 2 en
3 | 3 | 8.6 Replacement diagram of the three-winding transformer In the replacement diagram of the three-winding transformer, the relationship between the internal impedances is straightforward. Z 1 , Z 2 en Z
en de transformatorimpedanties | and the transformer impedances | Replacement diagram of the three-winding transformer In the replacement diagram of the three-winding transformer, the relationship between the internal impedances is straightforward. Z 1 , Z 2 en Z 3
Z | Z | three-winding transformer In the replacement diagram of the three-winding transformer, the relationship between the internal impedances is straightforward. Z 1 , Z 2 en Z 3 and the transformer impedances
12 | 12 | transformer In the replacement diagram of the three-winding transformer, the relationship between the internal impedances is straightforward. Z 1 , Z 2 en Z 3 and the transformer impedances Z
, | , | In the replacement diagram of the three-winding transformer, the relationship between the internal impedances is straightforward. Z 1 , Z 2 en Z 3 and the transformer impedances Z 12
Z | Z | the replacement diagram of the three-winding transformer, the relationship between the internal impedances is straightforward. Z 1 , Z 2 en Z 3 and the transformer impedances Z 12 ,
13 | 13 | replacement diagram of the three-winding transformer, the relationship between the internal impedances is straightforward. Z 1 , Z 2 en Z 3 and the transformer impedances Z 12 , Z
en | en | diagram of the three-winding transformer, the relationship between the internal impedances is straightforward. Z 1 , Z 2 en Z 3 and the transformer impedances Z 12 , Z 13
Z | Z | of the three-winding transformer, the relationship between the internal impedances is straightforward. Z 1 , Z 2 en Z 3 and the transformer impedances Z 12 , Z 13 en
23 | 23 | the three-winding transformer, the relationship between the internal impedances is straightforward. Z 1 , Z 2 en Z 3 and the transformer impedances Z 12 , Z 13 en Z
zichtbaar. De interne impedanties kunnen hieruit eenvoudig afgeleid worden van de transformatorimpedanties: | visible. The internal impedances can be easily derived from the transformer impedances: | three-winding transformer, the relationship between the internal impedances is straightforward. Z 1 , Z 2 en Z 3 and the transformer impedances Z 12 , Z 13 en Z 23
[ | [ | , Z 2 en Z 3 and the transformer impedances Z 12 , Z 13 en Z 23 visible. The internal impedances can be easily derived from the transformer impedances:
8.46 | 8.46 | Z 2 en Z 3 and the transformer impedances Z 12 , Z 13 en Z 23 visible. The internal impedances can be easily derived from the transformer impedances: [
] | ] | 2 en Z 3 and the transformer impedances Z 12 , Z 13 en Z 23 visible. The internal impedances can be easily derived from the transformer impedances: [ 8.46
Het nullastverlies wordt op dezelfde manier als bij de transformator met twee wikkelingen vastgesteld. Het nullastverlies en de nullaststroom worden op een van de wikkelingen gemeten en de impedanties kunnen op elke andere wikkeling betrokken worden door deze om te rekenen. | The no-load loss is determined in the same way as with the transformer with two windings. The no-load loss and the no-load current are measured on one of the windings, and the impedances can be related to any other winding by converting them. | en Z 3 and the transformer impedances Z 12 , Z 13 en Z 23 visible. The internal impedances can be easily derived from the transformer impedances: [ 8.46 ]
Als voorbeeld worden de impedanties berekend van een YNynd transformator voor HS, TS en MS. De naamplaatgegevens zijn hieronder vermeld. | As an example, the impedances of a YNynd transformer for HV, LV, and MV are calculated. The nameplate data are listed below. | with two windings. The no-load loss and the no-load current are measured on one of the windings, and the impedances can be related to any other winding by converting them.
Gegeven | Gegeven | related to any other winding by converting them. As an example, the impedances of a YNynd transformer for HV, LV, and MV are calculated. The nameplate data are listed below.
Primair | Primair | to any other winding by converting them. As an example, the impedances of a YNynd transformer for HV, LV, and MV are calculated. The nameplate data are listed below. Gegeven
Secundair | Secundair | any other winding by converting them. As an example, the impedances of a YNynd transformer for HV, LV, and MV are calculated. The nameplate data are listed below. Gegeven Primair
Tertiair | Tertiair | other winding by converting them. As an example, the impedances of a YNynd transformer for HV, LV, and MV are calculated. The nameplate data are listed below. Gegeven Primair Secundair
Eenheid | Eenheid | winding by converting them. As an example, the impedances of a YNynd transformer for HV, LV, and MV are calculated. The nameplate data are listed below. Gegeven Primair Secundair Tertiair
U | U | by converting them. As an example, the impedances of a YNynd transformer for HV, LV, and MV are calculated. The nameplate data are listed below. Gegeven Primair Secundair Tertiair Eenheid
nom | nom | converting them. As an example, the impedances of a YNynd transformer for HV, LV, and MV are calculated. The nameplate data are listed below. Gegeven Primair Secundair Tertiair Eenheid U
150 | 150 | them. As an example, the impedances of a YNynd transformer for HV, LV, and MV are calculated. The nameplate data are listed below. Gegeven Primair Secundair Tertiair Eenheid U nom
52,5 | 52.5 | As an example, the impedances of a YNynd transformer for HV, LV, and MV are calculated. The nameplate data are listed below. Gegeven Primair Secundair Tertiair Eenheid U nom 150
10,5 | 10.5 | an example, the impedances of a YNynd transformer for HV, LV, and MV are calculated. The nameplate data are listed below. Gegeven Primair Secundair Tertiair Eenheid U nom 150 52.5
kV | kV | example, the impedances of a YNynd transformer for HV, LV, and MV are calculated. The nameplate data are listed below. Gegeven Primair Secundair Tertiair Eenheid U nom 150 52.5 10.5
S | S | the impedances of a YNynd transformer for HV, LV, and MV are calculated. The nameplate data are listed below. Gegeven Primair Secundair Tertiair Eenheid U nom 150 52.5 10.5 kV
nom | nom | impedances of a YNynd transformer for HV, LV, and MV are calculated. The nameplate data are listed below. Gegeven Primair Secundair Tertiair Eenheid U nom 150 52.5 10.5 kV S
100 | 100 | of a YNynd transformer for HV, LV, and MV are calculated. The nameplate data are listed below. Gegeven Primair Secundair Tertiair Eenheid U nom 150 52.5 10.5 kV S nom
100 | 100 | a YNynd transformer for HV, LV, and MV are calculated. The nameplate data are listed below. Gegeven Primair Secundair Tertiair Eenheid U nom 150 52.5 10.5 kV S nom 100
27 | 27 | YNynd transformer for HV, LV, and MV are calculated. The nameplate data are listed below. Gegeven Primair Secundair Tertiair Eenheid U nom 150 52.5 10.5 kV S nom 100 100
MVA | MVA | transformer for HV, LV, and MV are calculated. The nameplate data are listed below. Gegeven Primair Secundair Tertiair Eenheid U nom 150 52.5 10.5 kV S nom 100 100 27
Primair - Secundair | Primary - Secondary | for HV, LV, and MV are calculated. The nameplate data are listed below. Gegeven Primair Secundair Tertiair Eenheid U nom 150 52.5 10.5 kV S nom 100 100 27 MVA
Primair - Tertiair | Primary - Tertiary | and MV are calculated. The nameplate data are listed below. Gegeven Primair Secundair Tertiair Eenheid U nom 150 52.5 10.5 kV S nom 100 100 27 MVA Primary - Secondary
Secundair - Tertiair | Secondary - Tertiary | calculated. The nameplate data are listed below. Gegeven Primair Secundair Tertiair Eenheid U nom 150 52.5 10.5 kV S nom 100 100 27 MVA Primary - Secondary Primary - Tertiary
u | u | data are listed below. Gegeven Primair Secundair Tertiair Eenheid U nom 150 52.5 10.5 kV S nom 100 100 27 MVA Primary - Secondary Primary - Tertiary Secondary - Tertiary
k | k | are listed below. Gegeven Primair Secundair Tertiair Eenheid U nom 150 52.5 10.5 kV S nom 100 100 27 MVA Primary - Secondary Primary - Tertiary Secondary - Tertiary u
14,8 | 14.8 | listed below. Gegeven Primair Secundair Tertiair Eenheid U nom 150 52.5 10.5 kV S nom 100 100 27 MVA Primary - Secondary Primary - Tertiary Secondary - Tertiary u k
9,3 | 9.3 | below. Gegeven Primair Secundair Tertiair Eenheid U nom 150 52.5 10.5 kV S nom 100 100 27 MVA Primary - Secondary Primary - Tertiary Secondary - Tertiary u k 14.8
4,9 | 4.9 | Gegeven Primair Secundair Tertiair Eenheid U nom 150 52.5 10.5 kV S nom 100 100 27 MVA Primary - Secondary Primary - Tertiary Secondary - Tertiary u k 14.8 9.3
% | % | Primair Secundair Tertiair Eenheid U nom 150 52.5 10.5 kV S nom 100 100 27 MVA Primary - Secondary Primary - Tertiary Secondary - Tertiary u k 14.8 9.3 4.9
P | P | Secundair Tertiair Eenheid U nom 150 52.5 10.5 kV S nom 100 100 27 MVA Primary - Secondary Primary - Tertiary Secondary - Tertiary u k 14.8 9.3 4.9 %
k | k | Tertiair Eenheid U nom 150 52.5 10.5 kV S nom 100 100 27 MVA Primary - Secondary Primary - Tertiary Secondary - Tertiary u k 14.8 9.3 4.9 % P
465 | 465 | Eenheid U nom 150 52.5 10.5 kV S nom 100 100 27 MVA Primary - Secondary Primary - Tertiary Secondary - Tertiary u k 14.8 9.3 4.9 % P k
78 | 78 | U nom 150 52.5 10.5 kV S nom 100 100 27 MVA Primary - Secondary Primary - Tertiary Secondary - Tertiary u k 14.8 9.3 4.9 % P k 465
69 | 69 | nom 150 52.5 10.5 kV S nom 100 100 27 MVA Primary - Secondary Primary - Tertiary Secondary - Tertiary u k 14.8 9.3 4.9 % P k 465 78
kW | kW | 150 52.5 10.5 kV S nom 100 100 27 MVA Primary - Secondary Primary - Tertiary Secondary - Tertiary u k 14.8 9.3 4.9 % P k 465 78 69
Alle impedanties worden in dit voorbeeld betrokken op de hoogspanningszijde, dus op de nominale spanning van 150 kV. Voor de groottes van de impedanties volgt: | All impedances in this example are referenced to the high voltage side, thus at the nominal voltage of 150 kV. For the magnitudes of the impedances, the following applies: | 52.5 10.5 kV S nom 100 100 27 MVA Primary - Secondary Primary - Tertiary Secondary - Tertiary u k 14.8 9.3 4.9 % P k 465 78 69 kW
[ | [ | kW All impedances in this example are referenced to the high voltage side, thus at the nominal voltage of 150 kV. For the magnitudes of the impedances, the following applies:
8.47 | 8.47 | All impedances in this example are referenced to the high voltage side, thus at the nominal voltage of 150 kV. For the magnitudes of the impedances, the following applies: [
] | ] | impedances in this example are referenced to the high voltage side, thus at the nominal voltage of 150 kV. For the magnitudes of the impedances, the following applies: [ 8.47
Voor de weerstanden volgt na invullen: | For the resistances, after substitution, the following applies: | in this example are referenced to the high voltage side, thus at the nominal voltage of 150 kV. For the magnitudes of the impedances, the following applies: [ 8.47 ]
[ | [ | voltage side, thus at the nominal voltage of 150 kV. For the magnitudes of the impedances, the following applies: [ 8.47 ] For the resistances, after substitution, the following applies:
8.48 | 8.48 | side, thus at the nominal voltage of 150 kV. For the magnitudes of the impedances, the following applies: [ 8.47 ] For the resistances, after substitution, the following applies: [
] | ] | thus at the nominal voltage of 150 kV. For the magnitudes of the impedances, the following applies: [ 8.47 ] For the resistances, after substitution, the following applies: [ 8.48
Hieruit volgen uiteindelijk de reactanties: | From this, the reactances ultimately follow: | at the nominal voltage of 150 kV. For the magnitudes of the impedances, the following applies: [ 8.47 ] For the resistances, after substitution, the following applies: [ 8.48 ]
[ | [ | kV. For the magnitudes of the impedances, the following applies: [ 8.47 ] For the resistances, after substitution, the following applies: [ 8.48 ] From this, the reactances ultimately follow:
8.49 | 8.49 | For the magnitudes of the impedances, the following applies: [ 8.47 ] For the resistances, after substitution, the following applies: [ 8.48 ] From this, the reactances ultimately follow: [
] | ] | the magnitudes of the impedances, the following applies: [ 8.47 ] For the resistances, after substitution, the following applies: [ 8.48 ] From this, the reactances ultimately follow: [ 8.49
De reactanties zijn in dit geval ongeveer gelijk aan de groottes van de impedanties omdat de weerstanden relatief klein zijn. De interne impedanties van het vervangingsschema kunnen nu berekend worden: | The reactances are in this case approximately equal to the magnitudes of the impedances because the resistances are relatively small. The internal impedances of the equivalent circuit can now be calculated: | magnitudes of the impedances, the following applies: [ 8.47 ] For the resistances, after substitution, the following applies: [ 8.48 ] From this, the reactances ultimately follow: [ 8.49 ]
[ | [ | reactances are in this case approximately equal to the magnitudes of the impedances because the resistances are relatively small. The internal impedances of the equivalent circuit can now be calculated:
8.50 | 8.50 | are in this case approximately equal to the magnitudes of the impedances because the resistances are relatively small. The internal impedances of the equivalent circuit can now be calculated: [
] | ] | in this case approximately equal to the magnitudes of the impedances because the resistances are relatively small. The internal impedances of the equivalent circuit can now be calculated: [ 8.50
Opvallend is dat een van de reactanties een kleine negatieve waarde heeft. Dit is de reactantie van de wikkeling die in het midden ligt van de twee andere wikkelingen (Happoldt, 1978). De reactanties van de twee andere, aan de binnen- en buitenkant geplaatste wikkelingen, zijn ongeveer gelijk aan de kortsluitreactantie tussen hun en de in het midden geplaatste wikkeling ( | Notably, one of the reactances has a small negative value. This is the reactance of the winding that is located in the middle of the two other windings (Happoldt, 1978). The reactances of the two other windings, placed on the inside and outside, are approximately equal to the short-circuit reactance between them and the winding placed in the middle. | this case approximately equal to the magnitudes of the impedances because the resistances are relatively small. The internal impedances of the equivalent circuit can now be calculated: [ 8.50 ]
X | X | 1978). The reactances of the two other windings, placed on the inside and outside, are approximately equal to the short-circuit reactance between them and the winding placed in the middle.
1 | 1 | The reactances of the two other windings, placed on the inside and outside, are approximately equal to the short-circuit reactance between them and the winding placed in the middle. X
≈ X | ≈ X | reactances of the two other windings, placed on the inside and outside, are approximately equal to the short-circuit reactance between them and the winding placed in the middle. X 1
12 | 12 | the two other windings, placed on the inside and outside, are approximately equal to the short-circuit reactance between them and the winding placed in the middle. X 1 ≈ X
en | en | two other windings, placed on the inside and outside, are approximately equal to the short-circuit reactance between them and the winding placed in the middle. X 1 ≈ X 12
X | X | other windings, placed on the inside and outside, are approximately equal to the short-circuit reactance between them and the winding placed in the middle. X 1 ≈ X 12 en
3 | 3 | windings, placed on the inside and outside, are approximately equal to the short-circuit reactance between them and the winding placed in the middle. X 1 ≈ X 12 en X
≈ X | ≈ X | placed on the inside and outside, are approximately equal to the short-circuit reactance between them and the winding placed in the middle. X 1 ≈ X 12 en X 3
23 | 23 | the inside and outside, are approximately equal to the short-circuit reactance between them and the winding placed in the middle. X 1 ≈ X 12 en X 3 ≈ X
). | ). | inside and outside, are approximately equal to the short-circuit reactance between them and the winding placed in the middle. X 1 ≈ X 12 en X 3 ≈ X 23
8.3.5 Inverse impedantie | 8.3.5 Inverse impedance | and outside, are approximately equal to the short-circuit reactance between them and the winding placed in the middle. X 1 ≈ X 12 en X 3 ≈ X 23 ).
Voor een transformator geldt hetzelfde als voor de verbinding, indien de hoekverdraaiing van de fasen buiten beschouwing wordt gelaten. Door de constructie van de transformator mag worden aangenomen dat deze voldoende driefasensymmetrisch is. De inverse impedantie | For a transformer, the same applies as for the connection, if the phase angle shift is disregarded. Due to the construction of the transformer, it can be assumed that it is sufficiently three-phase symmetrical. The inverse impedance | approximately equal to the short-circuit reactance between them and the winding placed in the middle. X 1 ≈ X 12 en X 3 ≈ X 23 ). 8.3.5 Inverse impedance
Z | Z | for the connection, if the phase angle shift is disregarded. Due to the construction of the transformer, it can be assumed that it is sufficiently three-phase symmetrical. The inverse impedance
2 | 2 | the connection, if the phase angle shift is disregarded. Due to the construction of the transformer, it can be assumed that it is sufficiently three-phase symmetrical. The inverse impedance Z
wordt dan ook gelijk gesteld aan de normale impedantie | is therefore equated to the normal impedance | connection, if the phase angle shift is disregarded. Due to the construction of the transformer, it can be assumed that it is sufficiently three-phase symmetrical. The inverse impedance Z 2
Z | Z | disregarded. Due to the construction of the transformer, it can be assumed that it is sufficiently three-phase symmetrical. The inverse impedance Z 2 is therefore equated to the normal impedance
1 | 1 | Due to the construction of the transformer, it can be assumed that it is sufficiently three-phase symmetrical. The inverse impedance Z 2 is therefore equated to the normal impedance Z
. Voor de meeste toepassingen zoals loadflow- en kortsluitberekeningen volstaat deze aanpak. Indien de fasedraaiing daarentegen wel moet worden meegenomen in de modellering, wordt deze verwerkt in de overzetverhouding. In het inverse systeem is de overzetverhouding gelijk aan de complex geconjugeerde van de overzetverhouding in het normale systeem. | For most applications, such as load flow and short-circuit calculations, this approach is sufficient. However, if the phase shift must be taken into account in the modeling, it is incorporated into the transformation ratio. In the inverse system, the transformation ratio is equal to the complex conjugate of the transformation ratio in the normal system. | to the construction of the transformer, it can be assumed that it is sufficiently three-phase symmetrical. The inverse impedance Z 2 is therefore equated to the normal impedance Z 1
8.3.6 Homopolaire parameters | 8.3.6 Homopolar parameters | the modeling, it is incorporated into the transformation ratio. In the inverse system, the transformation ratio is equal to the complex conjugate of the transformation ratio in the normal system.
Bij transformatoren kan het sterpunt belast worden als het sterpunt via een spoel of weerstand geaard is. Van transformatoren met Yd, Dy, Yz en Yyd wikkelconfiguratie is het sterpunt doorgaans volledig belastbaar en kan het de nominale stroom voeren. Bij de Yz transformator geldt deze belastbaarheid voor de zigzagwikkeling en bij de Yyd transformator voor een van de twee sterwikkelingen. Bij deze transformatoren kan een homopolaire stroom lopen en zijn dus de homopolaire gegevens van belang. | In transformers, the neutral point can be loaded if it is grounded through a coil or resistor. For transformers with Yd, Dy, Yz, and Yyd winding configurations, the neutral point is generally fully loadable and can carry the nominal current. In the Yz transformer, this loadability applies to the zigzag winding, and in the Yyd transformer, it applies to one of the two star windings. In these transformers, a homopolar current can flow, making the homopolar parameters important. | is incorporated into the transformation ratio. In the inverse system, the transformation ratio is equal to the complex conjugate of the transformation ratio in the normal system. 8.3.6 Homopolar parameters
De constructie van de transformatorkern en de transformatorbak hebben geen invloed op de normale en inverse impedanties, maar wel op de homopolaire impedanties. De homopolaire impedantie van de transformator hangt niet af van de strooiing van de magneetvelden, maar van de elektrische schakeling van de wikkelingen en de magnetische schakeling van de transformatorkern. | The construction of the transformer core and the transformer tank does not affect the normal and inverse impedances, but it does affect the homopolar impedances. The homopolar impedance of the transformer does not depend on the dispersion of the magnetic fields, but on the electrical configuration of the windings and the magnetic configuration of the transformer core. | the zigzag winding, and in the Yyd transformer, it applies to one of the two star windings. In these transformers, a homopolar current can flow, making the homopolar parameters important.
Figuur 8.7 Homopolaire spanningsbron aangesloten op een driehoekswikkeling | Figure 8.7 Homopolar voltage source connected to a delta winding | impedance of the transformer does not depend on the dispersion of the magnetic fields, but on the electrical configuration of the windings and the magnetic configuration of the transformer core.
Driehoek-ster | Delta-star | of the magnetic fields, but on the electrical configuration of the windings and the magnetic configuration of the transformer core. Figure 8.7 Homopolar voltage source connected to a delta winding
De homopolaire impedantie van een ster-driehoek transformator is van de driehoekzijde uit bekeken oneindig, omdat de driehoekschakeling geen verbinding met aarde heeft. Figuur 8.7 illustreert wat er gebeurt indien de driehoekwikkeling aangesloten wordt op een homopolaire spanningsbron. Aangezien de stroomkring niet gesloten is, loopt er in de normale situatie geen stroom. | The homopolar impedance of a star-delta transformer is infinite when viewed from the delta side, because the delta configuration has no connection to the ground. Figure 8.7 illustrates what happens when the delta winding is connected to a homopolar voltage source. Since the circuit is not closed, no current flows under normal conditions. | the magnetic fields, but on the electrical configuration of the windings and the magnetic configuration of the transformer core. Figure 8.7 Homopolar voltage source connected to a delta winding Delta-star
Figuur 8.8 Fase-aardsluiting aan de zijde van de sterwikkeling | Figure 8.8 Phase-to-ground connection on the star winding side | the ground. Figure 8.7 illustrates what happens when the delta winding is connected to a homopolar voltage source. Since the circuit is not closed, no current flows under normal conditions.
Indien de transformator vanuit de driehoekswikkeling aan de secundaire zijde gevoed wordt en indien aan de primaire zijde aan de sterwikkeling een fase-aardsluiting optreedt, zal in het primaire circuit een homopolaire kortsluitstroom | If the transformer is fed from the delta winding on the secondary side and if a phase-to-ground fault occurs on the star winding on the primary side, a homopolar short-circuit current will flow in the primary circuit. | delta winding is connected to a homopolar voltage source. Since the circuit is not closed, no current flows under normal conditions. Figure 8.8 Phase-to-ground connection on the star winding side
I | I | delta winding on the secondary side and if a phase-to-ground fault occurs on the star winding on the primary side, a homopolar short-circuit current will flow in the primary circuit.
k | k | winding on the secondary side and if a phase-to-ground fault occurs on the star winding on the primary side, a homopolar short-circuit current will flow in the primary circuit. I
" | " | on the secondary side and if a phase-to-ground fault occurs on the star winding on the primary side, a homopolar short-circuit current will flow in the primary circuit. I k
vloeien, zoals weergegeven in figuur 8.8. Deze stroom vloeit alleen door de spoel die zich in de gestoorde fase bevindt. Deze stroom wordt getransformeerd met de overzetverhouding | flow, as shown in figure 8.8. This current flows only through the coil located in the faulty phase. This current is transformed with the transformation ratio | the secondary side and if a phase-to-ground fault occurs on the star winding on the primary side, a homopolar short-circuit current will flow in the primary circuit. I k "
t | t | circuit. I k " flow, as shown in figure 8.8. This current flows only through the coil located in the faulty phase. This current is transformed with the transformation ratio
naar de magnetisch gekoppelde spoel in het secundaire circuit. Doordat de primaire spoelen in ster zijn geschakeld en de secundaire spoelen in driehoek, verschijnt de factor √3 in de transformatie van de stroom. Als gevolg hiervan zal aan de voedende zijde in het secundaire circuit in twee fasen een stroom gaan vloeien. Deze stroom in het secundaire circuit is echter geen homopolaire stroom, omdat er aan die zijde van de transformator geen contact met aarde is. | to the magnetically coupled coil in the secondary circuit. Because the primary coils are connected in a star configuration and the secondary coils in a delta configuration, the factor √3 appears in the transformation of the current. As a result, a current will flow in two phases on the supply side in the secondary circuit. However, this current in the secondary circuit is not a homopolar current, because there is no contact with the ground on that side of the transformer. | I k " flow, as shown in figure 8.8. This current flows only through the coil located in the faulty phase. This current is transformed with the transformation ratio t
Figuur 8.9 Homopolaire spanningsbron aangesloten op een sterwikkeling | Figure 8.9 Homopolar voltage source connected to a star winding | in the secondary circuit. However, this current in the secondary circuit is not a homopolar current, because there is no contact with the ground on that side of the transformer.
Voor de sterwikkeling heeft de homopolaire reactantie ongeveer de grootte van de kortsluitreactantie. De homopolaire stromen in de sterwikkeling worden door de stroom in de driehoekwikkeling in evenwicht gebracht. Figuur 8.9 illustreert dat bij het aanbrengen van een homopolaire spanningsbron op de sterwikkeling de homopolaire stroom zich verdeelt over de drie primaire fasespoelen. Deze stromen worden getransformeerd met de overzetverhouding | For the star winding, the homopolar reactance is approximately the same as the short-circuit reactance. The homopolar currents in the star winding are balanced by the current in the delta winding. Figure 8.9 illustrates that when a homopolar voltage source is applied to the star winding, the homopolar current is distributed across the three primary phase coils. These currents are transformed according to the turns ratio. | circuit is not a homopolar current, because there is no contact with the ground on that side of the transformer. Figure 8.9 Homopolar voltage source connected to a star winding
t | t | a homopolar voltage source is applied to the star winding, the homopolar current is distributed across the three primary phase coils. These currents are transformed according to the turns ratio.
en de factor √3. | and the factor √3. | homopolar voltage source is applied to the star winding, the homopolar current is distributed across the three primary phase coils. These currents are transformed according to the turns ratio. t
De getransformeerde stroom vloeit door alle spoelen van de secundaire wikkeling. Aangezien de fasoren van deze stromen in alle secundaire spoelen qua grootte en richting gelijk zijn, worden zij door de driehoekschakeling kortgesloten. Dit verklaart dat de homopolaire reactantie in deze richting ongeveer gelijk is aan de normale kortsluitreactantie. De getransformeerde stromen vloeien dus niet naar het netwerk. Indien in het secundaire circuit een fase-aardsluiting optreedt, zal deze in het primaire circuit niet merkbaar zijn. Het homopolaire vervangingsschema van deze transformatorconfiguratie is gegeven in tabel 8.9. | The transformed current flows through all the coils of the secondary winding. Since the phasors of these currents in all secondary coils are equal in magnitude and direction, they are short-circuited by the delta connection. This explains that the homopolar reactance in this direction is approximately equal to the normal short-circuit reactance. Therefore, the transformed currents do not flow into the network. If a phase-to-ground fault occurs in the secondary circuit, it will not be noticeable in the primary circuit. The homopolar equivalent circuit of this transformer configuration is given in Table 8.9. | applied to the star winding, the homopolar current is distributed across the three primary phase coils. These currents are transformed according to the turns ratio. t and the factor √3.
Zigzagwikkeling | Zigzagwikkeling | a phase-to-ground fault occurs in the secondary circuit, it will not be noticeable in the primary circuit. The homopolar equivalent circuit of this transformer configuration is given in Table 8.9.
In de homopolaire situatie is een sterwikkeling magnetisch gekoppeld met andere sterwikkelingen of met driehoekwikkelingen. Een zigzagwikkeling is echter niet gekoppeld met overige wikkelingen (zie figuur 8.10). De homopolaire reactantie van een ster-zigzag transformator of een driehoek-zigzag transformator wordt alleen door de strooiing tussen de zig- en zagwikkelingen bepaald, omdat er geen homopolaire stromen in de ster- of driehoekswikkelingen worden geïnduceerd (Figuur 8.10). | In the homopolar situation, a star winding is magnetically coupled with other star windings or with delta windings. However, a zigzag winding is not coupled with other windings (see Figure 8.10). The homopolar reactance of a star-zigzag transformer or a delta-zigzag transformer is determined solely by the leakage between the zig and zag windings, because no homopolar currents are induced in the star or delta windings (Figure 8.10). | phase-to-ground fault occurs in the secondary circuit, it will not be noticeable in the primary circuit. The homopolar equivalent circuit of this transformer configuration is given in Table 8.9. Zigzagwikkeling
Figuur 8.10 Homopolaire spanningsbron aangesloten op een zigzagwikkeling | Figure 8.10 Homopolar voltage source connected to a zigzag winding | or a delta-zigzag transformer is determined solely by the leakage between the zig and zag windings, because no homopolar currents are induced in the star or delta windings (Figure 8.10).
Aangezien de 'zig- en zagwikkelingen' tot dezelfde stroomkring behoren en zodoende verhoudingsgewijs dicht bij elkaar zijn aangebracht, is de strooiing en daarom ook de homopolaire reactantie klein. De homopolaire reactantie komt overeen met de kortsluitreactantie tussen de beide deelwikkelingen, en ligt in de ordegrootte van 0,1 tot 0,2 maal de kortsluitreactantie. | Since the 'zig and zag windings' belong to the same circuit and are therefore relatively close to each other, the leakage and consequently the homopolar reactance is small. The homopolar reactance corresponds to the short-circuit reactance between the two sub-windings and is in the order of 0.1 to 0.2 times the short-circuit reactance. | between the zig and zag windings, because no homopolar currents are induced in the star or delta windings (Figure 8.10). Figure 8.10 Homopolar voltage source connected to a zigzag winding
Een nulpunttransformator is een spoel met alleen een zigzagwikkeling. Hiermee kan in een zwevend net een impedantie-geaard sterpunt worden gecreëerd. Deze transformator wordt in middenspanningsnetten met zwevend sterpunt toegepast als de ontwerper besluit het zwevende net, bijvoorbeeld om veiligheidsredenen, te voorzien van een geaard sterpunt. Elke fase-aardsluiting in het middenspanningsnet zal nu een homopolaire stroom veroorzaken, die door de nulpunttransformator gaat vloeien en door de beveiliging kan worden opgemerkt. Meer over de nulpunttransformator in paragraaf 8.4. | A neutral grounding transformer is a coil with only a zigzag winding. This allows for the creation of an impedance-grounded neutral point in an ungrounded network. This transformer is used in medium voltage networks with an ungrounded neutral when the designer decides to provide the ungrounded network with a grounded neutral point, for example, for safety reasons. Any phase-to-ground fault in the medium voltage network will now cause a homopolar current, which will flow through the neutral grounding transformer and can be detected by the protection system. More about the neutral grounding transformer can be found in section 8.4. | the homopolar reactance is small. The homopolar reactance corresponds to the short-circuit reactance between the two sub-windings and is in the order of 0.1 to 0.2 times the short-circuit reactance.
Ster-ster transformator | Star-star transformer | homopolar current, which will flow through the neutral grounding transformer and can be detected by the protection system. More about the neutral grounding transformer can be found in section 8.4.
Een YNy wikkelconfiguratie wordt in het algemeen niet aangeraden voor driefasentransformatoren omdat zij een vrij grote homopolaire impedantie hebben. Bij deze transformatoren is, in tegenstelling tot de driehoek-ster transformator en de transformator met zigzagwikkeling geen evenwicht in Amperewindingen mogelijk. De waarde van de homopolaire impedantie wordt grotendeels bepaald door de constructie van de transformatorkern, die van invloed is op de reluctantie (magnetische weerstand) en de magnetiseringsreactantie. De magnetiseringsreactantie is omgekeerd evenredig met de reluctantie. De reluctantie van het pad voor de magnetische flux buiten de ijzerkern is vele malen hoger dan van het pad door de ijzerkern. Daarom is in het algemeen de magnetiseringsreactantie groot indien het pad van de magnetische flux zich geheel in de ijzerkern bevindt. Indien de flux wordt gedwongen zich buiten de ijzerkern te begeven, is de magnetiseringsreactantie klein. De homopolaire reactantie, tenslotte, wordt bepaald uit de som van de lekreactantie en de magnetiseringsreactantie. | A YNy winding configuration is generally not recommended for three-phase transformers because they have a relatively high zero-sequence impedance. In these transformers, unlike the delta-star transformer and the transformer with zigzag winding, balance in Ampere-turns is not possible. The value of the zero-sequence impedance is largely determined by the construction of the transformer core, which affects the reluctance (magnetic resistance) and the magnetizing reactance. The magnetizing reactance is inversely proportional to the reluctance. The reluctance of the path for the magnetic flux outside the iron core is many times higher than that of the path through the iron core. Therefore, in general, the magnetizing reactance is high when the path of the magnetic flux is entirely within the iron core. If the flux is forced to travel outside the iron core, the magnetizing reactance is low. Finally, the zero-sequence reactance is determined by the sum of the leakage reactance and the magnetizing reactance. | which will flow through the neutral grounding transformer and can be detected by the protection system. More about the neutral grounding transformer can be found in section 8.4. Star-star transformer
De meeste driefasentransformatoren zijn samengesteld met drie afzonderlijke éénfasetransformatoren of zijn opgebouwd rond een kern met vijf of drie 'benen'. | Most three-phase transformers are composed of three separate single-phase transformers or are built around a core with five or three 'legs'. | is forced to travel outside the iron core, the magnetizing reactance is low. Finally, the zero-sequence reactance is determined by the sum of the leakage reactance and the magnetizing reactance.
Drie afzonderlijke éénfasetransformatoren | Three separate single-phase transformers | sum of the leakage reactance and the magnetizing reactance. Most three-phase transformers are composed of three separate single-phase transformers or are built around a core with five or three 'legs'.
Figuur 8.11 toont de configuratie met drie afzonderlijke transformatoren. In elke afzonderlijke kern kan de homopolaire magnetische flux volledig vloeien, waardoor de reluctantie zeer klein is. De magnetiseringsreactantie is omgekeerd evenredig met de reluctantie en is zeer groot. Als gevolg is de homopolaire impedantie, die wordt bepaald uit de som van de lekreactantie en de magnetiseringsreactantie, ook groot (Tleis, 2008). De verhouding X0/X1 van de homopolaire en de normale transformatorreactantie ligt in de ordegrootte van 10 tot 100 (Happoldt, 1978). | Figure 8.11 shows the configuration with three separate transformers. In each separate core, the homopolar magnetic flux can flow completely, resulting in very low reluctance. The magnetizing reactance is inversely proportional to the reluctance and is very high. Consequently, the homopolar impedance, which is determined from the sum of the leakage reactance and the magnetizing reactance, is also high (Tleis, 2008). The ratio X0/X1 of the homopolar to the normal transformer reactance is in the order of magnitude of 10 to 100 (Happoldt, 1978). | reactance and the magnetizing reactance. Most three-phase transformers are composed of three separate single-phase transformers or are built around a core with five or three 'legs'. Three separate single-phase transformers
Figuur 8.11 Homopolaire fluxen in drie afzonderlijke transformatoren | Figure 8.11 Homopolar fluxes in three separate transformers | magnetizing reactance, is also high (Tleis, 2008). The ratio X0/X1 of the homopolar to the normal transformer reactance is in the order of magnitude of 10 to 100 (Happoldt, 1978).
Ster-ster transformator met vijfbenige ijzerkern | Star-star transformer with five-legged iron core | ratio X0/X1 of the homopolar to the normal transformer reactance is in the order of magnitude of 10 to 100 (Happoldt, 1978). Figure 8.11 Homopolar fluxes in three separate transformers
Figuur 8.12 toont de driefasentransformator met een vijfbenige ijzerkern. Bij deze transformator kunnen de homopolaire magnetische fluxen zich volledig sluiten over het pad via de buitenste twee benen, zodat de reluctantie zeer klein is. Als gevolg kan de homopolaire reactantie dan zeer hoge waarden aannemen. Het gevaar bestaat echter dat bij een fase-aardkortsluiting de buitenste twee benen van de ijzerkern in verzadiging raken, hetgeen de waarde van de homopolaire impedantie reduceert (Tleis, 2008). De verhouding van X0/X1 ligt in de ordegrootte van 10 tot 100 (Happoldt, 1978). | Figure 8.12 shows the three-phase transformer with a five-legged iron core. In this transformer, the homopolar magnetic fluxes can completely close over the path via the outer two legs, resulting in very low reluctance. Consequently, the homopolar reactance can reach very high values. However, there is a risk that in the event of a phase-to-ground short circuit, the outer two legs of the iron core may become saturated, which reduces the value of the homopolar impedance (Tleis, 2008). The ratio of X0/X1 is in the order of magnitude of 10 to 100 (Happoldt, 1978). | the normal transformer reactance is in the order of magnitude of 10 to 100 (Happoldt, 1978). Figure 8.11 Homopolar fluxes in three separate transformers Star-star transformer with five-legged iron core
Figuur 8.12 Homopolaire fluxen in een transformator met vijfbenige ijzerkern | Figure 8.12 Homopolar fluxes in a transformer with a five-legged iron core | core may become saturated, which reduces the value of the homopolar impedance (Tleis, 2008). The ratio of X0/X1 is in the order of magnitude of 10 to 100 (Happoldt, 1978).
Ster-ster transformator met driebenige ijzerkern | Star-star transformer with three-legged iron core | (Tleis, 2008). The ratio of X0/X1 is in the order of magnitude of 10 to 100 (Happoldt, 1978). Figure 8.12 Homopolar fluxes in a transformer with a five-legged iron core
Figuur 8.13 toont de spoelen en de kern van een driefasentransformator met driebenige ijzerkern. Bij een driefasensymmetrische stroom door de spoelen vertonen ook de magnetische fluxen in de kern diezelfde driefasensymmetrie, met als gevolg dat de drie magnetische fluxen elkaar in de ijzerkern opheffen. Echter, de homopolaire stromen magnetiseren de drie benen van de transformatorkern in gelijke richting. In dat geval is de som van de magnetische fluxen in de drie benen niet gelijk aan nul. De magnetische fluxen moeten dan buiten de ijzerkern een retourpad vinden. Als gevolg daarvan zal bij zulke transformatoren de som van de magnetische fluxen zich door de lucht en over de transformatorbak sluiten. De transformatorbak heeft daardoor als het ware dezelfde invloed als een extra driehoekswikkeling. | Figure 8.13 shows the coils and the core of a three-phase transformer with a three-legged iron core. With a three-phase symmetrical current through the coils, the magnetic fluxes in the core also exhibit the same three-phase symmetry, resulting in the three magnetic fluxes canceling each other out in the iron core. However, the homopolar currents magnetize the three legs of the transformer core in the same direction. In that case, the sum of the magnetic fluxes in the three legs is not equal to zero. The magnetic fluxes then need to find a return path outside the iron core. As a result, in such transformers, the sum of the magnetic fluxes will close through the air and over the transformer tank. The transformer tank thus has the same effect as an additional delta winding. | is in the order of magnitude of 10 to 100 (Happoldt, 1978). Figure 8.12 Homopolar fluxes in a transformer with a five-legged iron core Star-star transformer with three-legged iron core
Figuur 8.13 Homopolaire fluxen in een transformator met driebenige ijzerkern | Figure 8.13 Homopolar fluxes in a transformer with a three-legged iron core | transformers, the sum of the magnetic fluxes will close through the air and over the transformer tank. The transformer tank thus has the same effect as an additional delta winding.
De reluctantie van het fluxpad buiten de ijzerkern is groot, waardoor de magnetiseringsreactantie klein is. De resulterende homopolaire reactantie is kleiner dan bij de transformator met vijfbenige kern maar is groter dan de normale kortsluitreactantie. De verhouding van X0/X1 ligt in de ordegrootte van 3 tot 10 (Happoldt, 1978). | The reluctance of the flux path outside the iron core is high, resulting in a low magnetizing reactance. The resulting homopolar reactance is smaller than that of the transformer with a five-legged core but greater than the normal short-circuit reactance. The ratio of X0/X1 is in the order of magnitude of 3 to 10 (Happoldt, 1978). | and over the transformer tank. The transformer tank thus has the same effect as an additional delta winding. Figure 8.13 Homopolar fluxes in a transformer with a three-legged iron core
In situaties van asymmetrie in het driefasenstelsel kan de homopolaire stroom vrij groot worden. Doordat de magnetische fluxen zich sluiten in de transformatorbak, kan deze hierdoor opgewarmd worden tot een onacceptabel hoge temperatuur. | In situations of asymmetry in the three-phase system, the homopolar current can become quite large. Because the magnetic fluxes close within the transformer tank, it can heat up to an unacceptably high temperature. | of the transformer with a five-legged core but greater than the normal short-circuit reactance. The ratio of X0/X1 is in the order of magnitude of 3 to 10 (Happoldt, 1978).
Ter verbetering van het gedrag in situaties dat een homopolaire stroom vloeit, worden transformatoren met ster-ster windingsconfiguratie meestal uitgerust met een derde driehoekswikkeling, waar de homopolaire stromen op gecontroleerde manier kunnen vloeien. De verhouding van X0/X1 van dit soort transformatoren ligt in de ordegrootte van 1 tot 2,4 (Happoldt, 1978). | To improve performance in situations where a homopolar current flows, transformers with a star-star winding configuration are usually equipped with a third delta winding, where the homopolar currents can flow in a controlled manner. The ratio of X0/X1 for this type of transformer ranges from approximately 1 to 2.4 (Happoldt, 1978). | asymmetry in the three-phase system, the homopolar current can become quite large. Because the magnetic fluxes close within the transformer tank, it can heat up to an unacceptably high temperature.
Tabel 8.8 geeft een overzicht van de homopolaire reactantie | Table 8.8 provides an overview of the homopolar reactance | third delta winding, where the homopolar currents can flow in a controlled manner. The ratio of X0/X1 for this type of transformer ranges from approximately 1 to 2.4 (Happoldt, 1978).
X | X | in a controlled manner. The ratio of X0/X1 for this type of transformer ranges from approximately 1 to 2.4 (Happoldt, 1978). Table 8.8 provides an overview of the homopolar reactance
0 | 0 | a controlled manner. The ratio of X0/X1 for this type of transformer ranges from approximately 1 to 2.4 (Happoldt, 1978). Table 8.8 provides an overview of the homopolar reactance X
van enkele transformatoren, uitgedrukt als factor van de normale kortsluitreactantie | of several transformers, expressed as a factor of the normal short-circuit reactance | controlled manner. The ratio of X0/X1 for this type of transformer ranges from approximately 1 to 2.4 (Happoldt, 1978). Table 8.8 provides an overview of the homopolar reactance X 0
X | X | from approximately 1 to 2.4 (Happoldt, 1978). Table 8.8 provides an overview of the homopolar reactance X 0 of several transformers, expressed as a factor of the normal short-circuit reactance
1 | 1 | approximately 1 to 2.4 (Happoldt, 1978). Table 8.8 provides an overview of the homopolar reactance X 0 of several transformers, expressed as a factor of the normal short-circuit reactance X
. De factoren gelden voor die zijde van de transformatoren waarvan het sterpunt geaard is, aangeduid met de letter | . The factors apply to the side of the transformers whose neutral point is grounded, indicated by the letter | 1 to 2.4 (Happoldt, 1978). Table 8.8 provides an overview of the homopolar reactance X 0 of several transformers, expressed as a factor of the normal short-circuit reactance X 1
N | N | expressed as a factor of the normal short-circuit reactance X 1 . The factors apply to the side of the transformers whose neutral point is grounded, indicated by the letter
of | of | as a factor of the normal short-circuit reactance X 1 . The factors apply to the side of the transformers whose neutral point is grounded, indicated by the letter N
n | n | a factor of the normal short-circuit reactance X 1 . The factors apply to the side of the transformers whose neutral point is grounded, indicated by the letter N of
. | . | factor of the normal short-circuit reactance X 1 . The factors apply to the side of the transformers whose neutral point is grounded, indicated by the letter N of n
Tabel 8.8 Homopolaire reactanties transformatoren | Table 8.8 Zero-sequence reactances of transformers | of the normal short-circuit reactance X 1 . The factors apply to the side of the transformers whose neutral point is grounded, indicated by the letter N of n .
Transformatorkern | Transformatorkern | 1 . The factors apply to the side of the transformers whose neutral point is grounded, indicated by the letter N of n . Table 8.8 Zero-sequence reactances of transformers
Verhouding X0/X1 voor schakeling | Ratio X0/X1 for connection | . The factors apply to the side of the transformers whose neutral point is grounded, indicated by the letter N of n . Table 8.8 Zero-sequence reactances of transformers Transformatorkern
Yzn | Yzn | to the side of the transformers whose neutral point is grounded, indicated by the letter N of n . Table 8.8 Zero-sequence reactances of transformers Transformatorkern Ratio X0/X1 for connection
YNd of Dyn | YNd or Dyn | the side of the transformers whose neutral point is grounded, indicated by the letter N of n . Table 8.8 Zero-sequence reactances of transformers Transformatorkern Ratio X0/X1 for connection Yzn
YNy + D | YNy + D | the transformers whose neutral point is grounded, indicated by the letter N of n . Table 8.8 Zero-sequence reactances of transformers Transformatorkern Ratio X0/X1 for connection Yzn YNd or Dyn
YNy of YNz | YNy or YNz | neutral point is grounded, indicated by the letter N of n . Table 8.8 Zero-sequence reactances of transformers Transformatorkern Ratio X0/X1 for connection Yzn YNd or Dyn YNy + D
Drie kernen | Three cores | grounded, indicated by the letter N of n . Table 8.8 Zero-sequence reactances of transformers Transformatorkern Ratio X0/X1 for connection Yzn YNd or Dyn YNy + D YNy or YNz
0,10 --- 0,15 | 0.10 --- 0.15 | by the letter N of n . Table 8.8 Zero-sequence reactances of transformers Transformatorkern Ratio X0/X1 for connection Yzn YNd or Dyn YNy + D YNy or YNz Three cores
0,7 … 1,0 | 0.7 … 1.0 | N of n . Table 8.8 Zero-sequence reactances of transformers Transformatorkern Ratio X0/X1 for connection Yzn YNd or Dyn YNy + D YNy or YNz Three cores 0.10 --- 0.15
a) | a) | . Table 8.8 Zero-sequence reactances of transformers Transformatorkern Ratio X0/X1 for connection Yzn YNd or Dyn YNy + D YNy or YNz Three cores 0.10 --- 0.15 0.7 … 1.0
1 … 2,4 | 1 … 2.4 | Table 8.8 Zero-sequence reactances of transformers Transformatorkern Ratio X0/X1 for connection Yzn YNd or Dyn YNy + D YNy or YNz Three cores 0.10 --- 0.15 0.7 … 1.0 a)
b) | b) | reactances of transformers Transformatorkern Ratio X0/X1 for connection Yzn YNd or Dyn YNy + D YNy or YNz Three cores 0.10 --- 0.15 0.7 … 1.0 a) 1 … 2.4
3 .. 10 | 3 .. 10 | of transformers Transformatorkern Ratio X0/X1 for connection Yzn YNd or Dyn YNy + D YNy or YNz Three cores 0.10 --- 0.15 0.7 … 1.0 a) 1 … 2.4 b)
b) | b) | Ratio X0/X1 for connection Yzn YNd or Dyn YNy + D YNy or YNz Three cores 0.10 --- 0.15 0.7 … 1.0 a) 1 … 2.4 b) 3 .. 10
Vijf kernen | Five cores | X0/X1 for connection Yzn YNd or Dyn YNy + D YNy or YNz Three cores 0.10 --- 0.15 0.7 … 1.0 a) 1 … 2.4 b) 3 .. 10 b)
0,10 --- 0,15 | 0.10 --- 0.15 | connection Yzn YNd or Dyn YNy + D YNy or YNz Three cores 0.10 --- 0.15 0.7 … 1.0 a) 1 … 2.4 b) 3 .. 10 b) Five cores
1,0 | 1.0 | or Dyn YNy + D YNy or YNz Three cores 0.10 --- 0.15 0.7 … 1.0 a) 1 … 2.4 b) 3 .. 10 b) Five cores 0.10 --- 0.15
1 … 2,4 | 1 … 2.4 | Dyn YNy + D YNy or YNz Three cores 0.10 --- 0.15 0.7 … 1.0 a) 1 … 2.4 b) 3 .. 10 b) Five cores 0.10 --- 0.15 1.0
b) | b) | D YNy or YNz Three cores 0.10 --- 0.15 0.7 … 1.0 a) 1 … 2.4 b) 3 .. 10 b) Five cores 0.10 --- 0.15 1.0 1 … 2.4
10 .. 100 | 10 .. 100 | YNy or YNz Three cores 0.10 --- 0.15 0.7 … 1.0 a) 1 … 2.4 b) 3 .. 10 b) Five cores 0.10 --- 0.15 1.0 1 … 2.4 b)
b) | b) | Three cores 0.10 --- 0.15 0.7 … 1.0 a) 1 … 2.4 b) 3 .. 10 b) Five cores 0.10 --- 0.15 1.0 1 … 2.4 b) 10 .. 100
Drie separate éénfasetransformatoren | Three separate single-phase transformers | cores 0.10 --- 0.15 0.7 … 1.0 a) 1 … 2.4 b) 3 .. 10 b) Five cores 0.10 --- 0.15 1.0 1 … 2.4 b) 10 .. 100 b)
0,10 --- 0,15 | 0.10 --- 0.15 | 0.7 … 1.0 a) 1 … 2.4 b) 3 .. 10 b) Five cores 0.10 --- 0.15 1.0 1 … 2.4 b) 10 .. 100 b) Three separate single-phase transformers
1,0 | 1.0 | a) 1 … 2.4 b) 3 .. 10 b) Five cores 0.10 --- 0.15 1.0 1 … 2.4 b) 10 .. 100 b) Three separate single-phase transformers 0.10 --- 0.15
1 … 2,4 | 1 … 2.4 | 1 … 2.4 b) 3 .. 10 b) Five cores 0.10 --- 0.15 1.0 1 … 2.4 b) 10 .. 100 b) Three separate single-phase transformers 0.10 --- 0.15 1.0
b) | b) | b) 3 .. 10 b) Five cores 0.10 --- 0.15 1.0 1 … 2.4 b) 10 .. 100 b) Three separate single-phase transformers 0.10 --- 0.15 1.0 1 … 2.4
10 .. 100 | 10 .. 100 | 3 .. 10 b) Five cores 0.10 --- 0.15 1.0 1 … 2.4 b) 10 .. 100 b) Three separate single-phase transformers 0.10 --- 0.15 1.0 1 … 2.4 b)
b) | b) | b) Five cores 0.10 --- 0.15 1.0 1 … 2.4 b) 10 .. 100 b) Three separate single-phase transformers 0.10 --- 0.15 1.0 1 … 2.4 b) 10 .. 100
Bij transformatoren van klein vermogen (MS/LS-distributietransformatoren) is de verhouding | For low-power transformers (MV/LV distribution transformers), the ratio | Five cores 0.10 --- 0.15 1.0 1 … 2.4 b) 10 .. 100 b) Three separate single-phase transformers 0.10 --- 0.15 1.0 1 … 2.4 b) 10 .. 100 b)
X | X | 2.4 b) 10 .. 100 b) Three separate single-phase transformers 0.10 --- 0.15 1.0 1 … 2.4 b) 10 .. 100 b) For low-power transformers (MV/LV distribution transformers), the ratio
0 | 0 | b) 10 .. 100 b) Three separate single-phase transformers 0.10 --- 0.15 1.0 1 … 2.4 b) 10 .. 100 b) For low-power transformers (MV/LV distribution transformers), the ratio X
/X | /X | 10 .. 100 b) Three separate single-phase transformers 0.10 --- 0.15 1.0 1 … 2.4 b) 10 .. 100 b) For low-power transformers (MV/LV distribution transformers), the ratio X 0
1 | 1 | .. 100 b) Three separate single-phase transformers 0.10 --- 0.15 1.0 1 … 2.4 b) 10 .. 100 b) For low-power transformers (MV/LV distribution transformers), the ratio X 0 /X
ongeveer gelijk aan 1,0. | approximately equal to 1.0. | 100 b) Three separate single-phase transformers 0.10 --- 0.15 1.0 1 … 2.4 b) 10 .. 100 b) For low-power transformers (MV/LV distribution transformers), the ratio X 0 /X 1
Sterk afhankelijk van de bouw van de transformator en van het aandeel van de strooiflux in verhouding tot de werkflux (de strooiflux sluit zich gedeeltelijk via de transformatorbehuizing). | Highly dependent on the construction of the transformer and the proportion of the leakage flux relative to the working flux (the leakage flux partially closes through the transformer housing). | single-phase transformers 0.10 --- 0.15 1.0 1 … 2.4 b) 10 .. 100 b) For low-power transformers (MV/LV distribution transformers), the ratio X 0 /X 1 approximately equal to 1.0.
Met behulp van de tabel 8.8 kunnen de homopolaire impedanties van de transformator geschat worden. Hierbij moet eerst het juiste homopolaire vervangingsschema voor de wikkelconfiguratie uit tabel 8.9 gekozen worden. In tabel 8.9 zijn de homopolaire transformatorimpedanties en de externe sterpuntsimpedantie | Using table 8.8, the homopolar impedances of the transformer can be estimated. First, the correct homopolar equivalent circuit for the winding configuration must be selected from table 8.9. Table 8.9 contains the homopolar transformer impedances and the external neutral point impedance. | 1.0. Highly dependent on the construction of the transformer and the proportion of the leakage flux relative to the working flux (the leakage flux partially closes through the transformer housing).
Z | Z | estimated. First, the correct homopolar equivalent circuit for the winding configuration must be selected from table 8.9. Table 8.9 contains the homopolar transformer impedances and the external neutral point impedance.
e | e | First, the correct homopolar equivalent circuit for the winding configuration must be selected from table 8.9. Table 8.9 contains the homopolar transformer impedances and the external neutral point impedance. Z
weergegeven. | displayed. | the correct homopolar equivalent circuit for the winding configuration must be selected from table 8.9. Table 8.9 contains the homopolar transformer impedances and the external neutral point impedance. Z e
Van bijvoorbeeld de YNynd transformator in het voorbeeld van paragraaf 8.3.4 ligt volgens tabel 8.8 de verhouding van | For example, for the YNynd transformer in the example of paragraph 8.3.4, according to table 8.8, the ratio of | correct homopolar equivalent circuit for the winding configuration must be selected from table 8.9. Table 8.9 contains the homopolar transformer impedances and the external neutral point impedance. Z e displayed.
X | X | transformer impedances and the external neutral point impedance. Z e displayed. For example, for the YNynd transformer in the example of paragraph 8.3.4, according to table 8.8, the ratio of
0 | 0 | impedances and the external neutral point impedance. Z e displayed. For example, for the YNynd transformer in the example of paragraph 8.3.4, according to table 8.8, the ratio of X
/X | /X | and the external neutral point impedance. Z e displayed. For example, for the YNynd transformer in the example of paragraph 8.3.4, according to table 8.8, the ratio of X 0
1 | 1 | the external neutral point impedance. Z e displayed. For example, for the YNynd transformer in the example of paragraph 8.3.4, according to table 8.8, the ratio of X 0 /X
tussen 1,0 en 2,4. In dit verklarende voorbeeld wordt aangenomen de verhouding 1,0 is en dat de methode ook van toepassing is op de weerstand. Voor de interne homopolaire impedanties van het vervangingsschema van tabel 8.9 betekent dit, wanneer gebruik wordt gemaakt van de berekende waarden van de interne impedanties van het normale componentsysteem volgens vergelijking 8.50: | between 1.0 and 2.4. In this explanatory example, it is assumed that the ratio is 1.0 and that the method also applies to the resistance. For the internal homopolar impedances of the equivalent circuit in table 8.9, this means that when using the calculated values of the internal impedances of the normal component system according to equation 8.50: | external neutral point impedance. Z e displayed. For example, for the YNynd transformer in the example of paragraph 8.3.4, according to table 8.8, the ratio of X 0 /X 1
Z | Z | homopolar impedances of the equivalent circuit in table 8.9, this means that when using the calculated values of the internal impedances of the normal component system according to equation 8.50:
0,1 | 0.1 | impedances of the equivalent circuit in table 8.9, this means that when using the calculated values of the internal impedances of the normal component system according to equation 8.50: Z
of the equivalent circuit in table 8.9, this means that when using the calculated values of the internal impedances of the normal component system according to equation 8.50: Z 0.1
1 | 1 | equivalent circuit in table 8.9, this means that when using the calculated values of the internal impedances of the normal component system according to equation 8.50: Z 0.1 = Z
circuit in table 8.9, this means that when using the calculated values of the internal impedances of the normal component system according to equation 8.50: Z 0.1 = Z 1
Z | Z | means that when using the calculated values of the internal impedances of the normal component system according to equation 8.50: Z 0.1 = Z 1 = 0.7 + j35.0 Ω
0,2 | 0.2 | that when using the calculated values of the internal impedances of the normal component system according to equation 8.50: Z 0.1 = Z 1 = 0.7 + j35.0 Ω Z
when using the calculated values of the internal impedances of the normal component system according to equation 8.50: Z 0.1 = Z 1 = 0.7 + j35.0 Ω Z 0.2
2 | 2 | the calculated values of the internal impedances of the normal component system according to equation 8.50: Z 0.1 = Z 1 = 0.7 + j35.0 Ω Z 0.2 = Z
calculated values of the internal impedances of the normal component system according to equation 8.50: Z 0.1 = Z 1 = 0.7 + j35.0 Ω Z 0.2 = Z 2
Z | Z | impedances of the normal component system according to equation 8.50: Z 0.1 = Z 1 = 0.7 + j35.0 Ω Z 0.2 = Z 2 = 0.4 – j1.7 Ω
0,3 | 0.3 | of the normal component system according to equation 8.50: Z 0.1 = Z 1 = 0.7 + j35.0 Ω Z 0.2 = Z 2 = 0.4 – j1.7 Ω Z
the normal component system according to equation 8.50: Z 0.1 = Z 1 = 0.7 + j35.0 Ω Z 0.2 = Z 2 = 0.4 – j1.7 Ω Z 0.3
3 | 3 | component system according to equation 8.50: Z 0.1 = Z 1 = 0.7 + j35.0 Ω Z 0.2 = Z 2 = 0.4 – j1.7 Ω Z 0.3 = Z
system according to equation 8.50: Z 0.1 = Z 1 = 0.7 + j35.0 Ω Z 0.2 = Z 2 = 0.4 – j1.7 Ω Z 0.3 = Z 3
Voor een YNynd driewikkelingstransformator worden eerst de normale transformatorimpedanties berekend uit de naamplaatgegevens en vervolgens de interne impedanties | For a YNynd three-winding transformer, the normal transformer impedances are first calculated from the nameplate data and then the internal impedances. | Z 0.1 = Z 1 = 0.7 + j35.0 Ω Z 0.2 = Z 2 = 0.4 – j1.7 Ω Z 0.3 = Z 3 = 1.7 + j42.5 Ω
Z | Z | 0.3 = Z 3 = 1.7 + j42.5 Ω For a YNynd three-winding transformer, the normal transformer impedances are first calculated from the nameplate data and then the internal impedances.
1 | 1
, | , | Z 3 = 1.7 + j42.5 Ω For a YNynd three-winding transformer, the normal transformer impedances are first calculated from the nameplate data and then the internal impedances. Z 1
Z | Z | 3 = 1.7 + j42.5 Ω For a YNynd three-winding transformer, the normal transformer impedances are first calculated from the nameplate data and then the internal impedances. Z 1 ,
2 | 2
en | en | 1.7 + j42.5 Ω For a YNynd three-winding transformer, the normal transformer impedances are first calculated from the nameplate data and then the internal impedances. Z 1 , Z 2
Z | Z | + j42.5 Ω For a YNynd three-winding transformer, the normal transformer impedances are first calculated from the nameplate data and then the internal impedances. Z 1 , Z 2 en
3 | 3 | j42.5 Ω For a YNynd three-winding transformer, the normal transformer impedances are first calculated from the nameplate data and then the internal impedances. Z 1 , Z 2 en Z
van het vervangingsschema van figuur 8.6. De verhouding van | the equivalent circuit of figure 8.6. The ratio of | Ω For a YNynd three-winding transformer, the normal transformer impedances are first calculated from the nameplate data and then the internal impedances. Z 1 , Z 2 en Z 3
X | X | impedances are first calculated from the nameplate data and then the internal impedances. Z 1 , Z 2 en Z 3 the equivalent circuit of figure 8.6. The ratio of
0 | 0 | are first calculated from the nameplate data and then the internal impedances. Z 1 , Z 2 en Z 3 the equivalent circuit of figure 8.6. The ratio of X
/X | /X | first calculated from the nameplate data and then the internal impedances. Z 1 , Z 2 en Z 3 the equivalent circuit of figure 8.6. The ratio of X 0
1 | 1 | calculated from the nameplate data and then the internal impedances. Z 1 , Z 2 en Z 3 the equivalent circuit of figure 8.6. The ratio of X 0 /X
ligt voor dit soort transformatoren tussen 1,0 en 2,4. Ook bij deze transformator wordt aangenomen dat deze verhouding mag worden toegepast op de weerstand. Met het verhoudingsgetal kunnen nu de impedanties | for this type of transformer lies between 1.0 and 2.4. It is also assumed for this transformer that this ratio can be applied to the resistance. With the ratio, the impedances can now | from the nameplate data and then the internal impedances. Z 1 , Z 2 en Z 3 the equivalent circuit of figure 8.6. The ratio of X 0 /X 1
Z | Z | of transformer lies between 1.0 and 2.4. It is also assumed for this transformer that this ratio can be applied to the resistance. With the ratio, the impedances can now
0,1 | 0.1 | transformer lies between 1.0 and 2.4. It is also assumed for this transformer that this ratio can be applied to the resistance. With the ratio, the impedances can now Z
, | , | lies between 1.0 and 2.4. It is also assumed for this transformer that this ratio can be applied to the resistance. With the ratio, the impedances can now Z 0.1
Z | Z | between 1.0 and 2.4. It is also assumed for this transformer that this ratio can be applied to the resistance. With the ratio, the impedances can now Z 0.1 ,
0,2 | 0.2 | 1.0 and 2.4. It is also assumed for this transformer that this ratio can be applied to the resistance. With the ratio, the impedances can now Z 0.1 , Z
en | en | and 2.4. It is also assumed for this transformer that this ratio can be applied to the resistance. With the ratio, the impedances can now Z 0.1 , Z 0.2
Z | Z | 2.4. It is also assumed for this transformer that this ratio can be applied to the resistance. With the ratio, the impedances can now Z 0.1 , Z 0.2 en
0,3 | 0.3 | It is also assumed for this transformer that this ratio can be applied to the resistance. With the ratio, the impedances can now Z 0.1 , Z 0.2 en Z
berekend worden. In het vervangingsschema is er voor alle schakelingen van tabel 8.9 van uitgegaan dat alle impedanties betrokken worden op het spanningsniveau van de primaire zijde. Daarom kan voor de YNynd transformatorconfiguratie de aardings-impedantie aan de primaire wikkeling | be calculated. In the equivalent circuit, it is assumed for all circuits in table 8.9 that all impedances are referred to the voltage level of the primary side. Therefore, for the YNynd transformer configuration, the grounding impedance can be referred to the primary winding. | is also assumed for this transformer that this ratio can be applied to the resistance. With the ratio, the impedances can now Z 0.1 , Z 0.2 en Z 0.3
Z | Z | 8.9 that all impedances are referred to the voltage level of the primary side. Therefore, for the YNynd transformer configuration, the grounding impedance can be referred to the primary winding.
e1 | e1 | that all impedances are referred to the voltage level of the primary side. Therefore, for the YNynd transformer configuration, the grounding impedance can be referred to the primary winding. Z
gewoon in het vervangingsschema ingevuld worden. De aardingsimpedantie aan de secundaire zijde moet echter eerst omgezet worden naar het spanningsniveau van de primaire zijde door de waarde te vermenigvuldigen met | simply be filled in the equivalent circuit. However, the grounding impedance on the secondary side must first be converted to the voltage level of the primary side by multiplying the value by | all impedances are referred to the voltage level of the primary side. Therefore, for the YNynd transformer configuration, the grounding impedance can be referred to the primary winding. Z e1
(U | (U | filled in the equivalent circuit. However, the grounding impedance on the secondary side must first be converted to the voltage level of the primary side by multiplying the value by
1 | 1 | in the equivalent circuit. However, the grounding impedance on the secondary side must first be converted to the voltage level of the primary side by multiplying the value by (U
/U | /U | the equivalent circuit. However, the grounding impedance on the secondary side must first be converted to the voltage level of the primary side by multiplying the value by (U 1
2 | 2 | equivalent circuit. However, the grounding impedance on the secondary side must first be converted to the voltage level of the primary side by multiplying the value by (U 1 /U
) | ) | circuit. However, the grounding impedance on the secondary side must first be converted to the voltage level of the primary side by multiplying the value by (U 1 /U 2
2 | 2 | However, the grounding impedance on the secondary side must first be converted to the voltage level of the primary side by multiplying the value by (U 1 /U 2 )
. Indien de secundaire wikkeling niet geaard is, wordt voor | . If the secondary winding is not grounded, then for | the grounding impedance on the secondary side must first be converted to the voltage level of the primary side by multiplying the value by (U 1 /U 2 ) 2
Z | Z | converted to the voltage level of the primary side by multiplying the value by (U 1 /U 2 ) 2 . If the secondary winding is not grounded, then for
e2 | e2 | to the voltage level of the primary side by multiplying the value by (U 1 /U 2 ) 2 . If the secondary winding is not grounded, then for Z
oneindig ingevuld. | infinity is substituted. | the voltage level of the primary side by multiplying the value by (U 1 /U 2 ) 2 . If the secondary winding is not grounded, then for Z e2
Tabel 8.9 Homopolaire vervangingsschema's voor transformatoren | Table 8.9 Zero-sequence equivalent circuits for transformers | of the primary side by multiplying the value by (U 1 /U 2 ) 2 . If the secondary winding is not grounded, then for Z e2 infinity is substituted.
Configuratie | Configuratie | value by (U 1 /U 2 ) 2 . If the secondary winding is not grounded, then for Z e2 infinity is substituted. Table 8.9 Zero-sequence equivalent circuits for transformers
Schakeling | Schakeling | by (U 1 /U 2 ) 2 . If the secondary winding is not grounded, then for Z e2 infinity is substituted. Table 8.9 Zero-sequence equivalent circuits for transformers Configuratie
Homopolair vervangingsschema | Zero-sequence equivalent circuit | (U 1 /U 2 ) 2 . If the secondary winding is not grounded, then for Z e2 infinity is substituted. Table 8.9 Zero-sequence equivalent circuits for transformers Configuratie Schakeling
YNy | YNy | 2 ) 2 . If the secondary winding is not grounded, then for Z e2 infinity is substituted. Table 8.9 Zero-sequence equivalent circuits for transformers Configuratie Schakeling Zero-sequence equivalent circuit
YNd | YNd | ) 2 . If the secondary winding is not grounded, then for Z e2 infinity is substituted. Table 8.9 Zero-sequence equivalent circuits for transformers Configuratie Schakeling Zero-sequence equivalent circuit YNy
ZNy | ZNy | 2 . If the secondary winding is not grounded, then for Z e2 infinity is substituted. Table 8.9 Zero-sequence equivalent circuits for transformers Configuratie Schakeling Zero-sequence equivalent circuit YNy YNd
ZNd | ZNd | . If the secondary winding is not grounded, then for Z e2 infinity is substituted. Table 8.9 Zero-sequence equivalent circuits for transformers Configuratie Schakeling Zero-sequence equivalent circuit YNy YNd ZNy
YNynd | YNynd | If the secondary winding is not grounded, then for Z e2 infinity is substituted. Table 8.9 Zero-sequence equivalent circuits for transformers Configuratie Schakeling Zero-sequence equivalent circuit YNy YNd ZNy ZNd
Indien de schattingsmethode niet voldoende nauwkeurig wordt bevonden, moeten de homopolaire impedanties gemeten worden. Afhankelijk van het type transformator en de toegepaste configuratie in de wikkelingen zijn 1, 2 of 3 metingen nodig. In het geval dat geen sterpunt is uitgevoerd, is geen homopolaire meting mogelijk. Een homopolaire meting kan namelijk alleen plaatsvinden vanaf een YN- of een ZN-wikkeling. In het geval van een transformator met een YNd configuratie volstaat een meting aan de primaire zijde met de sterwikkeling. In geval van een transformator met een YNynd configuratie moeten minimaal drie metingen worden uitgevoerd. Dit kan op de volgende twee manieren plaatsvinden. | If the estimation method is not found to be sufficiently accurate, the zero-sequence impedances must be measured. Depending on the type of transformer and the applied configuration in the windings, 1, 2, or 3 measurements are needed. In the case where no neutral point is implemented, a zero-sequence measurement is not possible. A zero-sequence measurement can only be conducted from a YN or ZN winding. In the case of a transformer with a YNd configuration, a measurement on the primary side with the star winding is sufficient. In the case of a transformer with a YNynd configuration, at least three measurements must be performed. This can be done in the following two ways. | the secondary winding is not grounded, then for Z e2 infinity is substituted. Table 8.9 Zero-sequence equivalent circuits for transformers Configuratie Schakeling Zero-sequence equivalent circuit YNy YNd ZNy ZNd YNynd
De driehoekswikkeling van de YNynd transformator kan geopend worden | The delta winding of the YNynd transformer can be opened | star winding is sufficient. In the case of a transformer with a YNynd configuration, at least three measurements must be performed. This can be done in the following two ways.
Indien het mogelijk is de driehoekswikkeling te openen (sommige transformatoren hebben daar een voorziening voor), kunnen direct de homopolaire impedanties van wikkeling 1 naar 2, van 1 naar 3 en van 2 naar 3 gemeten worden (Kraaij). De meting wordt uitgevoerd door een homopolaire spanning op de drie parallelgeschakelde spoelen van de te meten zijde aan te brengen. Onderstaande methode wordt daartoe gevolgd: | If it is possible to open the delta winding (some transformers have a provision for this), the homopolar impedances from winding 1 to 2, from 1 to 3, and from 2 to 3 can be measured directly (Kraaij). The measurement is performed by applying a homopolar voltage to the three parallel-connected coils on the side to be measured. The following method is used for this purpose: | with a YNynd configuration, at least three measurements must be performed. This can be done in the following two ways. The delta winding of the YNynd transformer can be opened
Meting | Meting | directly (Kraaij). The measurement is performed by applying a homopolar voltage to the three parallel-connected coils on the side to be measured. The following method is used for this purpose:
Primaire wikkeling | Primary winding | (Kraaij). The measurement is performed by applying a homopolar voltage to the three parallel-connected coils on the side to be measured. The following method is used for this purpose: Meting
Secundaire wikkeling | Secondary winding | measurement is performed by applying a homopolar voltage to the three parallel-connected coils on the side to be measured. The following method is used for this purpose: Meting Primary winding
Tertiaire wikkeling | Tertiary winding | performed by applying a homopolar voltage to the three parallel-connected coils on the side to be measured. The following method is used for this purpose: Meting Primary winding Secondary winding
Z | Z | applying a homopolar voltage to the three parallel-connected coils on the side to be measured. The following method is used for this purpose: Meting Primary winding Secondary winding Tertiary winding
0,12 | 0.12 | a homopolar voltage to the three parallel-connected coils on the side to be measured. The following method is used for this purpose: Meting Primary winding Secondary winding Tertiary winding Z
Homopolaire spanning | Homopolar voltage | homopolar voltage to the three parallel-connected coils on the side to be measured. The following method is used for this purpose: Meting Primary winding Secondary winding Tertiary winding Z 0.12
Kortsluiten | Kortsluiten | to the three parallel-connected coils on the side to be measured. The following method is used for this purpose: Meting Primary winding Secondary winding Tertiary winding Z 0.12 Homopolar voltage
Driehoek openen | Open delta | the three parallel-connected coils on the side to be measured. The following method is used for this purpose: Meting Primary winding Secondary winding Tertiary winding Z 0.12 Homopolar voltage Kortsluiten
Z | Z | parallel-connected coils on the side to be measured. The following method is used for this purpose: Meting Primary winding Secondary winding Tertiary winding Z 0.12 Homopolar voltage Kortsluiten Open delta
0,13 | 0.13 | coils on the side to be measured. The following method is used for this purpose: Meting Primary winding Secondary winding Tertiary winding Z 0.12 Homopolar voltage Kortsluiten Open delta Z
Homopolaire spanning | Homopolar voltage | on the side to be measured. The following method is used for this purpose: Meting Primary winding Secondary winding Tertiary winding Z 0.12 Homopolar voltage Kortsluiten Open delta Z 0.13
Open laten | Leave open | side to be measured. The following method is used for this purpose: Meting Primary winding Secondary winding Tertiary winding Z 0.12 Homopolar voltage Kortsluiten Open delta Z 0.13 Homopolar voltage
Driehoek sluiten | Close delta | be measured. The following method is used for this purpose: Meting Primary winding Secondary winding Tertiary winding Z 0.12 Homopolar voltage Kortsluiten Open delta Z 0.13 Homopolar voltage Leave open
Z | Z | The following method is used for this purpose: Meting Primary winding Secondary winding Tertiary winding Z 0.12 Homopolar voltage Kortsluiten Open delta Z 0.13 Homopolar voltage Leave open Close delta
0,23 | 0.23 | following method is used for this purpose: Meting Primary winding Secondary winding Tertiary winding Z 0.12 Homopolar voltage Kortsluiten Open delta Z 0.13 Homopolar voltage Leave open Close delta Z
Open laten | Leave open | method is used for this purpose: Meting Primary winding Secondary winding Tertiary winding Z 0.12 Homopolar voltage Kortsluiten Open delta Z 0.13 Homopolar voltage Leave open Close delta Z 0.23
Homopolaire spanning | Homopolar voltage | used for this purpose: Meting Primary winding Secondary winding Tertiary winding Z 0.12 Homopolar voltage Kortsluiten Open delta Z 0.13 Homopolar voltage Leave open Close delta Z 0.23 Leave open
Driehoek sluiten | Close delta | this purpose: Meting Primary winding Secondary winding Tertiary winding Z 0.12 Homopolar voltage Kortsluiten Open delta Z 0.13 Homopolar voltage Leave open Close delta Z 0.23 Leave open Homopolar voltage
Alle gemeten impedanties moeten vervolgens betrokken worden op hetzelfde spanningsniveau, bijvoorbeeld van de primaire zijde. Hierna kunnen de impedanties | All measured impedances must then be referenced to the same voltage level, for example, from the primary side. After this, the impedances can | Meting Primary winding Secondary winding Tertiary winding Z 0.12 Homopolar voltage Kortsluiten Open delta Z 0.13 Homopolar voltage Leave open Close delta Z 0.23 Leave open Homopolar voltage Close delta
Z | Z | 0.23 Leave open Homopolar voltage Close delta All measured impedances must then be referenced to the same voltage level, for example, from the primary side. After this, the impedances can
0,1 | 0.1 | Leave open Homopolar voltage Close delta All measured impedances must then be referenced to the same voltage level, for example, from the primary side. After this, the impedances can Z
, | , | open Homopolar voltage Close delta All measured impedances must then be referenced to the same voltage level, for example, from the primary side. After this, the impedances can Z 0.1
Z | Z | Homopolar voltage Close delta All measured impedances must then be referenced to the same voltage level, for example, from the primary side. After this, the impedances can Z 0.1 ,
0,2 | 0.2 | voltage Close delta All measured impedances must then be referenced to the same voltage level, for example, from the primary side. After this, the impedances can Z 0.1 , Z
en | en | Close delta All measured impedances must then be referenced to the same voltage level, for example, from the primary side. After this, the impedances can Z 0.1 , Z 0.2
Z | Z | delta All measured impedances must then be referenced to the same voltage level, for example, from the primary side. After this, the impedances can Z 0.1 , Z 0.2 en
0,3 | 0.3 | All measured impedances must then be referenced to the same voltage level, for example, from the primary side. After this, the impedances can Z 0.1 , Z 0.2 en Z
van het vervangingsschema berekend worden op dezelfde wijze als de normale impedanties. | of the equivalent circuit can be calculated in the same way as the normal impedances. | measured impedances must then be referenced to the same voltage level, for example, from the primary side. After this, the impedances can Z 0.1 , Z 0.2 en Z 0.3
Rekenvoorbeeld | Rekenvoorbeeld | primary side. After this, the impedances can Z 0.1 , Z 0.2 en Z 0.3 of the equivalent circuit can be calculated in the same way as the normal impedances.
Impedantie | Impedantie | side. After this, the impedances can Z 0.1 , Z 0.2 en Z 0.3 of the equivalent circuit can be calculated in the same way as the normal impedances. Rekenvoorbeeld
Gemeten waarde (Ω) | Measured value (Ω) | After this, the impedances can Z 0.1 , Z 0.2 en Z 0.3 of the equivalent circuit can be calculated in the same way as the normal impedances. Rekenvoorbeeld Impedantie
Betrokken op primaire zijde (Ω) | Referred to the primary side (Ω) | impedances can Z 0.1 , Z 0.2 en Z 0.3 of the equivalent circuit can be calculated in the same way as the normal impedances. Rekenvoorbeeld Impedantie Measured value (Ω)
Z | Z | 0.2 en Z 0.3 of the equivalent circuit can be calculated in the same way as the normal impedances. Rekenvoorbeeld Impedantie Measured value (Ω) Referred to the primary side (Ω)
0,12 | 0.12 | en Z 0.3 of the equivalent circuit can be calculated in the same way as the normal impedances. Rekenvoorbeeld Impedantie Measured value (Ω) Referred to the primary side (Ω) Z
1,1 + j33,3 | 1.1 + j33.3 | Z 0.3 of the equivalent circuit can be calculated in the same way as the normal impedances. Rekenvoorbeeld Impedantie Measured value (Ω) Referred to the primary side (Ω) Z 0.12
1,1 + j33,3 | 1.1 + j33.3 | the equivalent circuit can be calculated in the same way as the normal impedances. Rekenvoorbeeld Impedantie Measured value (Ω) Referred to the primary side (Ω) Z 0.12 1.1 + j33.3
Z | Z | can be calculated in the same way as the normal impedances. Rekenvoorbeeld Impedantie Measured value (Ω) Referred to the primary side (Ω) Z 0.12 1.1 + j33.3 1.1 + j33.3
0,13 | 0.13 | be calculated in the same way as the normal impedances. Rekenvoorbeeld Impedantie Measured value (Ω) Referred to the primary side (Ω) Z 0.12 1.1 + j33.3 1.1 + j33.3 Z
2,4 + j77,5 | 2.4 + j77.5 | calculated in the same way as the normal impedances. Rekenvoorbeeld Impedantie Measured value (Ω) Referred to the primary side (Ω) Z 0.12 1.1 + j33.3 1.1 + j33.3 Z 0.13
2,4 + j77,5 | 2.4 + j77.5 | same way as the normal impedances. Rekenvoorbeeld Impedantie Measured value (Ω) Referred to the primary side (Ω) Z 0.12 1.1 + j33.3 1.1 + j33.3 Z 0.13 2.4 + j77.5
Z | Z | the normal impedances. Rekenvoorbeeld Impedantie Measured value (Ω) Referred to the primary side (Ω) Z 0.12 1.1 + j33.3 1.1 + j33.3 Z 0.13 2.4 + j77.5 2.4 + j77.5
0,23 | 0.23 | normal impedances. Rekenvoorbeeld Impedantie Measured value (Ω) Referred to the primary side (Ω) Z 0.12 1.1 + j33.3 1.1 + j33.3 Z 0.13 2.4 + j77.5 2.4 + j77.5 Z
0,3 + j5,0 | 0.3 + j5.0 | impedances. Rekenvoorbeeld Impedantie Measured value (Ω) Referred to the primary side (Ω) Z 0.12 1.1 + j33.3 1.1 + j33.3 Z 0.13 2.4 + j77.5 2.4 + j77.5 Z 0.23
2,5 + j40,8 | 2.5 + j40.8 | Measured value (Ω) Referred to the primary side (Ω) Z 0.12 1.1 + j33.3 1.1 + j33.3 Z 0.13 2.4 + j77.5 2.4 + j77.5 Z 0.23 0.3 + j5.0
Hieruit kunnen de impedanties | From this, the impedances can | Referred to the primary side (Ω) Z 0.12 1.1 + j33.3 1.1 + j33.3 Z 0.13 2.4 + j77.5 2.4 + j77.5 Z 0.23 0.3 + j5.0 2.5 + j40.8
Z | Z | (Ω) Z 0.12 1.1 + j33.3 1.1 + j33.3 Z 0.13 2.4 + j77.5 2.4 + j77.5 Z 0.23 0.3 + j5.0 2.5 + j40.8 From this, the impedances can
0,1 | 0.1 | Z 0.12 1.1 + j33.3 1.1 + j33.3 Z 0.13 2.4 + j77.5 2.4 + j77.5 Z 0.23 0.3 + j5.0 2.5 + j40.8 From this, the impedances can Z
, | , | 0.12 1.1 + j33.3 1.1 + j33.3 Z 0.13 2.4 + j77.5 2.4 + j77.5 Z 0.23 0.3 + j5.0 2.5 + j40.8 From this, the impedances can Z 0.1
Z | Z | 1.1 + j33.3 1.1 + j33.3 Z 0.13 2.4 + j77.5 2.4 + j77.5 Z 0.23 0.3 + j5.0 2.5 + j40.8 From this, the impedances can Z 0.1 ,
0,2 | 0.2 | + j33.3 1.1 + j33.3 Z 0.13 2.4 + j77.5 2.4 + j77.5 Z 0.23 0.3 + j5.0 2.5 + j40.8 From this, the impedances can Z 0.1 , Z
en | en | j33.3 1.1 + j33.3 Z 0.13 2.4 + j77.5 2.4 + j77.5 Z 0.23 0.3 + j5.0 2.5 + j40.8 From this, the impedances can Z 0.1 , Z 0.2
Z | Z | 1.1 + j33.3 Z 0.13 2.4 + j77.5 2.4 + j77.5 Z 0.23 0.3 + j5.0 2.5 + j40.8 From this, the impedances can Z 0.1 , Z 0.2 en
0,3 | 0.3 | + j33.3 Z 0.13 2.4 + j77.5 2.4 + j77.5 Z 0.23 0.3 + j5.0 2.5 + j40.8 From this, the impedances can Z 0.1 , Z 0.2 en Z
van het vervangingsschema berekend worden: | can be calculated from the replacement diagram: | j33.3 Z 0.13 2.4 + j77.5 2.4 + j77.5 Z 0.23 0.3 + j5.0 2.5 + j40.8 From this, the impedances can Z 0.1 , Z 0.2 en Z 0.3
[ | [ | + j77.5 Z 0.23 0.3 + j5.0 2.5 + j40.8 From this, the impedances can Z 0.1 , Z 0.2 en Z 0.3 can be calculated from the replacement diagram:
8.51 | 8.51 | j77.5 Z 0.23 0.3 + j5.0 2.5 + j40.8 From this, the impedances can Z 0.1 , Z 0.2 en Z 0.3 can be calculated from the replacement diagram: [
] | ] | Z 0.23 0.3 + j5.0 2.5 + j40.8 From this, the impedances can Z 0.1 , Z 0.2 en Z 0.3 can be calculated from the replacement diagram: [ 8.51
De driehoekswikkeling van de YNynd transformator kan niet geopend worden | The delta winding of the YNynd transformer cannot be opened. | 0.23 0.3 + j5.0 2.5 + j40.8 From this, the impedances can Z 0.1 , Z 0.2 en Z 0.3 can be calculated from the replacement diagram: [ 8.51 ]
Indien het niet mogelijk is de driehoekswikkeling te openen, wordt bij de meting een ietwat gewijzigde methode gevolgd. Het is namelijk zo dat bij de meting van wikkeling 1 naar wikkeling 2, waarbij wikkeling 2 wordt kortgesloten, ook de niet geopende wikkeling 3 wordt meegemeten. In wezen wordt dan de impedantie gemeten van wikkeling 1 naar de parallelschakeling van wikkelingen 2 en 3. Dit wordt aangegeven met // in de index. Daarentegen wordt wel de impedantie gemeten van wikkeling 1 naar 3 en van wikkeling 2 naar 3. | If it is not possible to open the delta winding, a slightly modified method is followed during the measurement. Specifically, when measuring from winding 1 to winding 2, with winding 2 short-circuited, the non-opened winding 3 is also included in the measurement. Essentially, the impedance is then measured from winding 1 to the parallel connection of windings 2 and 3. This is indicated with // in the index. Conversely, the impedance is measured from winding 1 to 3 and from winding 2 to 3. | impedances can Z 0.1 , Z 0.2 en Z 0.3 can be calculated from the replacement diagram: [ 8.51 ] The delta winding of the YNynd transformer cannot be opened.
Meting | Meting | connection of windings 2 and 3. This is indicated with // in the index. Conversely, the impedance is measured from winding 1 to 3 and from winding 2 to 3.
Primaire wikkeling | Primary winding | of windings 2 and 3. This is indicated with // in the index. Conversely, the impedance is measured from winding 1 to 3 and from winding 2 to 3. Meting
Secundaire wikkeling | Secondary winding | 2 and 3. This is indicated with // in the index. Conversely, the impedance is measured from winding 1 to 3 and from winding 2 to 3. Meting Primary winding
Tertiaire wikkeling | Tertiary winding | 3. This is indicated with // in the index. Conversely, the impedance is measured from winding 1 to 3 and from winding 2 to 3. Meting Primary winding Secondary winding
Z | Z | is indicated with // in the index. Conversely, the impedance is measured from winding 1 to 3 and from winding 2 to 3. Meting Primary winding Secondary winding Tertiary winding
0,12//3 | 0.12//3 | indicated with // in the index. Conversely, the impedance is measured from winding 1 to 3 and from winding 2 to 3. Meting Primary winding Secondary winding Tertiary winding Z
Homopolaire spanning | Zero-sequence voltage | with // in the index. Conversely, the impedance is measured from winding 1 to 3 and from winding 2 to 3. Meting Primary winding Secondary winding Tertiary winding Z 0.12//3
Kortsluiten | Kortsluiten | in the index. Conversely, the impedance is measured from winding 1 to 3 and from winding 2 to 3. Meting Primary winding Secondary winding Tertiary winding Z 0.12//3 Zero-sequence voltage
Driehoek gesloten | Delta closed | the index. Conversely, the impedance is measured from winding 1 to 3 and from winding 2 to 3. Meting Primary winding Secondary winding Tertiary winding Z 0.12//3 Zero-sequence voltage Kortsluiten
Z | Z | Conversely, the impedance is measured from winding 1 to 3 and from winding 2 to 3. Meting Primary winding Secondary winding Tertiary winding Z 0.12//3 Zero-sequence voltage Kortsluiten Delta closed
0,13 | 0.13 | the impedance is measured from winding 1 to 3 and from winding 2 to 3. Meting Primary winding Secondary winding Tertiary winding Z 0.12//3 Zero-sequence voltage Kortsluiten Delta closed Z
Homopolaire spanning | Zero-sequence voltage | impedance is measured from winding 1 to 3 and from winding 2 to 3. Meting Primary winding Secondary winding Tertiary winding Z 0.12//3 Zero-sequence voltage Kortsluiten Delta closed Z 0.13
Open laten | Leave open | measured from winding 1 to 3 and from winding 2 to 3. Meting Primary winding Secondary winding Tertiary winding Z 0.12//3 Zero-sequence voltage Kortsluiten Delta closed Z 0.13 Zero-sequence voltage
Driehoek gesloten | Delta closed | winding 1 to 3 and from winding 2 to 3. Meting Primary winding Secondary winding Tertiary winding Z 0.12//3 Zero-sequence voltage Kortsluiten Delta closed Z 0.13 Zero-sequence voltage Leave open
Z | Z | to 3 and from winding 2 to 3. Meting Primary winding Secondary winding Tertiary winding Z 0.12//3 Zero-sequence voltage Kortsluiten Delta closed Z 0.13 Zero-sequence voltage Leave open Delta closed
0,23 | 0.23 | 3 and from winding 2 to 3. Meting Primary winding Secondary winding Tertiary winding Z 0.12//3 Zero-sequence voltage Kortsluiten Delta closed Z 0.13 Zero-sequence voltage Leave open Delta closed Z
Open laten | Leave open | and from winding 2 to 3. Meting Primary winding Secondary winding Tertiary winding Z 0.12//3 Zero-sequence voltage Kortsluiten Delta closed Z 0.13 Zero-sequence voltage Leave open Delta closed Z 0.23
Homopolaire spanning | Zero-sequence voltage | winding 2 to 3. Meting Primary winding Secondary winding Tertiary winding Z 0.12//3 Zero-sequence voltage Kortsluiten Delta closed Z 0.13 Zero-sequence voltage Leave open Delta closed Z 0.23 Leave open
Driehoek gesloten | Delta closed | to 3. Meting Primary winding Secondary winding Tertiary winding Z 0.12//3 Zero-sequence voltage Kortsluiten Delta closed Z 0.13 Zero-sequence voltage Leave open Delta closed Z 0.23 Leave open Zero-sequence voltage
Alle gemeten impedanties moeten vervolgens betrokken worden op hetzelfde spanningsniveau, bijvoorbeeld van de primaire zijde. Hierna kunnen de impedanties | All measured impedances must then be referenced to the same voltage level, for example, from the primary side. After this, the impedances can | Meting Primary winding Secondary winding Tertiary winding Z 0.12//3 Zero-sequence voltage Kortsluiten Delta closed Z 0.13 Zero-sequence voltage Leave open Delta closed Z 0.23 Leave open Zero-sequence voltage Delta closed
Z | Z | 0.23 Leave open Zero-sequence voltage Delta closed All measured impedances must then be referenced to the same voltage level, for example, from the primary side. After this, the impedances can
0,1 | 0.1 | Leave open Zero-sequence voltage Delta closed All measured impedances must then be referenced to the same voltage level, for example, from the primary side. After this, the impedances can Z
, | , | open Zero-sequence voltage Delta closed All measured impedances must then be referenced to the same voltage level, for example, from the primary side. After this, the impedances can Z 0.1
Z | Z | Zero-sequence voltage Delta closed All measured impedances must then be referenced to the same voltage level, for example, from the primary side. After this, the impedances can Z 0.1 ,
0,2 | 0.2 | voltage Delta closed All measured impedances must then be referenced to the same voltage level, for example, from the primary side. After this, the impedances can Z 0.1 , Z
en | en | Delta closed All measured impedances must then be referenced to the same voltage level, for example, from the primary side. After this, the impedances can Z 0.1 , Z 0.2
Z | Z | closed All measured impedances must then be referenced to the same voltage level, for example, from the primary side. After this, the impedances can Z 0.1 , Z 0.2 en
0,3 | 0.3 | All measured impedances must then be referenced to the same voltage level, for example, from the primary side. After this, the impedances can Z 0.1 , Z 0.2 en Z
van het vervangingsschema berekend worden. De afleiding van onderstaande formules wordt hier niet gegeven. | can be calculated from the equivalent circuit. The derivation of the formulas below is not provided here. | measured impedances must then be referenced to the same voltage level, for example, from the primary side. After this, the impedances can Z 0.1 , Z 0.2 en Z 0.3
[ | [ | After this, the impedances can Z 0.1 , Z 0.2 en Z 0.3 can be calculated from the equivalent circuit. The derivation of the formulas below is not provided here.
8.52 | 8.52 | this, the impedances can Z 0.1 , Z 0.2 en Z 0.3 can be calculated from the equivalent circuit. The derivation of the formulas below is not provided here. [
] | ] | the impedances can Z 0.1 , Z 0.2 en Z 0.3 can be calculated from the equivalent circuit. The derivation of the formulas below is not provided here. [ 8.52
Rekenvoorbeeld | Rekenvoorbeeld | impedances can Z 0.1 , Z 0.2 en Z 0.3 can be calculated from the equivalent circuit. The derivation of the formulas below is not provided here. [ 8.52 ]
Impedantie | Impedantie | can Z 0.1 , Z 0.2 en Z 0.3 can be calculated from the equivalent circuit. The derivation of the formulas below is not provided here. [ 8.52 ] Rekenvoorbeeld
Gemeten waarde (Ω) | Measured value (Ω) | Z 0.1 , Z 0.2 en Z 0.3 can be calculated from the equivalent circuit. The derivation of the formulas below is not provided here. [ 8.52 ] Rekenvoorbeeld Impedantie
Betrokken op primaire zijde (Ω) | Referred to the primary side (Ω) | Z 0.2 en Z 0.3 can be calculated from the equivalent circuit. The derivation of the formulas below is not provided here. [ 8.52 ] Rekenvoorbeeld Impedantie Measured value (Ω)
Z | Z | be calculated from the equivalent circuit. The derivation of the formulas below is not provided here. [ 8.52 ] Rekenvoorbeeld Impedantie Measured value (Ω) Referred to the primary side (Ω)
0,12//3 | 0.12//3 | calculated from the equivalent circuit. The derivation of the formulas below is not provided here. [ 8.52 ] Rekenvoorbeeld Impedantie Measured value (Ω) Referred to the primary side (Ω) Z
1,1 + j33,2 | 1.1 + j33.2 | from the equivalent circuit. The derivation of the formulas below is not provided here. [ 8.52 ] Rekenvoorbeeld Impedantie Measured value (Ω) Referred to the primary side (Ω) Z 0.12//3
1,1 + j33,2 | 1.1 + j33.2 | circuit. The derivation of the formulas below is not provided here. [ 8.52 ] Rekenvoorbeeld Impedantie Measured value (Ω) Referred to the primary side (Ω) Z 0.12//3 1.1 + j33.2
Z | Z | of the formulas below is not provided here. [ 8.52 ] Rekenvoorbeeld Impedantie Measured value (Ω) Referred to the primary side (Ω) Z 0.12//3 1.1 + j33.2 1.1 + j33.2
0,13 | 0.13 | the formulas below is not provided here. [ 8.52 ] Rekenvoorbeeld Impedantie Measured value (Ω) Referred to the primary side (Ω) Z 0.12//3 1.1 + j33.2 1.1 + j33.2 Z
2,4 + j77,5 | 2.4 + j77.5 | formulas below is not provided here. [ 8.52 ] Rekenvoorbeeld Impedantie Measured value (Ω) Referred to the primary side (Ω) Z 0.12//3 1.1 + j33.2 1.1 + j33.2 Z 0.13
2,4 + j77,5 | 2.4 + j77.5 | not provided here. [ 8.52 ] Rekenvoorbeeld Impedantie Measured value (Ω) Referred to the primary side (Ω) Z 0.12//3 1.1 + j33.2 1.1 + j33.2 Z 0.13 2.4 + j77.5
Z | Z | [ 8.52 ] Rekenvoorbeeld Impedantie Measured value (Ω) Referred to the primary side (Ω) Z 0.12//3 1.1 + j33.2 1.1 + j33.2 Z 0.13 2.4 + j77.5 2.4 + j77.5
0,23 | 0.23 | 8.52 ] Rekenvoorbeeld Impedantie Measured value (Ω) Referred to the primary side (Ω) Z 0.12//3 1.1 + j33.2 1.1 + j33.2 Z 0.13 2.4 + j77.5 2.4 + j77.5 Z
0,3 + j5,0 | 0.3 + j5.0 | ] Rekenvoorbeeld Impedantie Measured value (Ω) Referred to the primary side (Ω) Z 0.12//3 1.1 + j33.2 1.1 + j33.2 Z 0.13 2.4 + j77.5 2.4 + j77.5 Z 0.23
2,5 + j40,8 | 2.5 + j40.8 | Measured value (Ω) Referred to the primary side (Ω) Z 0.12//3 1.1 + j33.2 1.1 + j33.2 Z 0.13 2.4 + j77.5 2.4 + j77.5 Z 0.23 0.3 + j5.0
Hieruit kunnen de impedanties | From this, the impedances can | Referred to the primary side (Ω) Z 0.12//3 1.1 + j33.2 1.1 + j33.2 Z 0.13 2.4 + j77.5 2.4 + j77.5 Z 0.23 0.3 + j5.0 2.5 + j40.8
Z | Z | (Ω) Z 0.12//3 1.1 + j33.2 1.1 + j33.2 Z 0.13 2.4 + j77.5 2.4 + j77.5 Z 0.23 0.3 + j5.0 2.5 + j40.8 From this, the impedances can
0,1 | 0.1 | Z 0.12//3 1.1 + j33.2 1.1 + j33.2 Z 0.13 2.4 + j77.5 2.4 + j77.5 Z 0.23 0.3 + j5.0 2.5 + j40.8 From this, the impedances can Z
, Z | , Z | 0.12//3 1.1 + j33.2 1.1 + j33.2 Z 0.13 2.4 + j77.5 2.4 + j77.5 Z 0.23 0.3 + j5.0 2.5 + j40.8 From this, the impedances can Z 0.1
0,2 | 0.2 | + j33.2 1.1 + j33.2 Z 0.13 2.4 + j77.5 2.4 + j77.5 Z 0.23 0.3 + j5.0 2.5 + j40.8 From this, the impedances can Z 0.1 , Z
en Z | and Z | j33.2 1.1 + j33.2 Z 0.13 2.4 + j77.5 2.4 + j77.5 Z 0.23 0.3 + j5.0 2.5 + j40.8 From this, the impedances can Z 0.1 , Z 0.2
0,3 | 0.3 | + j33.2 Z 0.13 2.4 + j77.5 2.4 + j77.5 Z 0.23 0.3 + j5.0 2.5 + j40.8 From this, the impedances can Z 0.1 , Z 0.2 and Z
van het vervangingsschema berekend worden: | can be calculated from the replacement diagram: | j33.2 Z 0.13 2.4 + j77.5 2.4 + j77.5 Z 0.23 0.3 + j5.0 2.5 + j40.8 From this, the impedances can Z 0.1 , Z 0.2 and Z 0.3
[ | [ | + j77.5 Z 0.23 0.3 + j5.0 2.5 + j40.8 From this, the impedances can Z 0.1 , Z 0.2 and Z 0.3 can be calculated from the replacement diagram:
8.53 | 8.53 | j77.5 Z 0.23 0.3 + j5.0 2.5 + j40.8 From this, the impedances can Z 0.1 , Z 0.2 and Z 0.3 can be calculated from the replacement diagram: [
] | ] | Z 0.23 0.3 + j5.0 2.5 + j40.8 From this, the impedances can Z 0.1 , Z 0.2 and Z 0.3 can be calculated from the replacement diagram: [ 8.53
Meting aan een transformator met ZN-wikkeling | Measurement on a transformer with ZN winding | 0.23 0.3 + j5.0 2.5 + j40.8 From this, the impedances can Z 0.1 , Z 0.2 and Z 0.3 can be calculated from the replacement diagram: [ 8.53 ]
Bij een meting aan een YN-wikkeling kan sprake zijn van een koppeling met een andere wikkeling. Zo is er altijd een koppeling naar een driehoekwikkeling. Een zigzagwikkeling is echter homopolair niet gekoppeld. Een ZN-wikkeling kan altijd direct gemeten worden. | When measuring a YN winding, there may be a coupling with another winding. For instance, there is always a coupling to a delta winding. However, a zigzag winding is not homopolar coupled. A ZN winding can always be measured directly. | From this, the impedances can Z 0.1 , Z 0.2 and Z 0.3 can be calculated from the replacement diagram: [ 8.53 ] Measurement on a transformer with ZN winding
Bij een YNdzn transformator worden twee onafhankelijke metingen uitgevoerd, namelijk een meting van de YN naar de d wikkeling en een meting van de zn wikkeling. | In a YNdzn transformer, two independent measurements are performed, namely a measurement from the YN winding to the d winding and a measurement of the zn winding. | with another winding. For instance, there is always a coupling to a delta winding. However, a zigzag winding is not homopolar coupled. A ZN winding can always be measured directly.
Sterpuntimpedantie | Sterpuntimpedantie | be measured directly. In a YNdzn transformer, two independent measurements are performed, namely a measurement from the YN winding to the d winding and a measurement of the zn winding.
De impedantie van het sterpunt naar aarde hoort in het homopolaire schema thuis. Op dezelfde wijze als in paragraaf 8.2.7 beschreven, moet deze impedantie met 3 worden vermenigvuldigd voor opname in het homopolaire componentnetwerk. | The impedance from the neutral point to ground belongs in the homopolar scheme. As described in paragraph 8.2.7, this impedance must be multiplied by 3 for inclusion in the homopolar component network. | measured directly. In a YNdzn transformer, two independent measurements are performed, namely a measurement from the YN winding to the d winding and a measurement of the zn winding. Sterpuntimpedantie
[ | [ | from the neutral point to ground belongs in the homopolar scheme. As described in paragraph 8.2.7, this impedance must be multiplied by 3 for inclusion in the homopolar component network.
8.54 | 8.54 | the neutral point to ground belongs in the homopolar scheme. As described in paragraph 8.2.7, this impedance must be multiplied by 3 for inclusion in the homopolar component network. [
] | ] | neutral point to ground belongs in the homopolar scheme. As described in paragraph 8.2.7, this impedance must be multiplied by 3 for inclusion in the homopolar component network. [ 8.54
8.3.7 Correctie voor kortsluitberekeningen volgens IEC | 8.3.7 Correction for short-circuit calculations according to IEC | point to ground belongs in the homopolar scheme. As described in paragraph 8.2.7, this impedance must be multiplied by 3 for inclusion in the homopolar component network. [ 8.54 ]
Een transformator verbindt twee of meer netwerken van verschillende spanningsniveaus. De internationale norm IEC 60909 schrijft voor dat bij kortsluitberekeningen volgens die norm een correctiefactor | A transformer connects two or more networks of different voltage levels. The international standard IEC 60909 prescribes that for short-circuit calculations according to that standard, a correction factor | As described in paragraph 8.2.7, this impedance must be multiplied by 3 for inclusion in the homopolar component network. [ 8.54 ] 8.3.7 Correction for short-circuit calculations according to IEC
K | K | to IEC A transformer connects two or more networks of different voltage levels. The international standard IEC 60909 prescribes that for short-circuit calculations according to that standard, a correction factor
T | T | IEC A transformer connects two or more networks of different voltage levels. The international standard IEC 60909 prescribes that for short-circuit calculations according to that standard, a correction factor K
op de impedantie van het normale systeem wordt toegepast. Deze factor vertegenwoordigt de invloed van het in bedrijf zijn van de transformator via een correctie op de impedantie. De correctiefactor wordt als volgt berekend: | on the impedance of the normal system is applied. This factor represents the influence of the transformer being in operation through a correction on the impedance. The correction factor is calculated as follows: | A transformer connects two or more networks of different voltage levels. The international standard IEC 60909 prescribes that for short-circuit calculations according to that standard, a correction factor K T
[ | [ | of the normal system is applied. This factor represents the influence of the transformer being in operation through a correction on the impedance. The correction factor is calculated as follows:
8.55 | 8.55 | the normal system is applied. This factor represents the influence of the transformer being in operation through a correction on the impedance. The correction factor is calculated as follows: [
] | ] | normal system is applied. This factor represents the influence of the transformer being in operation through a correction on the impedance. The correction factor is calculated as follows: [ 8.55
waarin: | where: | system is applied. This factor represents the influence of the transformer being in operation through a correction on the impedance. The correction factor is calculated as follows: [ 8.55 ]
c | c | is applied. This factor represents the influence of the transformer being in operation through a correction on the impedance. The correction factor is calculated as follows: [ 8.55 ] where:
max | max | applied. This factor represents the influence of the transformer being in operation through a correction on the impedance. The correction factor is calculated as follows: [ 8.55 ] where: c
spanningsparameter voor de kortsluitberekening; 1,05 voor LS-netten met tolerantie van +6% en in alle overige gevallen 1,1 | voltage parameter for the short-circuit calculation; 1.05 for low-voltage networks with a tolerance of +6% and in all other cases 1.1 | This factor represents the influence of the transformer being in operation through a correction on the impedance. The correction factor is calculated as follows: [ 8.55 ] where: c max
x | x | calculated as follows: [ 8.55 ] where: c max voltage parameter for the short-circuit calculation; 1.05 for low-voltage networks with a tolerance of +6% and in all other cases 1.1
T | T | as follows: [ 8.55 ] where: c max voltage parameter for the short-circuit calculation; 1.05 for low-voltage networks with a tolerance of +6% and in all other cases 1.1 x
per unit waarde van de reactantie: | per unit value of the reactance: | follows: [ 8.55 ] where: c max voltage parameter for the short-circuit calculation; 1.05 for low-voltage networks with a tolerance of +6% and in all other cases 1.1 x T
x | x | max voltage parameter for the short-circuit calculation; 1.05 for low-voltage networks with a tolerance of +6% and in all other cases 1.1 x T per unit value of the reactance:
T | T | voltage parameter for the short-circuit calculation; 1.05 for low-voltage networks with a tolerance of +6% and in all other cases 1.1 x T per unit value of the reactance: x
parameter for the short-circuit calculation; 1.05 for low-voltage networks with a tolerance of +6% and in all other cases 1.1 x T per unit value of the reactance: x T
T | T | the short-circuit calculation; 1.05 for low-voltage networks with a tolerance of +6% and in all other cases 1.1 x T per unit value of the reactance: x T = X
/ (U | / (U | short-circuit calculation; 1.05 for low-voltage networks with a tolerance of +6% and in all other cases 1.1 x T per unit value of the reactance: x T = X T
nom,T | nom,T | 1.05 for low-voltage networks with a tolerance of +6% and in all other cases 1.1 x T per unit value of the reactance: x T = X T / (U
2 | 2 | for low-voltage networks with a tolerance of +6% and in all other cases 1.1 x T per unit value of the reactance: x T = X T / (U nom,T
/ S | / S | low-voltage networks with a tolerance of +6% and in all other cases 1.1 x T per unit value of the reactance: x T = X T / (U nom,T 2
nom,T | nom,T | with a tolerance of +6% and in all other cases 1.1 x T per unit value of the reactance: x T = X T / (U nom,T 2 / S
) | ) | a tolerance of +6% and in all other cases 1.1 x T per unit value of the reactance: x T = X T / (U nom,T 2 / S nom,T
Deze correctiefactor wordt toegepast op de transformatorimpedanties in het normale, inverse en homopolaire systeem. Voor transformatoren met twee wikkelingen zijn dan de gecorrigeerde impedanties: | This correction factor is applied to the transformer impedances in the normal, inverse, and homopolar systems. For transformers with two windings, the corrected impedances are: | tolerance of +6% and in all other cases 1.1 x T per unit value of the reactance: x T = X T / (U nom,T 2 / S nom,T )
[ | [ | 2 / S nom,T ) This correction factor is applied to the transformer impedances in the normal, inverse, and homopolar systems. For transformers with two windings, the corrected impedances are:
8.56 | 8.56 | / S nom,T ) This correction factor is applied to the transformer impedances in the normal, inverse, and homopolar systems. For transformers with two windings, the corrected impedances are: [
] | ] | S nom,T ) This correction factor is applied to the transformer impedances in the normal, inverse, and homopolar systems. For transformers with two windings, the corrected impedances are: [ 8.56
Voor een driewikkelingstransformator worden drie correctiefactoren bepaald: | For a three-winding transformer, three correction factors are determined: | nom,T ) This correction factor is applied to the transformer impedances in the normal, inverse, and homopolar systems. For transformers with two windings, the corrected impedances are: [ 8.56 ]
[ | [ | transformer impedances in the normal, inverse, and homopolar systems. For transformers with two windings, the corrected impedances are: [ 8.56 ] For a three-winding transformer, three correction factors are determined:
8.57 | 8.57 | impedances in the normal, inverse, and homopolar systems. For transformers with two windings, the corrected impedances are: [ 8.56 ] For a three-winding transformer, three correction factors are determined: [
] | ] | in the normal, inverse, and homopolar systems. For transformers with two windings, the corrected impedances are: [ 8.56 ] For a three-winding transformer, three correction factors are determined: [ 8.57
Deze correctiefactor wordt toegepast op de transformatorimpedanties in het normale, inverse en homopolaire systeem. Voor transformatoren met twee wikkelingen zijn dan de gecorrigeerde impedanties: | This correction factor is applied to the transformer impedances in the normal, inverse, and homopolar systems. For transformers with two windings, the corrected impedances are: | the normal, inverse, and homopolar systems. For transformers with two windings, the corrected impedances are: [ 8.56 ] For a three-winding transformer, three correction factors are determined: [ 8.57 ]
en | en | are determined: [ 8.57 ] This correction factor is applied to the transformer impedances in the normal, inverse, and homopolar systems. For transformers with two windings, the corrected impedances are:
[ | [ | determined: [ 8.57 ] This correction factor is applied to the transformer impedances in the normal, inverse, and homopolar systems. For transformers with two windings, the corrected impedances are: en
8.58 | 8.58 | [ 8.57 ] This correction factor is applied to the transformer impedances in the normal, inverse, and homopolar systems. For transformers with two windings, the corrected impedances are: en [
] | ] | 8.57 ] This correction factor is applied to the transformer impedances in the normal, inverse, and homopolar systems. For transformers with two windings, the corrected impedances are: en [ 8.58
Daarna worden de gecorrigeerde impedanties omgezet naar de interne transformatorimpedanties van het vervangingsschema. | Afterward, the corrected impedances are converted to the internal transformer impedances of the equivalent circuit. | ] This correction factor is applied to the transformer impedances in the normal, inverse, and homopolar systems. For transformers with two windings, the corrected impedances are: en [ 8.58 ]
De correctiefactor wordt niet toegepast op de eventueel aanwezige aardingsimpedantie tussen sterpunt en aarde. | The correction factor is not applied to any grounding impedance that may be present between the neutral point and ground. | homopolar systems. For transformers with two windings, the corrected impedances are: en [ 8.58 ] Afterward, the corrected impedances are converted to the internal transformer impedances of the equivalent circuit.
8.3.8 Inrushstromen | 8.3.8 Inrush Currents | converted to the internal transformer impedances of the equivalent circuit. The correction factor is not applied to any grounding impedance that may be present between the neutral point and ground.
Bij het inschakelen van een onbelaste transformator treden inrushstromen op. Deze stromen kunnen waarden van 10 tot 15 maal de nominale stroom bereiken. Deze stromen hebben invloed op de transformatorbeveiliging en veroorzaken spanningsdips. De grootte van de inrushstroom kan worden vastgesteld door een meting of met een berekening. | When energizing an unloaded transformer, inrush currents occur. These currents can reach values of 10 to 15 times the nominal current. These currents affect transformer protection and cause voltage dips. The magnitude of the inrush current can be determined by measurement or by calculation. | internal transformer impedances of the equivalent circuit. The correction factor is not applied to any grounding impedance that may be present between the neutral point and ground. 8.3.8 Inrush Currents
De inrushstroom wordt veroorzaakt doordat in de transformatorkern na het uitschakelen nog lange tijd een remanente flux aanwezig kan zijn. Afhankelijk van het moment dat in de sinus van de 50 Hz spanning wordt ingeschakeld, kan deze flux samen met het opbouwen van de flux na het inschakelen van de netspanning leiden tot verzadiging van de ijzerkern. De inrushstroom wordt gekenmerkt door een sterke tweede harmonische. De inrushstroom zwakt relatief langzaam af. Dit is afhankelijk van de R/X verhouding in het voedende net. | The inrush current is caused by the presence of residual flux in the transformer core that can remain for a long time after switching off. Depending on the moment in the 50 Hz voltage sine wave when switching on occurs, this flux, combined with the buildup of flux after switching on the mains voltage, can lead to saturation of the iron core. The inrush current is characterized by a strong second harmonic. The inrush current diminishes relatively slowly. This is dependent on the R/X ratio in the supplying network. | 10 to 15 times the nominal current. These currents affect transformer protection and cause voltage dips. The magnitude of the inrush current can be determined by measurement or by calculation.
Figuur 8.14 Inrushstroom bij het inschakelen van een onbelaste transformator | Figure 8.14 Inrush current when energizing an unloaded transformer | the iron core. The inrush current is characterized by a strong second harmonic. The inrush current diminishes relatively slowly. This is dependent on the R/X ratio in the supplying network.
Er bestaan modellen voor de berekening van de inrushstroom, maar deze zijn complex en maken gebruik van parameters die de netplanner meestal niet tot zijn beschikking heeft. In veel gevallen is alleen de maximale waarde van de inrushstroom van belang. Deze waarde kan worden benaderd met behulp van een kortsluitberekening, waarbij de transformator aan de secundaire zijde wordt kortgesloten. In geval van een net met impedantie | There are models for calculating the inrush current, but these are complex and use parameters that the network planner usually does not have at their disposal. In many cases, only the maximum value of the inrush current is important. This value can be approximated using a short-circuit calculation, where the transformer is short-circuited on the secondary side. In the case of a network with impedance | a strong second harmonic. The inrush current diminishes relatively slowly. This is dependent on the R/X ratio in the supplying network. Figure 8.14 Inrush current when energizing an unloaded transformer
Z | Z | inrush current is important. This value can be approximated using a short-circuit calculation, where the transformer is short-circuited on the secondary side. In the case of a network with impedance
Q | Q | current is important. This value can be approximated using a short-circuit calculation, where the transformer is short-circuited on the secondary side. In the case of a network with impedance Z
(vergelijking 8.2) en een transformator met impedantie | (equation 8.2) and a transformer with impedance | is important. This value can be approximated using a short-circuit calculation, where the transformer is short-circuited on the secondary side. In the case of a network with impedance Z Q
Z | Z | using a short-circuit calculation, where the transformer is short-circuited on the secondary side. In the case of a network with impedance Z Q (equation 8.2) and a transformer with impedance
T | T | a short-circuit calculation, where the transformer is short-circuited on the secondary side. In the case of a network with impedance Z Q (equation 8.2) and a transformer with impedance Z
(vergelijking 8.34) is de maximale waarde van de inrushstroom: | (equation 8.34) is the maximum value of the inrush current: | short-circuit calculation, where the transformer is short-circuited on the secondary side. In the case of a network with impedance Z Q (equation 8.2) and a transformer with impedance Z T
[ | [ | side. In the case of a network with impedance Z Q (equation 8.2) and a transformer with impedance Z T (equation 8.34) is the maximum value of the inrush current:
8.59 | 8.59 | In the case of a network with impedance Z Q (equation 8.2) and a transformer with impedance Z T (equation 8.34) is the maximum value of the inrush current: [
] | ] | the case of a network with impedance Z Q (equation 8.2) and a transformer with impedance Z T (equation 8.34) is the maximum value of the inrush current: [ 8.59
8.4 Aardingstransformator en nulpunttransformator | 8.4 Grounding Transformer and Neutral Point Transformer | case of a network with impedance Z Q (equation 8.2) and a transformer with impedance Z T (equation 8.34) is the maximum value of the inrush current: [ 8.59 ]
Een aardingstransformator en een nulpunttransformator zijn in principe beide hetzelfde apparaat. Beide zijn opgebouwd als een zigzag-transformator. Deze transformatoren worden in MS-netten en in LS-netten toegepast. In MS-netten die gevoed worden met een Yd-transformator is geen sterpunt aanwezig op de secundaire zijde van de transformator. Indien in deze netten toch een sterpunt gewenst is, zodat het net impedantie-geaard kan worden, wordt een aardingstransformator toegepast. In LS-netten komt het voor dat de belastingen in zodanige mate asymmetrisch over de fasen verdeeld zijn, dat de fasespanningen onderling verschillen. Het gevolg is dat een stroom door de nulgeleider loopt die extra verliezen veroorzaakt en dat bovendien de spanning op de nulgeleider niet meer nul is (sterpuntverschuiving). Dit verschijnsel is het sterkst in uitgestrekte LS-netten met relatief weinig aansluitingen. | A grounding transformer and a neutral point transformer are essentially the same device. Both are constructed as a zigzag transformer. These transformers are used in medium voltage (MV) networks and low voltage (LV) networks. In MV networks that are supplied with a Yd transformer, there is no neutral point on the secondary side of the transformer. If a neutral point is desired in these networks so that the network can be impedance-grounded, a grounding transformer is used. In LV networks, it can occur that the loads are distributed asymmetrically across the phases to such an extent that the phase voltages differ from each other. The result is that a current flows through the neutral conductor, causing additional losses, and furthermore, the voltage on the neutral conductor is no longer zero (neutral point shift). This phenomenon is most pronounced in extensive LV networks with relatively few connections. | Q (equation 8.2) and a transformer with impedance Z T (equation 8.34) is the maximum value of the inrush current: [ 8.59 ] 8.4 Grounding Transformer and Neutral Point Transformer
Een nulpunttransformator vermindert de scheefheid van de stromen in het LS-net en daarmee de scheefheid van de spanningen. | A neutral point transformer reduces the imbalance of currents in the LV network and thereby the imbalance of voltages. | additional losses, and furthermore, the voltage on the neutral conductor is no longer zero (neutral point shift). This phenomenon is most pronounced in extensive LV networks with relatively few connections.
Door toepassing van de aardings- of nulpunttransformator wijzigt de stroomverdeling in het net. In geval van een eenfasebelasting in een LS-net vermindert hierdoor de spanningsverlaging van de belaste fase ten opzichte van de nulgeleider. Tegelijkertijd vermindert de spanningsverhoging op de onbelaste fasen ten opzichte van de nulgeleider. | By applying the grounding or neutral point transformer, the current distribution in the network changes. In the case of a single-phase load in an LV network, this reduces the voltage drop of the loaded phase relative to the neutral conductor. At the same time, it reduces the voltage rise on the unloaded phases relative to the neutral conductor. | is most pronounced in extensive LV networks with relatively few connections. A neutral point transformer reduces the imbalance of currents in the LV network and thereby the imbalance of voltages.
Een aardings- of nulpunttransformator is in principe een driefasentransformator met een overzetverhouding van 1. De wikkelingen op een driebenig juk zijn geschakeld in een zigzagconfiguratie, zoals aangegeven in figuur 8.15. Indien de transformator op een normaal symmetrisch driefasensysteem is aangesloten, is de impedantie zeer hoog. Er vloeit dan alleen de magnetiseringsstroom. De spanning op het sterpunt van de nulpunttransformator is dan nul. | A grounding or neutral point transformer is essentially a three-phase transformer with a turns ratio of 1. The windings on a three-legged core are connected in a zigzag configuration, as shown in figure 8.15. When the transformer is connected to a normally symmetrical three-phase system, the impedance is very high. Only the magnetizing current flows then. The voltage at the neutral point of the neutral point transformer is then zero. | the voltage drop of the loaded phase relative to the neutral conductor. At the same time, it reduces the voltage rise on the unloaded phases relative to the neutral conductor.
Figuur 8.15 Werking van een aardings- of nulpuntstransformator in een MS-net | Figure 8.15 Operation of a grounding or neutral point transformer in a medium voltage network | a normally symmetrical three-phase system, the impedance is very high. Only the magnetizing current flows then. The voltage at the neutral point of the neutral point transformer is then zero.
Indien door de transformator een homopolaire stroom loopt, is de homopolaire impedantie zeer klein. Dat wordt met behulp van figuur 8.15 aangetoond. Deze figuur toont de werking van een aardingstransformator in een MS-net, waarin tussen fase C en de aarde een kortsluiting is aangebracht. De pijlen langs de wikkelingen geven de stroomrichting van | If a homopolar current flows through the transformer, the homopolar impedance is very small. This is demonstrated with the help of figure 8.15. This figure shows the operation of a grounding transformer in a medium voltage network, where a short circuit is created between phase C and the ground. The arrows along the windings indicate the direction of the current. | then. The voltage at the neutral point of the neutral point transformer is then zero. Figure 8.15 Operation of a grounding or neutral point transformer in a medium voltage network
I | I | grounding transformer in a medium voltage network, where a short circuit is created between phase C and the ground. The arrows along the windings indicate the direction of the current.
0 | 0 | transformer in a medium voltage network, where a short circuit is created between phase C and the ground. The arrows along the windings indicate the direction of the current. I
aan. De veldrichting is daarmee gekoppeld. Het blijkt dat in elke poot van het juk de magnetische velden elkaar opheffen, waardoor de reactantie zeer klein is. Aangezien de koperweerstand van de spoelen klein is, kan gesproken worden van een kortsluitsituatie. Voor gelijke stromen met dezelfde richting heeft de nulpunttransformator dus een verwaarloosbare impedantie. De kortsluitstroom is | on. The field direction is thus coupled. It turns out that in each leg of the yoke, the magnetic fields cancel each other out, resulting in very low reactance. Since the copper resistance of the coils is small, it can be considered a short-circuit situation. For equal currents in the same direction, the neutral point transformer therefore has negligible impedance. The short-circuit current is | in a medium voltage network, where a short circuit is created between phase C and the ground. The arrows along the windings indicate the direction of the current. I 0
3I | 3I | the coils is small, it can be considered a short-circuit situation. For equal currents in the same direction, the neutral point transformer therefore has negligible impedance. The short-circuit current is
0 | 0 | coils is small, it can be considered a short-circuit situation. For equal currents in the same direction, the neutral point transformer therefore has negligible impedance. The short-circuit current is 3I
. In elke fase vloeit 1/3 van de totale (homopolaire) kortsluitstroom, namelijk | . In each phase, 1/3 of the total (homopolar) short-circuit current flows, namely | is small, it can be considered a short-circuit situation. For equal currents in the same direction, the neutral point transformer therefore has negligible impedance. The short-circuit current is 3I 0
I | I | the same direction, the neutral point transformer therefore has negligible impedance. The short-circuit current is 3I 0 . In each phase, 1/3 of the total (homopolar) short-circuit current flows, namely
0 | 0 | same direction, the neutral point transformer therefore has negligible impedance. The short-circuit current is 3I 0 . In each phase, 1/3 of the total (homopolar) short-circuit current flows, namely I
. Aan de voedende zijde is zichtbaar hoe de stromen zich over de drie fasen verdelen, namelijk 1/3 van de kortsluitstroom over de ongestoorde fasen en 2/3 van de kortsluitstroom over de gestoorde fase. | On the supply side, it is visible how the currents are distributed over the three phases, namely 1/3 of the short-circuit current over the undisturbed phases and 2/3 of the short-circuit current over the disturbed phase. | direction, the neutral point transformer therefore has negligible impedance. The short-circuit current is 3I 0 . In each phase, 1/3 of the total (homopolar) short-circuit current flows, namely I 0
Figuur 8.16 Werking van een ideale aardings- of nulpuntstransformator in een LS-net | Figure 8.16 Operation of an ideal grounding or neutral point transformer in an LV network | visible how the currents are distributed over the three phases, namely 1/3 of the short-circuit current over the undisturbed phases and 2/3 of the short-circuit current over the disturbed phase.
Figuur 8.16 toont de situatie van een nulpuntstransformator bij een asymmetrische belasting in een LS-net. In het net is tussen fase L3 en de nulgeleider een eenfasebelasting aangebracht, waardoor een stroom ter grootte | Figure 8.16 shows the situation of a neutral point transformer under an asymmetric load in an LV network. In the network, a single-phase load is connected between phase L3 and the neutral conductor, resulting in a current of | current over the undisturbed phases and 2/3 of the short-circuit current over the disturbed phase. Figure 8.16 Operation of an ideal grounding or neutral point transformer in an LV network
I | I | point transformer under an asymmetric load in an LV network. In the network, a single-phase load is connected between phase L3 and the neutral conductor, resulting in a current of
loopt. Zonder de nulpunttransformator zou de retourstroom via de nulgeleider lopen. Door toepassing van de nulpunttransformator loopt in het ideale geval één derde van de retourstroom door ieder van de wikkelingen, waardoor aan de voedende kant geen stroom meer door de nulgeleider vloeit. Daardoor zorgt de nulpunttransformator voor een betere verdeling van de stromen door de fasegeleiders: 1/3 door de onbelaste fasegeleiders en 2/3 door de belaste fasegeleider. In de praktijk is de nulpunttransformator niet ideaal, maar heeft deze een zekere impedantie, waardoor niet alle retourstroom door de transformator uit de nulgeleider wordt weggenomen. | flows. Without the neutral point transformer, the return current would flow through the neutral conductor. By using the neutral point transformer, ideally, one-third of the return current flows through each of the windings, resulting in no current flowing through the neutral conductor on the supply side. This ensures a better distribution of currents through the phase conductors: 1/3 through the unloaded phase conductors and 2/3 through the loaded phase conductor. In practice, the neutral point transformer is not ideal and has a certain impedance, which means not all the return current is removed from the neutral conductor by the transformer. | transformer under an asymmetric load in an LV network. In the network, a single-phase load is connected between phase L3 and the neutral conductor, resulting in a current of I
De nulpunttransformator heeft geen invloed op het normale en het inverse componentsysteem en heeft in die systemen dus geen vervangingsschema. Het vervagingsschema in het homopolaire systeem is gegeven in tabel 8.10. Hierin zijn de homopolaire impedantie van de aardingstransformator en de externe sterpuntsimpedantie Z | The neutral point transformer has no effect on the normal and inverse component systems and therefore has no equivalent circuit in those systems. The equivalent circuit in the homopolar system is given in Table 8.10. This includes the homopolar impedance of the grounding transformer and the external neutral point impedance Z. | In practice, the neutral point transformer is not ideal and has a certain impedance, which means not all the return current is removed from the neutral conductor by the transformer.
e | e | those systems. The equivalent circuit in the homopolar system is given in Table 8.10. This includes the homopolar impedance of the grounding transformer and the external neutral point impedance Z.
weergegeven. | shown. | systems. The equivalent circuit in the homopolar system is given in Table 8.10. This includes the homopolar impedance of the grounding transformer and the external neutral point impedance Z. e
Tabel 8.10 Homopolaire vervangingsschema's voor een aardings- of nulpunttransformator | Table 8.10 Homopolar equivalent circuits for a grounding or neutral point transformer | The equivalent circuit in the homopolar system is given in Table 8.10. This includes the homopolar impedance of the grounding transformer and the external neutral point impedance Z. e shown.
Configuratie | Configuratie | This includes the homopolar impedance of the grounding transformer and the external neutral point impedance Z. e shown. Table 8.10 Homopolar equivalent circuits for a grounding or neutral point transformer
Schakeling | Schakeling | includes the homopolar impedance of the grounding transformer and the external neutral point impedance Z. e shown. Table 8.10 Homopolar equivalent circuits for a grounding or neutral point transformer Configuratie
Homopolair vervangingsschema | Homopolar equivalent circuit | the homopolar impedance of the grounding transformer and the external neutral point impedance Z. e shown. Table 8.10 Homopolar equivalent circuits for a grounding or neutral point transformer Configuratie Schakeling
ZN | ZN | of the grounding transformer and the external neutral point impedance Z. e shown. Table 8.10 Homopolar equivalent circuits for a grounding or neutral point transformer Configuratie Schakeling Homopolar equivalent circuit
Van een aardings- of nulpunttransformator wordt de homopolaire impedantie op dezelfde wijze gemeten als bij een kabel, zoals beschreven in paragraaf 8.2.7. Bij de meting worden de drie fasen van de transformator met elkaar verbonden. Over de drie aansluitingen en de nul wordt een spanningsbron met spanning | The homopolar impedance of a grounding or neutral point transformer is measured in the same way as for a cable, as described in paragraph 8.2.7. During the measurement, the three phases of the transformer are connected to each other. A voltage source with voltage is applied across the three terminals and the neutral. | the grounding transformer and the external neutral point impedance Z. e shown. Table 8.10 Homopolar equivalent circuits for a grounding or neutral point transformer Configuratie Schakeling Homopolar equivalent circuit ZN
U | U | paragraph 8.2.7. During the measurement, the three phases of the transformer are connected to each other. A voltage source with voltage is applied across the three terminals and the neutral.
0 | 0 | 8.2.7. During the measurement, the three phases of the transformer are connected to each other. A voltage source with voltage is applied across the three terminals and the neutral. U
aangesloten. De gemeten stroom vanuit de voeding is volgens figuur 8.1 gelijk aan | connected. The measured current from the power supply is, according to figure 8.1, equal to | During the measurement, the three phases of the transformer are connected to each other. A voltage source with voltage is applied across the three terminals and the neutral. U 0
I | I | voltage source with voltage is applied across the three terminals and the neutral. U 0 connected. The measured current from the power supply is, according to figure 8.1, equal to
M | M | source with voltage is applied across the three terminals and the neutral. U 0 connected. The measured current from the power supply is, according to figure 8.1, equal to I
en deze vertakt zich in drie stromen van | and this branches into three currents of | with voltage is applied across the three terminals and the neutral. U 0 connected. The measured current from the power supply is, according to figure 8.1, equal to I M
I | I | terminals and the neutral. U 0 connected. The measured current from the power supply is, according to figure 8.1, equal to I M and this branches into three currents of
0 | 0 | and the neutral. U 0 connected. The measured current from the power supply is, according to figure 8.1, equal to I M and this branches into three currents of I
die door ieder van de fasen vloeit. De homopolaire impedantie van de nulpunttransformator is dan: | that flows through each of the phases. The homopolar impedance of the neutral point transformer is then: | the neutral. U 0 connected. The measured current from the power supply is, according to figure 8.1, equal to I M and this branches into three currents of I 0
[ | [ | equal to I M and this branches into three currents of I 0 that flows through each of the phases. The homopolar impedance of the neutral point transformer is then:
8.60 | 8.60 | to I M and this branches into three currents of I 0 that flows through each of the phases. The homopolar impedance of the neutral point transformer is then: [
] | ] | I M and this branches into three currents of I 0 that flows through each of the phases. The homopolar impedance of the neutral point transformer is then: [ 8.60
De eventueel aanwezige aardingsimpedantie | The possibly present grounding impedance | M and this branches into three currents of I 0 that flows through each of the phases. The homopolar impedance of the neutral point transformer is then: [ 8.60 ]
Z | Z | three currents of I 0 that flows through each of the phases. The homopolar impedance of the neutral point transformer is then: [ 8.60 ] The possibly present grounding impedance
sterpunt | sterpunt | currents of I 0 that flows through each of the phases. The homopolar impedance of the neutral point transformer is then: [ 8.60 ] The possibly present grounding impedance Z
staat in serie met de transformator en moet voor de berekeningen met 3 vermenigvuldigd bij de homopolaire transformatorimpedantie worden opgeteld: | is in series with the transformer and must be multiplied by 3 for the calculations and added to the homopolar transformer impedance: | of I 0 that flows through each of the phases. The homopolar impedance of the neutral point transformer is then: [ 8.60 ] The possibly present grounding impedance Z sterpunt
[ | [ | ] The possibly present grounding impedance Z sterpunt is in series with the transformer and must be multiplied by 3 for the calculations and added to the homopolar transformer impedance:
8.61 | 8.61 | The possibly present grounding impedance Z sterpunt is in series with the transformer and must be multiplied by 3 for the calculations and added to the homopolar transformer impedance: [
] | ] | possibly present grounding impedance Z sterpunt is in series with the transformer and must be multiplied by 3 for the calculations and added to the homopolar transformer impedance: [ 8.61
Een nulpunttransformator in een LS-net wordt soms gecombineerd met een spanningsregeling, die is aangesloten op een aantal aftakkingen van de wikkelingen. | A neutral point transformer in an LV network is sometimes combined with a voltage regulator, which is connected to several taps of the windings. | present grounding impedance Z sterpunt is in series with the transformer and must be multiplied by 3 for the calculations and added to the homopolar transformer impedance: [ 8.61 ]
8.5 Smoorspoelen | 8.5 Chokes | homopolar transformer impedance: [ 8.61 ] A neutral point transformer in an LV network is sometimes combined with a voltage regulator, which is connected to several taps of the windings.
In MS-distributienetten worden smoorspoelen toegepast om de kortsluitstromen te beperken. Ze worden in het voedingsstation geplaatst aan het begin van de middenspanningsstreng, vlak na de vermogenschakelaar. Door de impedantie van de smoorspoel wordt de streng, elektrisch gezien, verlengd en daarmee het kortsluitvermogen achter de smoorspoel gereduceerd. Hierdoor blijft de schade ten gevolge van kortsluitstromen beperkt. | In MV distribution networks, chokes are used to limit short-circuit currents. They are placed in the substation at the beginning of the medium-voltage line, right after the circuit breaker. Due to the impedance of the choke, the line is electrically extended, thereby reducing the short-circuit power behind the choke. This limits the damage caused by short-circuit currents. | impedance: [ 8.61 ] A neutral point transformer in an LV network is sometimes combined with a voltage regulator, which is connected to several taps of the windings. 8.5 Chokes
De smoorspoel is ontworpen voor een specifieke nominale stroom en een impedantie. Vaak zijn niet de nominale stroom en de impedantie gegeven, maar het nominale vermogen, de relatieve kortsluitspanning en het kortsluitvermogen. Onderstaande vergelijkingen geven aan hoe deze parameters in elkaar kunnen worden omgerekend. | The choke is designed for a specific nominal current and impedance. Often, the nominal current and impedance are not provided, but rather the nominal power, the relative short-circuit voltage, and the short-circuit power. The following equations indicate how these parameters can be converted into each other. | circuit breaker. Due to the impedance of the choke, the line is electrically extended, thereby reducing the short-circuit power behind the choke. This limits the damage caused by short-circuit currents.
[ | [ | impedance are not provided, but rather the nominal power, the relative short-circuit voltage, and the short-circuit power. The following equations indicate how these parameters can be converted into each other.
8.62 | 8.62 | are not provided, but rather the nominal power, the relative short-circuit voltage, and the short-circuit power. The following equations indicate how these parameters can be converted into each other. [
] | ] | not provided, but rather the nominal power, the relative short-circuit voltage, and the short-circuit power. The following equations indicate how these parameters can be converted into each other. [ 8.62
Meestal is de weerstand veel kleiner dan de reactantie. Voor een smoorspoel van | Usually, the resistance is much smaller than the reactance. For a choke coil of | provided, but rather the nominal power, the relative short-circuit voltage, and the short-circuit power. The following equations indicate how these parameters can be converted into each other. [ 8.62 ]
U | U | The following equations indicate how these parameters can be converted into each other. [ 8.62 ] Usually, the resistance is much smaller than the reactance. For a choke coil of
S,nom | S,nom | following equations indicate how these parameters can be converted into each other. [ 8.62 ] Usually, the resistance is much smaller than the reactance. For a choke coil of U
equations indicate how these parameters can be converted into each other. [ 8.62 ] Usually, the resistance is much smaller than the reactance. For a choke coil of U S,nom
geldt bij voorbeeld: | applies, for example: | these parameters can be converted into each other. [ 8.62 ] Usually, the resistance is much smaller than the reactance. For a choke coil of U S,nom = 10 kV
S | S | be converted into each other. [ 8.62 ] Usually, the resistance is much smaller than the reactance. For a choke coil of U S,nom = 10 kV applies, for example:
S,nom | S,nom | converted into each other. [ 8.62 ] Usually, the resistance is much smaller than the reactance. For a choke coil of U S,nom = 10 kV applies, for example: S
into each other. [ 8.62 ] Usually, the resistance is much smaller than the reactance. For a choke coil of U S,nom = 10 kV applies, for example: S S,nom
u | u | [ 8.62 ] Usually, the resistance is much smaller than the reactance. For a choke coil of U S,nom = 10 kV applies, for example: S S,nom = 5.8 MVA
k | k | 8.62 ] Usually, the resistance is much smaller than the reactance. For a choke coil of U S,nom = 10 kV applies, for example: S S,nom = 5.8 MVA u
] Usually, the resistance is much smaller than the reactance. For a choke coil of U S,nom = 10 kV applies, for example: S S,nom = 5.8 MVA u k
P | P | the resistance is much smaller than the reactance. For a choke coil of U S,nom = 10 kV applies, for example: S S,nom = 5.8 MVA u k = 1.74%
k | k | resistance is much smaller than the reactance. For a choke coil of U S,nom = 10 kV applies, for example: S S,nom = 5.8 MVA u k = 1.74% P
is much smaller than the reactance. For a choke coil of U S,nom = 10 kV applies, for example: S S,nom = 5.8 MVA u k = 1.74% P k
Dit komt overeen met: | This corresponds to: | than the reactance. For a choke coil of U S,nom = 10 kV applies, for example: S S,nom = 5.8 MVA u k = 1.74% P k = 2.69 kW
I | I | For a choke coil of U S,nom = 10 kV applies, for example: S S,nom = 5.8 MVA u k = 1.74% P k = 2.69 kW This corresponds to:
nom | nom | a choke coil of U S,nom = 10 kV applies, for example: S S,nom = 5.8 MVA u k = 1.74% P k = 2.69 kW This corresponds to: I
choke coil of U S,nom = 10 kV applies, for example: S S,nom = 5.8 MVA u k = 1.74% P k = 2.69 kW This corresponds to: I nom
R | R | U S,nom = 10 kV applies, for example: S S,nom = 5.8 MVA u k = 1.74% P k = 2.69 kW This corresponds to: I nom = 335 A
S | S | S,nom = 10 kV applies, for example: S S,nom = 5.8 MVA u k = 1.74% P k = 2.69 kW This corresponds to: I nom = 335 A R
X | X | applies, for example: S S,nom = 5.8 MVA u k = 1.74% P k = 2.69 kW This corresponds to: I nom = 335 A R S = 0.008 Ω
S | S | for example: S S,nom = 5.8 MVA u k = 1.74% P k = 2.69 kW This corresponds to: I nom = 335 A R S = 0.008 Ω X
example: S S,nom = 5.8 MVA u k = 1.74% P k = 2.69 kW This corresponds to: I nom = 335 A R S = 0.008 Ω X S
Van een smoorspoel wordt vaak aangenomen dat de homopolaire impedantie en de inverse impedantie gelijk zijn aan de normale impedantie: | It is often assumed that for a choke coil, the homopolar impedance and the inverse impedance are equal to the normal impedance:
Z | Z
S,0 | S,0 | 0.008 Ω X S = 0.3 Ω It is often assumed that for a choke coil, the homopolar impedance and the inverse impedance are equal to the normal impedance: Z
≈ Z | ≈ Z | Ω X S = 0.3 Ω It is often assumed that for a choke coil, the homopolar impedance and the inverse impedance are equal to the normal impedance: Z S,0
S | S | S = 0.3 Ω It is often assumed that for a choke coil, the homopolar impedance and the inverse impedance are equal to the normal impedance: Z S,0 ≈ Z
Z | Z
S,2 | S,2 | 0.3 Ω It is often assumed that for a choke coil, the homopolar impedance and the inverse impedance are equal to the normal impedance: Z S,0 ≈ Z S Z
≈ Z | ≈ Z | Ω It is often assumed that for a choke coil, the homopolar impedance and the inverse impedance are equal to the normal impedance: Z S,0 ≈ Z S Z S,2
S | S | is often assumed that for a choke coil, the homopolar impedance and the inverse impedance are equal to the normal impedance: Z S,0 ≈ Z S Z S,2 ≈ Z
8.6 Belasting | 8.6 Load | often assumed that for a choke coil, the homopolar impedance and the inverse impedance are equal to the normal impedance: Z S,0 ≈ Z S Z S,2 ≈ Z S
De belasting in een elektriciteitsnet is de som van stromen die worden opgenomen door een niet nader gespecificeerde mix van apparaten van diverse aard, zoals motoren, verlichting en vermogenselektronica. In de industrie bestaat de belasting voornamelijk uit motoren. In een woonwijk bestaat deze voornamelijk uit verlichting en in mindere mate uit motoren en elektronische apparaten. Op landelijke schaal wordt de belasting gevormd door industrienetten en distributienetten. Het moge duidelijk zijn dat de belasting niet bestaat. Als een belasting niet hoeft te worden opgesplitst in specifieke soorten, kan worden volstaan met een algemene geaggregeerde belasting. | The load in an electrical grid is the sum of currents drawn by an unspecified mix of devices of various kinds, such as motors, lighting, and power electronics. In industry, the load mainly consists of motors. In a residential area, it mainly consists of lighting and, to a lesser extent, motors and electronic devices. On a national scale, the load is formed by industrial networks and distribution networks. It should be clear that the load does not exist. If a load does not need to be broken down into specific types, a general aggregated load will suffice. | that for a choke coil, the homopolar impedance and the inverse impedance are equal to the normal impedance: Z S,0 ≈ Z S Z S,2 ≈ Z S 8.6 Load
De belasting wordt gespecificeerd met het opgenomen driefasig vermogen of de opgenomen stroom en de arbeidsfactor. Beide kunnen in elkaar worden omgerekend. Voor het driefasige vermogen geldt: | The load is specified by the absorbed three-phase power or the absorbed current and the power factor. Both can be converted into each other. For the three-phase power, the following applies: | networks. It should be clear that the load does not exist. If a load does not need to be broken down into specific types, a general aggregated load will suffice.
[ | [ | load is specified by the absorbed three-phase power or the absorbed current and the power factor. Both can be converted into each other. For the three-phase power, the following applies:
8.63 | 8.63 | is specified by the absorbed three-phase power or the absorbed current and the power factor. Both can be converted into each other. For the three-phase power, the following applies: [
] | ] | specified by the absorbed three-phase power or the absorbed current and the power factor. Both can be converted into each other. For the three-phase power, the following applies: [ 8.63
Waarin: | Where: | by the absorbed three-phase power or the absorbed current and the power factor. Both can be converted into each other. For the three-phase power, the following applies: [ 8.63 ]
S | S | the absorbed three-phase power or the absorbed current and the power factor. Both can be converted into each other. For the three-phase power, the following applies: [ 8.63 ] Where:
driefasig complex vermogen | three-phase complex power | absorbed three-phase power or the absorbed current and the power factor. Both can be converted into each other. For the three-phase power, the following applies: [ 8.63 ] Where: S
P | P | or the absorbed current and the power factor. Both can be converted into each other. For the three-phase power, the following applies: [ 8.63 ] Where: S three-phase complex power
driefasig actief vermogen | three-phase active power | the absorbed current and the power factor. Both can be converted into each other. For the three-phase power, the following applies: [ 8.63 ] Where: S three-phase complex power P
Q | Q | and the power factor. Both can be converted into each other. For the three-phase power, the following applies: [ 8.63 ] Where: S three-phase complex power P three-phase active power
driefasig blindvermogen | three-phase reactive power | the power factor. Both can be converted into each other. For the three-phase power, the following applies: [ 8.63 ] Where: S three-phase complex power P three-phase active power Q
U | U | Both can be converted into each other. For the three-phase power, the following applies: [ 8.63 ] Where: S three-phase complex power P three-phase active power Q three-phase reactive power
gekoppelde spanning | line-to-line voltage | can be converted into each other. For the three-phase power, the following applies: [ 8.63 ] Where: S three-phase complex power P three-phase active power Q three-phase reactive power U
I | I | converted into each other. For the three-phase power, the following applies: [ 8.63 ] Where: S three-phase complex power P three-phase active power Q three-phase reactive power U line-to-line voltage
fasestroom | fasestroom | into each other. For the three-phase power, the following applies: [ 8.63 ] Where: S three-phase complex power P three-phase active power Q three-phase reactive power U line-to-line voltage I
cos(φ) | cos(φ) | each other. For the three-phase power, the following applies: [ 8.63 ] Where: S three-phase complex power P three-phase active power Q three-phase reactive power U line-to-line voltage I fasestroom
arbeidsfactor | arbeidsfactor | other. For the three-phase power, the following applies: [ 8.63 ] Where: S three-phase complex power P three-phase active power Q three-phase reactive power U line-to-line voltage I fasestroom cos(φ)
Door gebruik te maken van de wet van Ohm kan de belasting ook worden uitgedrukt als functie van de spanning en de belastingsimpedantie | By using Ohm's law, the load can also be expressed as a function of the voltage and the load impedance. | For the three-phase power, the following applies: [ 8.63 ] Where: S three-phase complex power P three-phase active power Q three-phase reactive power U line-to-line voltage I fasestroom cos(φ) arbeidsfactor
Z | Z | three-phase reactive power U line-to-line voltage I fasestroom cos(φ) arbeidsfactor By using Ohm's law, the load can also be expressed as a function of the voltage and the load impedance.
: | : | reactive power U line-to-line voltage I fasestroom cos(φ) arbeidsfactor By using Ohm's law, the load can also be expressed as a function of the voltage and the load impedance. Z
[ | [ | power U line-to-line voltage I fasestroom cos(φ) arbeidsfactor By using Ohm's law, the load can also be expressed as a function of the voltage and the load impedance. Z :
8.64 | 8.64 | U line-to-line voltage I fasestroom cos(φ) arbeidsfactor By using Ohm's law, the load can also be expressed as a function of the voltage and the load impedance. Z : [
] | ] | line-to-line voltage I fasestroom cos(φ) arbeidsfactor By using Ohm's law, the load can also be expressed as a function of the voltage and the load impedance. Z : [ 8.64
Bovenstaande formules tonen aan dat de belasting niet altijd constant is, maar afhangt van de spanning. Het belastingsmodel wordt gekozen naar gelang het spanningsafhankelijke gedrag. Indien de belasting voorgesteld wordt door een constante impedantie, hangt de actuele waarde van de opgenomen belasting af van het kwadraat van de spanning. In dat geval neemt de opgenomen stroom lineair toe met toenemende spanning. Indien de belasting wordt voorgesteld door een constante opgenomen stroom, is de actuele waarde van de opgenomen belasting lineair evenredig met de spanning. Het is ook mogelijk de belasting te modelleren met een constant opgenomen vermogen. In dat geval neemt de opgenomen stroom omgekeerd evenredig af bij een toenemende spanning. | The above formulas show that the load is not always constant but depends on the voltage. The load model is chosen according to the voltage-dependent behavior. If the load is represented by a constant impedance, the actual value of the absorbed load depends on the square of the voltage. In that case, the absorbed current increases linearly with increasing voltage. If the load is represented by a constant absorbed current, the actual value of the absorbed load is linearly proportional to the voltage. It is also possible to model the load with a constant absorbed power. In that case, the absorbed current decreases inversely with increasing voltage. | voltage I fasestroom cos(φ) arbeidsfactor By using Ohm's law, the load can also be expressed as a function of the voltage and the load impedance. Z : [ 8.64 ]
Het gedrag van de belasting ten aanzien van veranderingen van de spanning wordt bepaald door de mix van apparaten, die ermee gerepresenteerd wordt. Met name het verschil van spanningsniveau is bepalend voor de mix van apparaten en daarmee voor het spanningsafhankelijke gedrag. Tabel 8.11 geeft een overzicht van het spanningsafhankelijke gedrag van diverse belastingsoorten, waarbij de belasting samengesteld wordt met een mix van constant vermogen en constante impedantie (Kundur, 1994). Hierbij kan een apparaat zich als volgt gedragen: | The behavior of the load with respect to changes in voltage is determined by the mix of devices it represents. Specifically, the difference in voltage level is crucial for the mix of devices and thus for the voltage-dependent behavior. Table 8.11 provides an overview of the voltage-dependent behavior of various types of loads, where the load is composed of a mix of constant power and constant impedance (Kundur, 1994). In this context, a device can behave as follows: | is linearly proportional to the voltage. It is also possible to model the load with a constant absorbed power. In that case, the absorbed current decreases inversely with increasing voltage.
de impedantie is constant, zoals bij een gloeilamp; | the impedance is constant, as with an incandescent lamp; | of various types of loads, where the load is composed of a mix of constant power and constant impedance (Kundur, 1994). In this context, a device can behave as follows:
de opgenomen stroom is constant, zoals bij een vermogenselektronisch apparaat; | the current drawn is constant, as with a power electronic device; | composed of a mix of constant power and constant impedance (Kundur, 1994). In this context, a device can behave as follows: the impedance is constant, as with an incandescent lamp;
het opgenomen vermogen is constant, zoals bij een motor. | the power consumption is constant, as with a motor. | 1994). In this context, a device can behave as follows: the impedance is constant, as with an incandescent lamp; the current drawn is constant, as with a power electronic device;
Tabel 8.11 Belastingsgedrag | Table 8.11 Load Behavior | follows: the impedance is constant, as with an incandescent lamp; the current drawn is constant, as with a power electronic device; the power consumption is constant, as with a motor.
Type belasting | Type of load | constant, as with an incandescent lamp; the current drawn is constant, as with a power electronic device; the power consumption is constant, as with a motor. Table 8.11 Load Behavior
Arbeidsfactor | Arbeidsfactor | an incandescent lamp; the current drawn is constant, as with a power electronic device; the power consumption is constant, as with a motor. Table 8.11 Load Behavior Type of load
Aandeel constant | Constant share | incandescent lamp; the current drawn is constant, as with a power electronic device; the power consumption is constant, as with a motor. Table 8.11 Load Behavior Type of load Arbeidsfactor
vermogen (%) | power (%) | the current drawn is constant, as with a power electronic device; the power consumption is constant, as with a motor. Table 8.11 Load Behavior Type of load Arbeidsfactor Constant share
Aandeel constante | Constant share | drawn is constant, as with a power electronic device; the power consumption is constant, as with a motor. Table 8.11 Load Behavior Type of load Arbeidsfactor Constant share power (%)
impedantie (%) | impedance (%) | constant, as with a power electronic device; the power consumption is constant, as with a motor. Table 8.11 Load Behavior Type of load Arbeidsfactor Constant share power (%) Constant share
P | P | with a power electronic device; the power consumption is constant, as with a motor. Table 8.11 Load Behavior Type of load Arbeidsfactor Constant share power (%) Constant share impedance (%)
constant | constant | a power electronic device; the power consumption is constant, as with a motor. Table 8.11 Load Behavior Type of load Arbeidsfactor Constant share power (%) Constant share impedance (%) P
Q | Q | power electronic device; the power consumption is constant, as with a motor. Table 8.11 Load Behavior Type of load Arbeidsfactor Constant share power (%) Constant share impedance (%) P constant
constant | constant | electronic device; the power consumption is constant, as with a motor. Table 8.11 Load Behavior Type of load Arbeidsfactor Constant share power (%) Constant share impedance (%) P constant Q
P | P | device; the power consumption is constant, as with a motor. Table 8.11 Load Behavior Type of load Arbeidsfactor Constant share power (%) Constant share impedance (%) P constant Q constant
impedantie,nom | impedance, nominal | the power consumption is constant, as with a motor. Table 8.11 Load Behavior Type of load Arbeidsfactor Constant share power (%) Constant share impedance (%) P constant Q constant P
Q | Q | consumption is constant, as with a motor. Table 8.11 Load Behavior Type of load Arbeidsfactor Constant share power (%) Constant share impedance (%) P constant Q constant P impedance, nominal
impedantie,nom | impedance, nominal | is constant, as with a motor. Table 8.11 Load Behavior Type of load Arbeidsfactor Constant share power (%) Constant share impedance (%) P constant Q constant P impedance, nominal Q
Industrieel | Industrieel | as with a motor. Table 8.11 Load Behavior Type of load Arbeidsfactor Constant share power (%) Constant share impedance (%) P constant Q constant P impedance, nominal Q impedance, nominal
0,85 | 0.85 | with a motor. Table 8.11 Load Behavior Type of load Arbeidsfactor Constant share power (%) Constant share impedance (%) P constant Q constant P impedance, nominal Q impedance, nominal Industrieel
90 | 90 | a motor. Table 8.11 Load Behavior Type of load Arbeidsfactor Constant share power (%) Constant share impedance (%) P constant Q constant P impedance, nominal Q impedance, nominal Industrieel 0.85
0 | 0 | motor. Table 8.11 Load Behavior Type of load Arbeidsfactor Constant share power (%) Constant share impedance (%) P constant Q constant P impedance, nominal Q impedance, nominal Industrieel 0.85 90
10 | 10 | Table 8.11 Load Behavior Type of load Arbeidsfactor Constant share power (%) Constant share impedance (%) P constant Q constant P impedance, nominal Q impedance, nominal Industrieel 0.85 90 0
100 | 100 | 8.11 Load Behavior Type of load Arbeidsfactor Constant share power (%) Constant share impedance (%) P constant Q constant P impedance, nominal Q impedance, nominal Industrieel 0.85 90 0 10
Zakelijk | Zakelijk | Load Behavior Type of load Arbeidsfactor Constant share power (%) Constant share impedance (%) P constant Q constant P impedance, nominal Q impedance, nominal Industrieel 0.85 90 0 10 100
0,90 | 0.90 | Behavior Type of load Arbeidsfactor Constant share power (%) Constant share impedance (%) P constant Q constant P impedance, nominal Q impedance, nominal Industrieel 0.85 90 0 10 100 Zakelijk
35 | 35 | Type of load Arbeidsfactor Constant share power (%) Constant share impedance (%) P constant Q constant P impedance, nominal Q impedance, nominal Industrieel 0.85 90 0 10 100 Zakelijk 0.90
0 | 0 | of load Arbeidsfactor Constant share power (%) Constant share impedance (%) P constant Q constant P impedance, nominal Q impedance, nominal Industrieel 0.85 90 0 10 100 Zakelijk 0.90 35
65 | 65 | load Arbeidsfactor Constant share power (%) Constant share impedance (%) P constant Q constant P impedance, nominal Q impedance, nominal Industrieel 0.85 90 0 10 100 Zakelijk 0.90 35 0
100 | 100 | Arbeidsfactor Constant share power (%) Constant share impedance (%) P constant Q constant P impedance, nominal Q impedance, nominal Industrieel 0.85 90 0 10 100 Zakelijk 0.90 35 0 65
Woningen | Woningen | Constant share power (%) Constant share impedance (%) P constant Q constant P impedance, nominal Q impedance, nominal Industrieel 0.85 90 0 10 100 Zakelijk 0.90 35 0 65 100
0,95 | 0.95 | share power (%) Constant share impedance (%) P constant Q constant P impedance, nominal Q impedance, nominal Industrieel 0.85 90 0 10 100 Zakelijk 0.90 35 0 65 100 Woningen
30 | 30 | power (%) Constant share impedance (%) P constant Q constant P impedance, nominal Q impedance, nominal Industrieel 0.85 90 0 10 100 Zakelijk 0.90 35 0 65 100 Woningen 0.95
0 | 0 | (%) Constant share impedance (%) P constant Q constant P impedance, nominal Q impedance, nominal Industrieel 0.85 90 0 10 100 Zakelijk 0.90 35 0 65 100 Woningen 0.95 30
70 | 70 | Constant share impedance (%) P constant Q constant P impedance, nominal Q impedance, nominal Industrieel 0.85 90 0 10 100 Zakelijk 0.90 35 0 65 100 Woningen 0.95 30 0
100 | 100 | share impedance (%) P constant Q constant P impedance, nominal Q impedance, nominal Industrieel 0.85 90 0 10 100 Zakelijk 0.90 35 0 65 100 Woningen 0.95 30 0 70
Verwarming | Verwarming | impedance (%) P constant Q constant P impedance, nominal Q impedance, nominal Industrieel 0.85 90 0 10 100 Zakelijk 0.90 35 0 65 100 Woningen 0.95 30 0 70 100
1,00 | 1.00 | (%) P constant Q constant P impedance, nominal Q impedance, nominal Industrieel 0.85 90 0 10 100 Zakelijk 0.90 35 0 65 100 Woningen 0.95 30 0 70 100 Verwarming
0 | 0 | P constant Q constant P impedance, nominal Q impedance, nominal Industrieel 0.85 90 0 10 100 Zakelijk 0.90 35 0 65 100 Woningen 0.95 30 0 70 100 Verwarming 1.00
0 | 0 | constant Q constant P impedance, nominal Q impedance, nominal Industrieel 0.85 90 0 10 100 Zakelijk 0.90 35 0 65 100 Woningen 0.95 30 0 70 100 Verwarming 1.00 0
100 | 100 | Q constant P impedance, nominal Q impedance, nominal Industrieel 0.85 90 0 10 100 Zakelijk 0.90 35 0 65 100 Woningen 0.95 30 0 70 100 Verwarming 1.00 0 0
100 | 100 | constant P impedance, nominal Q impedance, nominal Industrieel 0.85 90 0 10 100 Zakelijk 0.90 35 0 65 100 Woningen 0.95 30 0 70 100 Verwarming 1.00 0 0 100
Airconditioner | Airconditioner | P impedance, nominal Q impedance, nominal Industrieel 0.85 90 0 10 100 Zakelijk 0.90 35 0 65 100 Woningen 0.95 30 0 70 100 Verwarming 1.00 0 0 100 100
0,82 | 0.82 | impedance, nominal Q impedance, nominal Industrieel 0.85 90 0 10 100 Zakelijk 0.90 35 0 65 100 Woningen 0.95 30 0 70 100 Verwarming 1.00 0 0 100 100 Airconditioner
75 | 75 | nominal Q impedance, nominal Industrieel 0.85 90 0 10 100 Zakelijk 0.90 35 0 65 100 Woningen 0.95 30 0 70 100 Verwarming 1.00 0 0 100 100 Airconditioner 0.82
0 | 0 | Q impedance, nominal Industrieel 0.85 90 0 10 100 Zakelijk 0.90 35 0 65 100 Woningen 0.95 30 0 70 100 Verwarming 1.00 0 0 100 100 Airconditioner 0.82 75
25 | 25 | impedance, nominal Industrieel 0.85 90 0 10 100 Zakelijk 0.90 35 0 65 100 Woningen 0.95 30 0 70 100 Verwarming 1.00 0 0 100 100 Airconditioner 0.82 75 0
100 | 100 | nominal Industrieel 0.85 90 0 10 100 Zakelijk 0.90 35 0 65 100 Woningen 0.95 30 0 70 100 Verwarming 1.00 0 0 100 100 Airconditioner 0.82 75 0 25
Verlichting | Verlichting | Industrieel 0.85 90 0 10 100 Zakelijk 0.90 35 0 65 100 Woningen 0.95 30 0 70 100 Verwarming 1.00 0 0 100 100 Airconditioner 0.82 75 0 25 100
1,00 | 1.00 | 0.85 90 0 10 100 Zakelijk 0.90 35 0 65 100 Woningen 0.95 30 0 70 100 Verwarming 1.00 0 0 100 100 Airconditioner 0.82 75 0 25 100 Verlichting
25 | 25 | 90 0 10 100 Zakelijk 0.90 35 0 65 100 Woningen 0.95 30 0 70 100 Verwarming 1.00 0 0 100 100 Airconditioner 0.82 75 0 25 100 Verlichting 1.00
0 | 0 | 0 10 100 Zakelijk 0.90 35 0 65 100 Woningen 0.95 30 0 70 100 Verwarming 1.00 0 0 100 100 Airconditioner 0.82 75 0 25 100 Verlichting 1.00 25
75 | 75 | 10 100 Zakelijk 0.90 35 0 65 100 Woningen 0.95 30 0 70 100 Verwarming 1.00 0 0 100 100 Airconditioner 0.82 75 0 25 100 Verlichting 1.00 25 0
100 | 100 | 100 Zakelijk 0.90 35 0 65 100 Woningen 0.95 30 0 70 100 Verwarming 1.00 0 0 100 100 Airconditioner 0.82 75 0 25 100 Verlichting 1.00 25 0 75
Het correct modelleren van het spanningsafhankelijke gedrag is moeilijk omdat het spanningsafhankelijke gedrag van de individuele apparaten lang niet altijd goed bekend is. De exacte samenstelling van de mix van apparaatsoorten is moeilijk te schatten en bovendien seizoensafhankelijk. Soms worden in de literatuur getallen gegeven, maar deze kunnen van publicatie tot publicatie verschillen. | Accurately modeling the voltage-dependent behavior is challenging because the voltage-dependent behavior of individual devices is often not well known. The exact composition of the mix of device types is difficult to estimate and also varies seasonally. Sometimes figures are provided in the literature, but these can differ from one publication to another. | Zakelijk 0.90 35 0 65 100 Woningen 0.95 30 0 70 100 Verwarming 1.00 0 0 100 100 Airconditioner 0.82 75 0 25 100 Verlichting 1.00 25 0 75 100
In tabel 8.11 is de som van de constant vermogen- en constante impedantiedelen altijd 100% voor zowel het actieve vermogen als het blindvermogen. De actuele waarde van de belasting is in dit geval gelijk aan de som van het constante vermogensaandeel en het constante impedantie-aandeel, gecorrigeerd naar de actuele spanning: | In table 8.11, the sum of the constant power and constant impedance parts is always 100% for both active power and reactive power. The actual value of the load in this case is equal to the sum of the constant power share and the constant impedance share, adjusted to the actual voltage: | of the mix of device types is difficult to estimate and also varies seasonally. Sometimes figures are provided in the literature, but these can differ from one publication to another.
[ | [ | power. The actual value of the load in this case is equal to the sum of the constant power share and the constant impedance share, adjusted to the actual voltage:
8.65 | 8.65 | The actual value of the load in this case is equal to the sum of the constant power share and the constant impedance share, adjusted to the actual voltage: [
] | ] | actual value of the load in this case is equal to the sum of the constant power share and the constant impedance share, adjusted to the actual voltage: [ 8.65
De impedantie voor het constante impedantie-aandeel wordt berekend uit de nominale spanning: | The impedance for the constant impedance share is calculated from the nominal voltage: | value of the load in this case is equal to the sum of the constant power share and the constant impedance share, adjusted to the actual voltage: [ 8.65 ]
[ | [ | the constant power share and the constant impedance share, adjusted to the actual voltage: [ 8.65 ] The impedance for the constant impedance share is calculated from the nominal voltage:
8.66 | 8.66 | constant power share and the constant impedance share, adjusted to the actual voltage: [ 8.65 ] The impedance for the constant impedance share is calculated from the nominal voltage: [
] | ] | power share and the constant impedance share, adjusted to the actual voltage: [ 8.65 ] The impedance for the constant impedance share is calculated from the nominal voltage: [ 8.66
Figuur 8.17 illustreert de samenstelling van een belasting, uit een aandeel met constante impedantie en een aandeel met constant vermogen. Hierbij wordt de enkelfasige afbeelding van het driefasenstelsel gebruikt. | Figure 8.17 illustrates the composition of a load, consisting of a constant impedance share and a constant power share. Here, the single-phase representation of the three-phase system is used. | share and the constant impedance share, adjusted to the actual voltage: [ 8.65 ] The impedance for the constant impedance share is calculated from the nominal voltage: [ 8.66 ]
Figuur 8.17 Enkelfasige afbeelding van een driefasenbelasting met constante impedantie en constant vermogen | Figure 8.17 Single-phase representation of a three-phase load with constant impedance and constant power | ] Figure 8.17 illustrates the composition of a load, consisting of a constant impedance share and a constant power share. Here, the single-phase representation of the three-phase system is used.
In hoogspanningsnetten wordt in het algemeen model met 100% constant vermogen gebruikt voor alle belastingen, omdat die belastingen zich in werkelijkheid meestal achter geregelde transformatoren bevinden, die ervoor zorgen dat spanning op de belastingen binnen marges constant blijft. In distributienetten echter neigt het belastingsgedrag meer naar constante stroom en soms constante impedantie. | In high voltage networks, a model with 100% constant power is generally used for all loads, because these loads are usually located behind regulated transformers, which ensure that the voltage on the loads remains constant within margins. In distribution networks, however, the load behavior tends more towards constant current and sometimes constant impedance. | share and a constant power share. Here, the single-phase representation of the three-phase system is used. Figure 8.17 Single-phase representation of a three-phase load with constant impedance and constant power
De belasting doet niet mee aan kortsluitberekeningen volgens IEC 60909. Voor andere storingsanalyses kan de belasting wel gemodelleerd worden. Bij diverse storingsanalyses kan het voorkomen dat de spanning sterk daalt. In die gevallen is het niet wenselijk dat de belasting zich als een constante vermogensbelasting gedraagt. Voor dergelijke berekeningen wordt de belasting dan ook altijd omgerekend naar een equivalente constante impedantie-belasting. | The load is not included in short-circuit calculations according to IEC 60909. For other fault analyses, the load can be modeled. In various fault analyses, it can happen that the voltage drops significantly. In such cases, it is not desirable for the load to behave as a constant power load. For such calculations, the load is always converted to an equivalent constant impedance load. | regulated transformers, which ensure that the voltage on the loads remains constant within margins. In distribution networks, however, the load behavior tends more towards constant current and sometimes constant impedance.
8.7 Opwekking | 8.7 Generation | such cases, it is not desirable for the load to behave as a constant power load. For such calculations, the load is always converted to an equivalent constant impedance load.
Het is mogelijk een bepaalde hoeveelheid opgewekt vermogen te modelleren zonder de apparatuur nader te specificeren. Het vermogen kan opgewekt worden met een synchrone generator maar ook met een PV-installatie. In de loadflowberekening wordt dit dan gemodelleerd als een negatieve belasting. Het is gebruikelijk dat deze negatieve belasting gemodelleerd wordt met een constant vermogensgedrag. Dit soort opwekeenheden heeft meestal een zeer beperkte kortsluitbijdrage en wordt in de praktijk bij kortsluitingen meestal zeer snel van het net afgeschakeld. Op deze manier gemodelleerde opwekking doet daarom niet mee aan kortsluitberekeningen volgens IEC 60909. Voor andere storingsanalyses kan deze opwekking omgerekend worden naar een equivalente constante (negatieve) impedantiebelasting. | It is possible to model a certain amount of generated power without specifying the equipment in detail. The power can be generated with a synchronous generator or with a PV installation. In the load flow calculation, this is then modeled as a negative load. It is common for this negative load to be modeled with constant power behavior. This type of generation unit usually has a very limited short-circuit contribution and is typically quickly disconnected from the grid during short circuits. Therefore, generation modeled in this way does not participate in short-circuit calculations according to IEC 60909. For other fault analyses, this generation can be converted to an equivalent constant (negative) impedance load. | it is not desirable for the load to behave as a constant power load. For such calculations, the load is always converted to an equivalent constant impedance load. 8.7 Generation
8.8 Generatoren | 8.8 Generators | modeled in this way does not participate in short-circuit calculations according to IEC 60909. For other fault analyses, this generation can be converted to an equivalent constant (negative) impedance load.
Generatoren zijn uitgevoerd als synchrone of als asynchrone generator, maar het meest gebruikelijk is de synchrone generator. Deze is verkrijgbaar van kleine tot zeer grote vermogens. Een generator wordt aangedreven door een motor of door een turbine. Voor de kleinere vermogens tot enkele MW wordt meestal een op scheepsdiesels lijkende motor of een gasmotor gebruikt. De gasmotor-WKK wordt op grote schaal in de glastuinbouw toegepast. Voor de grotere vermogens, vanaf enkele tientallen MW, wordt de generator aangedreven door een gasturbine of, zoals in grote centrales, door stoomturbines. Het geleverde vermogen wordt door de motor of de turbine bepaald. Voor elektrotechnische berekeningen aan een productie-eenheid wordt ervan uitgegaan dat het mechanische vermogen constant is. Het geleverde elektrische vermogen is dan afhankelijk van het rendement, dat meestal wordt opgegeven in procent. Het gespecificeerde actieve vermogen van de productie-eenheid is meestal het elektrische vermogen in W. | Generators are designed as synchronous or asynchronous generators, but the most common is the synchronous generator. These are available in sizes ranging from small to very large capacities. A generator is driven by a motor or a turbine. For smaller capacities up to a few MW, a motor resembling marine diesels or a gas engine is usually used. The gas engine-CHP is widely used in greenhouse horticulture. For larger capacities, starting from a few tens of MW, the generator is driven by a gas turbine or, as in large power plants, by steam turbines. The delivered power is determined by the motor or the turbine. For electrical calculations on a production unit, it is assumed that the mechanical power is constant. The delivered electrical power then depends on the efficiency, which is usually specified as a percentage. The specified active power of the production unit is usually the electrical power in W. | this way does not participate in short-circuit calculations according to IEC 60909. For other fault analyses, this generation can be converted to an equivalent constant (negative) impedance load. 8.8 Generators
[ | [ | delivered electrical power then depends on the efficiency, which is usually specified as a percentage. The specified active power of the production unit is usually the electrical power in W.
8.67 | 8.67 | electrical power then depends on the efficiency, which is usually specified as a percentage. The specified active power of the production unit is usually the electrical power in W. [
] | ] | power then depends on the efficiency, which is usually specified as a percentage. The specified active power of the production unit is usually the electrical power in W. [ 8.67
Bij netberekeningen wordt de synchrone generator altijd gemodelleerd als een bron van constant actief elektrisch vermogen ( | In grid calculations, the synchronous generator is always modeled as a source of constant active electrical power. | then depends on the efficiency, which is usually specified as a percentage. The specified active power of the production unit is usually the electrical power in W. [ 8.67 ]
P | P | the production unit is usually the electrical power in W. [ 8.67 ] In grid calculations, the synchronous generator is always modeled as a source of constant active electrical power.
). Het blindvermogen ( | ). The reactive power ( | production unit is usually the electrical power in W. [ 8.67 ] In grid calculations, the synchronous generator is always modeled as a source of constant active electrical power. P
Q | Q | electrical power in W. [ 8.67 ] In grid calculations, the synchronous generator is always modeled as a source of constant active electrical power. P ). The reactive power (
), dat de generator kan leveren, is daar voor een groot deel onafhankelijk van. Er zijn diverse beperkingen, die volgen uit het vermogensdiagram van de generator. | ), which the generator can deliver, is largely independent of that. There are various limitations that follow from the power diagram of the generator. | power in W. [ 8.67 ] In grid calculations, the synchronous generator is always modeled as a source of constant active electrical power. P ). The reactive power ( Q
Figuur 8.18 Vermogensdiagram van de synchrone generator | Figure 8.18 Power diagram of the synchronous generator | ). The reactive power ( Q ), which the generator can deliver, is largely independent of that. There are various limitations that follow from the power diagram of the generator.
De beperkingen zijn hieronder toegelicht. | The limitations are explained below. | the generator can deliver, is largely independent of that. There are various limitations that follow from the power diagram of the generator. Figure 8.18 Power diagram of the synchronous generator
De beperking van het maximale aandrijfvermogen en van de mechanische belasting van de machine, die het maximale elektrische vermogen bepaalt. Deze is weergegeven met een horizontale lijn. | The limitation of the maximum drive power and the mechanical load of the machine, which determines the maximum electrical power. This is represented by a horizontal line. | largely independent of that. There are various limitations that follow from the power diagram of the generator. Figure 8.18 Power diagram of the synchronous generator The limitations are explained below.
De beperking van de maximale statorstroom, die wordt berekend uit het nominale vermogen en de nominale spanning. Deze beperking is weergegeven met een cirkelboog met een straal gelijk aan het nominale schijnbare vermogen | The limitation of the maximum stator current, which is calculated from the nominal power and the nominal voltage. This limitation is represented by an arc with a radius equal to the nominal apparent power. | are explained below. The limitation of the maximum drive power and the mechanical load of the machine, which determines the maximum electrical power. This is represented by a horizontal line.
S | S | maximum stator current, which is calculated from the nominal power and the nominal voltage. This limitation is represented by an arc with a radius equal to the nominal apparent power.
nom | nom | stator current, which is calculated from the nominal power and the nominal voltage. This limitation is represented by an arc with a radius equal to the nominal apparent power. S
. | . | current, which is calculated from the nominal power and the nominal voltage. This limitation is represented by an arc with a radius equal to the nominal apparent power. S nom
De beperking van de rotorstroom, die de bekrachtiging van de generator oplevert. Globaal genomen is het geproduceerde blindvermogen afhankelijk van de bekrachtiging. | The limitation of the rotor current, which results from the excitation of the generator. Generally speaking, the reactive power produced depends on the excitation. | which is calculated from the nominal power and the nominal voltage. This limitation is represented by an arc with a radius equal to the nominal apparent power. S nom .
De beperking van verlies aan stabiliteit. Bij een kleine rotorstroom neemt de generator blindvermogen op. Een kleine rotorstroom levert echter ook een minder sterke bekrachtiging op, waardoor het gevaar bestaat dat de synchrone generator niet meer synchroon met het net loopt. Als dat het geval is kan de generator zijn elektrisch vermogen niet meer kwijt en moet deze afgeschakeld worden. | The limitation of loss of stability. With a small rotor current, the generator absorbs reactive power. However, a small rotor current also results in weaker excitation, which poses the risk that the synchronous generator may no longer run in sync with the grid. If that happens, the generator can no longer deliver its electrical power and must be disconnected. | nominal apparent power. S nom . The limitation of the rotor current, which results from the excitation of the generator. Generally speaking, the reactive power produced depends on the excitation.
In de centrale wordt het vermogensdiagram gebruikt om de bedrijfsvoering van de generator te monitoren. Bij elektrotechnische berekeningen is het gebruikelijk om te volstaan met begrenzing door het maximum actieve vermogen | In the power plant, the power diagram is used to monitor the operation of the generator. In electrical engineering calculations, it is customary to limit by the maximum active power. | risk that the synchronous generator may no longer run in sync with the grid. If that happens, the generator can no longer deliver its electrical power and must be disconnected.
P | P | In the power plant, the power diagram is used to monitor the operation of the generator. In electrical engineering calculations, it is customary to limit by the maximum active power.
max | max | the power plant, the power diagram is used to monitor the operation of the generator. In electrical engineering calculations, it is customary to limit by the maximum active power. P
en het minimum en maximum blindvermogen | and the minimum and maximum reactive power | power plant, the power diagram is used to monitor the operation of the generator. In electrical engineering calculations, it is customary to limit by the maximum active power. P max
Q | Q | to monitor the operation of the generator. In electrical engineering calculations, it is customary to limit by the maximum active power. P max and the minimum and maximum reactive power
min | min | monitor the operation of the generator. In electrical engineering calculations, it is customary to limit by the maximum active power. P max and the minimum and maximum reactive power Q
en | en | the operation of the generator. In electrical engineering calculations, it is customary to limit by the maximum active power. P max and the minimum and maximum reactive power Q min
Q | Q | operation of the generator. In electrical engineering calculations, it is customary to limit by the maximum active power. P max and the minimum and maximum reactive power Q min en
max | max | of the generator. In electrical engineering calculations, it is customary to limit by the maximum active power. P max and the minimum and maximum reactive power Q min en Q
. Het geproduceerde blindvermogen is afhankelijk van de bekrachtiging, die wordt ingesteld door een automatische regeling. In de praktijk wordt de generator ingesteld op een vaste arbeidsfactor of op een spanningsregeling. | The produced reactive power depends on the excitation, which is set by an automatic control system. In practice, the generator is set to a fixed power factor or a voltage regulation. | the generator. In electrical engineering calculations, it is customary to limit by the maximum active power. P max and the minimum and maximum reactive power Q min en Q max
Vaste arbeidsfactor | Fixed power factor | produced reactive power depends on the excitation, which is set by an automatic control system. In practice, the generator is set to a fixed power factor or a voltage regulation.
Deze regelmogelijkheid wordt ook wel cos(φ)-regeling genoemd. De regeling zorgt ervoor dat het blindvermogen zodanig is dat de verhouding tussen actief en blindvermogen constant is. Voor gebruik in de loadflowberekeningen komt dit neer op een bron van constant actief vermogen | This control option is also known as cos(φ) control. The regulation ensures that the reactive power is such that the ratio between active and reactive power remains constant. For use in load flow calculations, this translates to a source of constant active power. | depends on the excitation, which is set by an automatic control system. In practice, the generator is set to a fixed power factor or a voltage regulation. Fixed power factor
P | P | the reactive power is such that the ratio between active and reactive power remains constant. For use in load flow calculations, this translates to a source of constant active power.
en blindvermogen | and reactive power | reactive power is such that the ratio between active and reactive power remains constant. For use in load flow calculations, this translates to a source of constant active power. P
Q | Q | such that the ratio between active and reactive power remains constant. For use in load flow calculations, this translates to a source of constant active power. P and reactive power
. Deze regelmogelijkheid wordt vaak gebruikt bij decentrale opwekking en in de industrie. | . This control option is often used in decentralized generation and in the industry. | that the ratio between active and reactive power remains constant. For use in load flow calculations, this translates to a source of constant active power. P and reactive power Q
Figuur 8.19 Spanningsregeling van de synchrone generator | Figure 8.19 Voltage regulation of the synchronous generator | flow calculations, this translates to a source of constant active power. P and reactive power Q . This control option is often used in decentralized generation and in the industry.
Spanningsregeling | Spanningsregeling | constant active power. P and reactive power Q . This control option is often used in decentralized generation and in the industry. Figure 8.19 Voltage regulation of the synchronous generator
Grotere productie-eenheden zijn vaak uitgerust met een spanningsregeling en zullen door het aanvullend leveren of reduceren van de afgegeven hoeveelheid blindvermogen ervoor zorgen dat de spanning in het net op een gewenst niveau gehouden wordt. In eilandbedrijf zullen ook de kleine generatoren met een spanningsregeling moeten worden uitgerust. De spanningsregeling regelt de bekrachtiging zodanig dat de spanning overeenkomt met een ingestelde waarde | Larger production units are often equipped with voltage regulation and will ensure that the voltage in the grid is maintained at a desired level by additionally supplying or reducing the amount of reactive power delivered. In island mode, small generators will also need to be equipped with voltage regulation. The voltage regulation adjusts the excitation in such a way that the voltage matches a set value. | active power. P and reactive power Q . This control option is often used in decentralized generation and in the industry. Figure 8.19 Voltage regulation of the synchronous generator Spanningsregeling
U | U | island mode, small generators will also need to be equipped with voltage regulation. The voltage regulation adjusts the excitation in such a way that the voltage matches a set value.
ref | ref | mode, small generators will also need to be equipped with voltage regulation. The voltage regulation adjusts the excitation in such a way that the voltage matches a set value. U
. In figuur 8.19 wordt dit weergegeven met het verschil | . In figure 8.19, this is illustrated with the difference | small generators will also need to be equipped with voltage regulation. The voltage regulation adjusts the excitation in such a way that the voltage matches a set value. U ref
, dat nul moet zijn. Als gevolg hiervan kan het geproduceerde blindvermogen alle waardes aannemen tussen het minimum en maximum blindvermogen | , which must be zero. As a result, the reactive power produced can take on any value between the minimum and maximum reactive power. | regulation. The voltage regulation adjusts the excitation in such a way that the voltage matches a set value. U ref . In figure 8.19, this is illustrated with the difference
Q | Q | this is illustrated with the difference , which must be zero. As a result, the reactive power produced can take on any value between the minimum and maximum reactive power.
min | min | is illustrated with the difference , which must be zero. As a result, the reactive power produced can take on any value between the minimum and maximum reactive power. Q
en | en | illustrated with the difference , which must be zero. As a result, the reactive power produced can take on any value between the minimum and maximum reactive power. Q min
Q | Q | with the difference , which must be zero. As a result, the reactive power produced can take on any value between the minimum and maximum reactive power. Q min en
max | max | the difference , which must be zero. As a result, the reactive power produced can take on any value between the minimum and maximum reactive power. Q min en Q
. | . | difference , which must be zero. As a result, the reactive power produced can take on any value between the minimum and maximum reactive power. Q min en Q max
Gedrag bij kortsluiting | Behavior during a short circuit | , which must be zero. As a result, the reactive power produced can take on any value between the minimum and maximum reactive power. Q min en Q max .
Een synchrone generator draagt bij aan de kortsluitstroom. De bijdrage wordt bepaald door de generator-impedantie. Van een synchrone generator zijn naast het nominale schijnbare vermogen ook de statorweerstand en de subtransiënte reactantie bekend. Deze weerstand en reactantie zijn meestal gegeven in per unit, genormeerd op de basisimpedantie van de generator zelf. De generator-impedantie wordt dan als volgt berekend: | A synchronous generator contributes to the short-circuit current. The contribution is determined by the generator impedance. For a synchronous generator, in addition to the nominal apparent power, the stator resistance and the subtransient reactance are also known. This resistance and reactance are usually given in per unit, normalized to the base impedance of the generator itself. The generator impedance is then calculated as follows: | As a result, the reactive power produced can take on any value between the minimum and maximum reactive power. Q min en Q max . Behavior during a short circuit
[ | [ | are also known. This resistance and reactance are usually given in per unit, normalized to the base impedance of the generator itself. The generator impedance is then calculated as follows:
8.68 | 8.68 | also known. This resistance and reactance are usually given in per unit, normalized to the base impedance of the generator itself. The generator impedance is then calculated as follows: [
] | ] | known. This resistance and reactance are usually given in per unit, normalized to the base impedance of the generator itself. The generator impedance is then calculated as follows: [ 8.68
met: | with: | This resistance and reactance are usually given in per unit, normalized to the base impedance of the generator itself. The generator impedance is then calculated as follows: [ 8.68 ]
r | r | resistance and reactance are usually given in per unit, normalized to the base impedance of the generator itself. The generator impedance is then calculated as follows: [ 8.68 ] with:
G | G | and reactance are usually given in per unit, normalized to the base impedance of the generator itself. The generator impedance is then calculated as follows: [ 8.68 ] with: r
statorweerstand (pu) | stator resistance (pu) | reactance are usually given in per unit, normalized to the base impedance of the generator itself. The generator impedance is then calculated as follows: [ 8.68 ] with: r G
x | x | given in per unit, normalized to the base impedance of the generator itself. The generator impedance is then calculated as follows: [ 8.68 ] with: r G stator resistance (pu)
d | d | in per unit, normalized to the base impedance of the generator itself. The generator impedance is then calculated as follows: [ 8.68 ] with: r G stator resistance (pu) x
" | " | per unit, normalized to the base impedance of the generator itself. The generator impedance is then calculated as follows: [ 8.68 ] with: r G stator resistance (pu) x d
subtransiënte reactantie (pu) | subtransient reactance (pu) | unit, normalized to the base impedance of the generator itself. The generator impedance is then calculated as follows: [ 8.68 ] with: r G stator resistance (pu) x d "
Z | Z | the base impedance of the generator itself. The generator impedance is then calculated as follows: [ 8.68 ] with: r G stator resistance (pu) x d " subtransient reactance (pu)
G,base | G,base | base impedance of the generator itself. The generator impedance is then calculated as follows: [ 8.68 ] with: r G stator resistance (pu) x d " subtransient reactance (pu) Z
generator basisimpedantie: | generator base impedance: | impedance of the generator itself. The generator impedance is then calculated as follows: [ 8.68 ] with: r G stator resistance (pu) x d " subtransient reactance (pu) Z G,base
Z | Z | generator itself. The generator impedance is then calculated as follows: [ 8.68 ] with: r G stator resistance (pu) x d " subtransient reactance (pu) Z G,base generator base impedance:
G,base | G,base | itself. The generator impedance is then calculated as follows: [ 8.68 ] with: r G stator resistance (pu) x d " subtransient reactance (pu) Z G,base generator base impedance: Z
The generator impedance is then calculated as follows: [ 8.68 ] with: r G stator resistance (pu) x d " subtransient reactance (pu) Z G,base generator base impedance: Z G,base
G,nom | G,nom | impedance is then calculated as follows: [ 8.68 ] with: r G stator resistance (pu) x d " subtransient reactance (pu) Z G,base generator base impedance: Z G,base = U
2 | 2 | is then calculated as follows: [ 8.68 ] with: r G stator resistance (pu) x d " subtransient reactance (pu) Z G,base generator base impedance: Z G,base = U G,nom
/ S | / S | then calculated as follows: [ 8.68 ] with: r G stator resistance (pu) x d " subtransient reactance (pu) Z G,base generator base impedance: Z G,base = U G,nom 2
nom,G | nom,G | as follows: [ 8.68 ] with: r G stator resistance (pu) x d " subtransient reactance (pu) Z G,base generator base impedance: Z G,base = U G,nom 2 / S
Voor gebruik in kortsluitberekeningen volgens IEC 60909 moet de waarde van de generator-impedantie worden gecorrigeerd met een factor | For use in short-circuit calculations according to IEC 60909, the value of the generator impedance must be corrected by a factor | follows: [ 8.68 ] with: r G stator resistance (pu) x d " subtransient reactance (pu) Z G,base generator base impedance: Z G,base = U G,nom 2 / S nom,G
K | K | Z G,base = U G,nom 2 / S nom,G For use in short-circuit calculations according to IEC 60909, the value of the generator impedance must be corrected by a factor
G | G | G,base = U G,nom 2 / S nom,G For use in short-circuit calculations according to IEC 60909, the value of the generator impedance must be corrected by a factor K
volgens onderstaande formule: | according to the formula below:
[ | [ | S nom,G For use in short-circuit calculations according to IEC 60909, the value of the generator impedance must be corrected by a factor K G according to the formula below:
8.69 | 8.69 | nom,G For use in short-circuit calculations according to IEC 60909, the value of the generator impedance must be corrected by a factor K G according to the formula below: [
] | ] | For use in short-circuit calculations according to IEC 60909, the value of the generator impedance must be corrected by a factor K G according to the formula below: [ 8.69
met: | with: | use in short-circuit calculations according to IEC 60909, the value of the generator impedance must be corrected by a factor K G according to the formula below: [ 8.69 ]
U | U | in short-circuit calculations according to IEC 60909, the value of the generator impedance must be corrected by a factor K G according to the formula below: [ 8.69 ] with:
nom | nom | short-circuit calculations according to IEC 60909, the value of the generator impedance must be corrected by a factor K G according to the formula below: [ 8.69 ] with: U
nominale knooppuntspanning | nominal node voltage | calculations according to IEC 60909, the value of the generator impedance must be corrected by a factor K G according to the formula below: [ 8.69 ] with: U nom
U | U | IEC 60909, the value of the generator impedance must be corrected by a factor K G according to the formula below: [ 8.69 ] with: U nom nominal node voltage
G,nom | G,nom | 60909, the value of the generator impedance must be corrected by a factor K G according to the formula below: [ 8.69 ] with: U nom nominal node voltage U
nominale spanning van de generator | nominal voltage of the generator | the value of the generator impedance must be corrected by a factor K G according to the formula below: [ 8.69 ] with: U nom nominal node voltage U G,nom
c | c | impedance must be corrected by a factor K G according to the formula below: [ 8.69 ] with: U nom nominal node voltage U G,nom nominal voltage of the generator
max | max | must be corrected by a factor K G according to the formula below: [ 8.69 ] with: U nom nominal node voltage U G,nom nominal voltage of the generator c
spanningsparameter voor de kortsluitberekening; 1,05 voor LS-netten met tolerantie van +6% en in alle overige gevallen 1,1 | voltage parameter for the short-circuit calculation; 1.05 for LV networks with a tolerance of +6% and in all other cases 1.1 | be corrected by a factor K G according to the formula below: [ 8.69 ] with: U nom nominal node voltage U G,nom nominal voltage of the generator c max
φ | φ | U G,nom nominal voltage of the generator c max voltage parameter for the short-circuit calculation; 1.05 for LV networks with a tolerance of +6% and in all other cases 1.1
G,nom | G,nom | G,nom nominal voltage of the generator c max voltage parameter for the short-circuit calculation; 1.05 for LV networks with a tolerance of +6% and in all other cases 1.1 φ
nominale hoek tussen stroom en spanning van de generator, afgeleid uit de nominale arbeidsfactor | nominal angle between current and voltage of the generator, derived from the nominal power factor | nominal voltage of the generator c max voltage parameter for the short-circuit calculation; 1.05 for LV networks with a tolerance of +6% and in all other cases 1.1 φ G,nom
Hiermee is de voor IEC 60909 gecorrigeerde generator-impedantie gelijk aan: | This results in the generator impedance corrected for IEC 60909 being equal to: | LV networks with a tolerance of +6% and in all other cases 1.1 φ G,nom nominal angle between current and voltage of the generator, derived from the nominal power factor
[ | [ | φ G,nom nominal angle between current and voltage of the generator, derived from the nominal power factor This results in the generator impedance corrected for IEC 60909 being equal to:
8.70 | 8.70 | G,nom nominal angle between current and voltage of the generator, derived from the nominal power factor This results in the generator impedance corrected for IEC 60909 being equal to: [
] | ] | nominal angle between current and voltage of the generator, derived from the nominal power factor This results in the generator impedance corrected for IEC 60909 being equal to: [ 8.70
De correctiefactor is geïntroduceerd omdat in de berekening de gecorrigeerde knooppuntspanning | The correction factor is introduced because in the calculation the corrected node voltage | angle between current and voltage of the generator, derived from the nominal power factor This results in the generator impedance corrected for IEC 60909 being equal to: [ 8.70 ]
c | c | factor This results in the generator impedance corrected for IEC 60909 being equal to: [ 8.70 ] The correction factor is introduced because in the calculation the corrected node voltage
max | max | This results in the generator impedance corrected for IEC 60909 being equal to: [ 8.70 ] The correction factor is introduced because in the calculation the corrected node voltage c
·U | ·U | results in the generator impedance corrected for IEC 60909 being equal to: [ 8.70 ] The correction factor is introduced because in the calculation the corrected node voltage c max
nom | nom | in the generator impedance corrected for IEC 60909 being equal to: [ 8.70 ] The correction factor is introduced because in the calculation the corrected node voltage c max ·U
/√3 | /√3 | the generator impedance corrected for IEC 60909 being equal to: [ 8.70 ] The correction factor is introduced because in the calculation the corrected node voltage c max ·U nom
wordt gebruikt in plaats van de subtransiënte spanning die in de synchrone machine optreedt. | is used instead of the subtransient voltage that occurs in the synchronous machine. | generator impedance corrected for IEC 60909 being equal to: [ 8.70 ] The correction factor is introduced because in the calculation the corrected node voltage c max ·U nom /√3
Indien de statorweerstand niet is gespecificeerd mag volgens IEC 60909 worden uitgegaan van de volgende richtlijnen: | If the stator resistance is not specified, the following guidelines according to IEC 60909 may be assumed: | correction factor is introduced because in the calculation the corrected node voltage c max ·U nom /√3 is used instead of the subtransient voltage that occurs in the synchronous machine.
R | R | is used instead of the subtransient voltage that occurs in the synchronous machine. If the stator resistance is not specified, the following guidelines according to IEC 60909 may be assumed:
G | G | used instead of the subtransient voltage that occurs in the synchronous machine. If the stator resistance is not specified, the following guidelines according to IEC 60909 may be assumed: R
instead of the subtransient voltage that occurs in the synchronous machine. If the stator resistance is not specified, the following guidelines according to IEC 60909 may be assumed: R G
d | d | the subtransient voltage that occurs in the synchronous machine. If the stator resistance is not specified, the following guidelines according to IEC 60909 may be assumed: R G = 0.05·X
" | " | subtransient voltage that occurs in the synchronous machine. If the stator resistance is not specified, the following guidelines according to IEC 60909 may be assumed: R G = 0.05·X d
voor generatoren met | for generators with | voltage that occurs in the synchronous machine. If the stator resistance is not specified, the following guidelines according to IEC 60909 may be assumed: R G = 0.05·X d "
U | U | in the synchronous machine. If the stator resistance is not specified, the following guidelines according to IEC 60909 may be assumed: R G = 0.05·X d " for generators with
G,nom | G,nom | the synchronous machine. If the stator resistance is not specified, the following guidelines according to IEC 60909 may be assumed: R G = 0.05·X d " for generators with U
> 1 kV en S | > 1 kV and S | synchronous machine. If the stator resistance is not specified, the following guidelines according to IEC 60909 may be assumed: R G = 0.05·X d " for generators with U G,nom
G,nom | G,nom | resistance is not specified, the following guidelines according to IEC 60909 may be assumed: R G = 0.05·X d " for generators with U G,nom > 1 kV and S
≥ 100 MVA | ≥ 100 MVA | is not specified, the following guidelines according to IEC 60909 may be assumed: R G = 0.05·X d " for generators with U G,nom > 1 kV and S G,nom
R | R | the following guidelines according to IEC 60909 may be assumed: R G = 0.05·X d " for generators with U G,nom > 1 kV and S G,nom ≥ 100 MVA
G | G | following guidelines according to IEC 60909 may be assumed: R G = 0.05·X d " for generators with U G,nom > 1 kV and S G,nom ≥ 100 MVA R
guidelines according to IEC 60909 may be assumed: R G = 0.05·X d " for generators with U G,nom > 1 kV and S G,nom ≥ 100 MVA R G
d | d | to IEC 60909 may be assumed: R G = 0.05·X d " for generators with U G,nom > 1 kV and S G,nom ≥ 100 MVA R G = 0.07·X
" | " | IEC 60909 may be assumed: R G = 0.05·X d " for generators with U G,nom > 1 kV and S G,nom ≥ 100 MVA R G = 0.07·X d
voor generatoren met | for generators with | 60909 may be assumed: R G = 0.05·X d " for generators with U G,nom > 1 kV and S G,nom ≥ 100 MVA R G = 0.07·X d "
U | U | assumed: R G = 0.05·X d " for generators with U G,nom > 1 kV and S G,nom ≥ 100 MVA R G = 0.07·X d " for generators with
G,nom | G,nom | R G = 0.05·X d " for generators with U G,nom > 1 kV and S G,nom ≥ 100 MVA R G = 0.07·X d " for generators with U
> 1 kV en S | > 1 kV and S | G = 0.05·X d " for generators with U G,nom > 1 kV and S G,nom ≥ 100 MVA R G = 0.07·X d " for generators with U G,nom
G,nom | G,nom | for generators with U G,nom > 1 kV and S G,nom ≥ 100 MVA R G = 0.07·X d " for generators with U G,nom > 1 kV and S
< 100 MVA | < 100 MVA | generators with U G,nom > 1 kV and S G,nom ≥ 100 MVA R G = 0.07·X d " for generators with U G,nom > 1 kV and S G,nom
R | R | G,nom > 1 kV and S G,nom ≥ 100 MVA R G = 0.07·X d " for generators with U G,nom > 1 kV and S G,nom < 100 MVA
G | G | > 1 kV and S G,nom ≥ 100 MVA R G = 0.07·X d " for generators with U G,nom > 1 kV and S G,nom < 100 MVA R
1 kV and S G,nom ≥ 100 MVA R G = 0.07·X d " for generators with U G,nom > 1 kV and S G,nom < 100 MVA R G
d | d | and S G,nom ≥ 100 MVA R G = 0.07·X d " for generators with U G,nom > 1 kV and S G,nom < 100 MVA R G = 0.15·X
" | " | S G,nom ≥ 100 MVA R G = 0.07·X d " for generators with U G,nom > 1 kV and S G,nom < 100 MVA R G = 0.15·X d
voor generatoren met | for generators with | G,nom ≥ 100 MVA R G = 0.07·X d " for generators with U G,nom > 1 kV and S G,nom < 100 MVA R G = 0.15·X d "
U | U | MVA R G = 0.07·X d " for generators with U G,nom > 1 kV and S G,nom < 100 MVA R G = 0.15·X d " for generators with
G,nom | G,nom | R G = 0.07·X d " for generators with U G,nom > 1 kV and S G,nom < 100 MVA R G = 0.15·X d " for generators with U
≤ 1 kV | ≤ 1 kV | G = 0.07·X d " for generators with U G,nom > 1 kV and S G,nom < 100 MVA R G = 0.15·X d " for generators with U G,nom
De impedantie voor het inverse systeem wordt in het algemeen gelijk genomen aan de impedantie van het normale systeem. | The impedance for the inverse system is generally considered to be equal to the impedance of the normal system. | d " for generators with U G,nom > 1 kV and S G,nom < 100 MVA R G = 0.15·X d " for generators with U G,nom ≤ 1 kV
De statorwikkelingen van de generator zijn meestal in driehoek geschakeld, zodat er geen sterpunt wordt uitgevoerd en er geen aansluiting met nul of aarde is. Indien de generator wel een uitgevoerd en geaard sterpunt heeft, is er een homopolaire impedantie, die voor kortsluitberekeningen volgens IEC 60909 ook met de correctiefactor moet worden vermenigvuldigd: | The stator windings of the generator are usually connected in a delta configuration, so there is no neutral point and no connection to neutral or ground. If the generator does have a neutral point that is brought out and grounded, there is a homopolar impedance, which for short-circuit calculations according to IEC 60909 must also be multiplied by the correction factor: | 0.15·X d " for generators with U G,nom ≤ 1 kV The impedance for the inverse system is generally considered to be equal to the impedance of the normal system.
[ | [ | a neutral point that is brought out and grounded, there is a homopolar impedance, which for short-circuit calculations according to IEC 60909 must also be multiplied by the correction factor:
8.71 | 8.71 | neutral point that is brought out and grounded, there is a homopolar impedance, which for short-circuit calculations according to IEC 60909 must also be multiplied by the correction factor: [
] | ] | point that is brought out and grounded, there is a homopolar impedance, which for short-circuit calculations according to IEC 60909 must also be multiplied by the correction factor: [ 8.71
De correctiefactor wordt niet toegepast op de eventueel aanwezige aardingsimpedantie tussen sterpunt en aarde. | The correction factor is not applied to any grounding impedance that may be present between the neutral point and the ground. | that is brought out and grounded, there is a homopolar impedance, which for short-circuit calculations according to IEC 60909 must also be multiplied by the correction factor: [ 8.71 ]
8.9 Motoren | 8.9 Motors | be multiplied by the correction factor: [ 8.71 ] The correction factor is not applied to any grounding impedance that may be present between the neutral point and the ground.
Motoren zijn uitgevoerd als synchrone of asynchrone machines. De synchrone motoren worden meestal toegepast voor zeer grote vermogens in industriële netten. De behandeling van deze motoren voor gebruik in loadflow- en kortsluitberekeningen gaat op geheel vergelijkbare wijze als bij de synchrone generatoren (Phase, 2006-2). | Motors are designed as synchronous or asynchronous machines. Synchronous motors are usually used for very high power in industrial networks. The handling of these motors for use in load flow and short-circuit calculations is done in a manner entirely similar to that of synchronous generators (Phase, 2006-2). | by the correction factor: [ 8.71 ] The correction factor is not applied to any grounding impedance that may be present between the neutral point and the ground. 8.9 Motors
De meeste motoren zijn uitgevoerd als asynchrone machines met een gewonden rotor of met een kortsluitanker. De werking berust op het feit dat de stromen met frequentie | Most motors are designed as asynchronous machines with a wound rotor or a squirrel-cage rotor. Their operation is based on the fact that the currents with frequency | in industrial networks. The handling of these motors for use in load flow and short-circuit calculations is done in a manner entirely similar to that of synchronous generators (Phase, 2006-2).
f | f | generators (Phase, 2006-2). Most motors are designed as asynchronous machines with a wound rotor or a squirrel-cage rotor. Their operation is based on the fact that the currents with frequency
stator | stator | (Phase, 2006-2). Most motors are designed as asynchronous machines with a wound rotor or a squirrel-cage rotor. Their operation is based on the fact that the currents with frequency f
in de driefasen statorwikkeling een roterend elektromagnetisch veld genereren in de luchtspleet tussen rotor en stator. Dit elektromagnetische veld induceert stromen in de rotorwikkelingen met frequentie | in the three-phase stator winding generate a rotating electromagnetic field in the air gap between rotor and stator. This electromagnetic field induces currents in the rotor windings with frequency | 2006-2). Most motors are designed as asynchronous machines with a wound rotor or a squirrel-cage rotor. Their operation is based on the fact that the currents with frequency f stator
f | f | stator in the three-phase stator winding generate a rotating electromagnetic field in the air gap between rotor and stator. This electromagnetic field induces currents in the rotor windings with frequency
rotor | rotor | in the three-phase stator winding generate a rotating electromagnetic field in the air gap between rotor and stator. This electromagnetic field induces currents in the rotor windings with frequency f
. De rotorstromen genereren op hun beurt een roterend elektromagnetisch veld in de luchtspleet en proberen volgens de wet van Lenz hun oorzaak op te heffen. Als gevolg ontstaat een koppel en gaat de rotor roteren in de richting van het door de stator gegenereerde elektromagnetische veld. Het rotortoerental | The rotor currents, in turn, generate a rotating electromagnetic field in the air gap and attempt to counteract their cause according to Lenz's law. As a result, a torque is produced, and the rotor begins to rotate in the direction of the electromagnetic field generated by the stator. The rotor speed | the three-phase stator winding generate a rotating electromagnetic field in the air gap between rotor and stator. This electromagnetic field induces currents in the rotor windings with frequency f rotor
n | n | to Lenz's law. As a result, a torque is produced, and the rotor begins to rotate in the direction of the electromagnetic field generated by the stator. The rotor speed
rotor | rotor | Lenz's law. As a result, a torque is produced, and the rotor begins to rotate in the direction of the electromagnetic field generated by the stator. The rotor speed n
wijkt af van het synchrone toerental | deviates from the synchronous speed | law. As a result, a torque is produced, and the rotor begins to rotate in the direction of the electromagnetic field generated by the stator. The rotor speed n rotor
n | n | torque is produced, and the rotor begins to rotate in the direction of the electromagnetic field generated by the stator. The rotor speed n rotor deviates from the synchronous speed
stator | stator | is produced, and the rotor begins to rotate in the direction of the electromagnetic field generated by the stator. The rotor speed n rotor deviates from the synchronous speed n
, vandaar de benaming asynchrone machine. Het toerental is afhankelijk van het aantal magnetische poolparen | , hence the name asynchronous machine. The rotational speed depends on the number of magnetic pole pairs. | produced, and the rotor begins to rotate in the direction of the electromagnetic field generated by the stator. The rotor speed n rotor deviates from the synchronous speed n stator
p | p | stator. The rotor speed n rotor deviates from the synchronous speed n stator , hence the name asynchronous machine. The rotational speed depends on the number of magnetic pole pairs.
in de machine: | in the machine: | The rotor speed n rotor deviates from the synchronous speed n stator , hence the name asynchronous machine. The rotational speed depends on the number of magnetic pole pairs. p
[ | [ | n rotor deviates from the synchronous speed n stator , hence the name asynchronous machine. The rotational speed depends on the number of magnetic pole pairs. p in the machine:
8.72 | 8.72 | rotor deviates from the synchronous speed n stator , hence the name asynchronous machine. The rotational speed depends on the number of magnetic pole pairs. p in the machine: [
] | ] | deviates from the synchronous speed n stator , hence the name asynchronous machine. The rotational speed depends on the number of magnetic pole pairs. p in the machine: [ 8.72
Aangezien het toerental van de asynchrone motor altijd afwijkt van het synchrone toerental, wordt gesproken van een slip | Since the rotational speed of the asynchronous motor always differs from the synchronous speed, it is referred to as slip. | from the synchronous speed n stator , hence the name asynchronous machine. The rotational speed depends on the number of magnetic pole pairs. p in the machine: [ 8.72 ]
s | s | magnetic pole pairs. p in the machine: [ 8.72 ] Since the rotational speed of the asynchronous motor always differs from the synchronous speed, it is referred to as slip.
: | : | pole pairs. p in the machine: [ 8.72 ] Since the rotational speed of the asynchronous motor always differs from the synchronous speed, it is referred to as slip. s
[ | [ | pairs. p in the machine: [ 8.72 ] Since the rotational speed of the asynchronous motor always differs from the synchronous speed, it is referred to as slip. s :
8.73 | 8.73 | p in the machine: [ 8.72 ] Since the rotational speed of the asynchronous motor always differs from the synchronous speed, it is referred to as slip. s : [
] | ] | in the machine: [ 8.72 ] Since the rotational speed of the asynchronous motor always differs from the synchronous speed, it is referred to as slip. s : [ 8.73
Hiermee is aangetoond dat de frequentie van de stromen in de rotorwikkelingen evenredig is met het verschil van het synchrone toerental en het rotortoerental. | This demonstrates that the frequency of the currents in the rotor windings is proportional to the difference between the synchronous speed and the rotor speed. | the machine: [ 8.72 ] Since the rotational speed of the asynchronous motor always differs from the synchronous speed, it is referred to as slip. s : [ 8.73 ]
Figuur 8.20 Koppel-toerentalkromme en slip van de asynchrone motor | Figure 8.20 Torque-speed curve and slip of the asynchronous motor | s : [ 8.73 ] This demonstrates that the frequency of the currents in the rotor windings is proportional to the difference between the synchronous speed and the rotor speed.
Een belangrijke curve die het gedrag van de motor voor verschillende toeren beschrijft, is de koppel-toerenkromme. Figuur 8.20 illustreert de koppel-toeren-kromme van een motor met twee poolparen en een synchroon toerental van 1500 omwentelingen per minuut. Het maximale koppel is 1 pu en wordt geleverd bij een slip van 0,2; dus bij een toerental van 1200 omwentelingen per minuut. De kromme laat zien dat het normale werkgebied zich bevindt tussen 1200 en 1500 omwentelingen per minuut. Indien de motor van nullast tot het maximale koppel belast wordt, zal het toerental volgens de kromme dalen van 1500 naar 1200 omwentelingen per minuut. Indien de motor zwaarder wordt belast dan het maximale koppel, kan hij dit koppel niet leveren en zal de motor volgens de kromme tot stilstand komen. De motor 'kippt' dan bij het maximale koppel (het kipp-koppel). In het gebied waar de asynchrone machine sneller draait dan het synchrone toerental, wordt hij door het aangekoppelde werktuig mechanisch aangedreven in plaats van belast en werkt hij als generator. | An important curve that describes the motor's behavior at different speeds is the torque-speed curve. Figure 8.20 illustrates the torque-speed curve of a motor with two pole pairs and a synchronous speed of 1500 revolutions per minute. The maximum torque is 1 pu and is delivered at a slip of 0.2; thus, at a speed of 1200 revolutions per minute. The curve shows that the normal operating range is between 1200 and 1500 revolutions per minute. If the motor is loaded from no load to maximum torque, the speed will drop from 1500 to 1200 revolutions per minute according to the curve. If the motor is loaded beyond the maximum torque, it cannot deliver this torque and will come to a stop according to the curve. The motor 'trips' at the maximum torque (the trip torque). In the region where the asynchronous machine runs faster than the synchronous speed, it is mechanically driven by the coupled load instead of being loaded and operates as a generator. | of the currents in the rotor windings is proportional to the difference between the synchronous speed and the rotor speed. Figure 8.20 Torque-speed curve and slip of the asynchronous motor
Het gespecificeerde vermogen van de motor is meestal het mechanische vermogen in W. Het van het net opgenomen elektrische vermogen is dan afhankelijk van het rendement, dat meestal wordt opgegeven in procent. | The specified power of the motor is usually the mechanical power in W. The electrical power drawn from the grid then depends on the efficiency, which is typically given as a percentage. | In the region where the asynchronous machine runs faster than the synchronous speed, it is mechanically driven by the coupled load instead of being loaded and operates as a generator.
[ | [ | power of the motor is usually the mechanical power in W. The electrical power drawn from the grid then depends on the efficiency, which is typically given as a percentage.
8.74 | 8.74 | of the motor is usually the mechanical power in W. The electrical power drawn from the grid then depends on the efficiency, which is typically given as a percentage. [
] | ] | the motor is usually the mechanical power in W. The electrical power drawn from the grid then depends on the efficiency, which is typically given as a percentage. [ 8.74
Het nominale schijnbare vermogen wordt berekend uit het nominale mechanische vermogen, het nominale rendement en de nominale arbeidsfactor: | The nominal apparent power is calculated from the nominal mechanical power, the nominal efficiency, and the nominal power factor: | motor is usually the mechanical power in W. The electrical power drawn from the grid then depends on the efficiency, which is typically given as a percentage. [ 8.74 ]
[ | [ | efficiency, which is typically given as a percentage. [ 8.74 ] The nominal apparent power is calculated from the nominal mechanical power, the nominal efficiency, and the nominal power factor:
8.75 | 8.75 | which is typically given as a percentage. [ 8.74 ] The nominal apparent power is calculated from the nominal mechanical power, the nominal efficiency, and the nominal power factor: [
] | ] | is typically given as a percentage. [ 8.74 ] The nominal apparent power is calculated from the nominal mechanical power, the nominal efficiency, and the nominal power factor: [ 8.75
De nominale stroom wordt berekend uit het nominale schijnbare vermogen en de nominale spanning: | The nominal current is calculated from the nominal apparent power and the nominal voltage: | typically given as a percentage. [ 8.74 ] The nominal apparent power is calculated from the nominal mechanical power, the nominal efficiency, and the nominal power factor: [ 8.75 ]
[ | [ | from the nominal mechanical power, the nominal efficiency, and the nominal power factor: [ 8.75 ] The nominal current is calculated from the nominal apparent power and the nominal voltage:
8.76 | 8.76 | the nominal mechanical power, the nominal efficiency, and the nominal power factor: [ 8.75 ] The nominal current is calculated from the nominal apparent power and the nominal voltage: [
] | ] | nominal mechanical power, the nominal efficiency, and the nominal power factor: [ 8.75 ] The nominal current is calculated from the nominal apparent power and the nominal voltage: [ 8.76
Voor een loadflowberekening kan worden uitgegaan van een constant actief vermogen voor het motormodel, afhankelijk van het gevraagde mechanische vermogen. De asynchrone motor neemt altijd blindvermogen op. De hoeveelheid opgenomen blindvermogen is echter minder eenvoudig te beschrijven en is afhankelijk van de spanning en het mechanische vermogen. Figuur 8.21 geeft het rendement en de cos(φ) weer als functie van de mechanische belasting. Het valt op dat de curve van het rendement over het grootste werkgebied een redelijk vlakke lijn volgt. De waarde van de cos(φ) neemt snel af bij afnemende mechanische belasting. Het gedrag van de motor wordt bij afnemende belasting steeds inductiever. Bij nullast neemt de motor bijna alleen maar blindvermogen op. Dit wordt veroorzaakt door de hoofdveldreactantie in de motor. | For a load flow calculation, a constant active power can be assumed for the motor model, depending on the required mechanical power. The asynchronous motor always absorbs reactive power. However, the amount of absorbed reactive power is less straightforward to describe and depends on the voltage and mechanical power. Figure 8.21 shows the efficiency and the power factor (cos(φ)) as a function of the mechanical load. It is noticeable that the efficiency curve follows a relatively flat line over the largest working area. The value of the power factor (cos(φ)) decreases rapidly with decreasing mechanical load. The behavior of the motor becomes increasingly inductive with decreasing load. At no load, the motor almost exclusively absorbs reactive power. This is caused by the main field reactance in the motor. | mechanical power, the nominal efficiency, and the nominal power factor: [ 8.75 ] The nominal current is calculated from the nominal apparent power and the nominal voltage: [ 8.76 ]
Figuur 8.21 Rendement en cos(phi) van de asynchrone motor als functie van het vermogen | Figure 8.21 Efficiency and power factor (cos(phi)) of the asynchronous motor as a function of power | of the motor becomes increasingly inductive with decreasing load. At no load, the motor almost exclusively absorbs reactive power. This is caused by the main field reactance in the motor.
Uit deze gegevens kunnen de motorimpedanties worden afgeleid (Cotton, 1967). Voor de loadflow kan in veel gevallen worden volstaan met onderstaande vereenvoudiging: | From this data, the motor impedances can be derived (Cotton, 1967). For the load flow, the following simplification is often sufficient: | absorbs reactive power. This is caused by the main field reactance in the motor. Figure 8.21 Efficiency and power factor (cos(phi)) of the asynchronous motor as a function of power
[ | [ | of the asynchronous motor as a function of power From this data, the motor impedances can be derived (Cotton, 1967). For the load flow, the following simplification is often sufficient:
8.77 | 8.77 | the asynchronous motor as a function of power From this data, the motor impedances can be derived (Cotton, 1967). For the load flow, the following simplification is often sufficient: [
] | ] | asynchronous motor as a function of power From this data, the motor impedances can be derived (Cotton, 1967). For the load flow, the following simplification is often sufficient: [ 8.77
met: | with: | motor as a function of power From this data, the motor impedances can be derived (Cotton, 1967). For the load flow, the following simplification is often sufficient: [ 8.77 ]
P | P | as a function of power From this data, the motor impedances can be derived (Cotton, 1967). For the load flow, the following simplification is often sufficient: [ 8.77 ] with:
M | M | a function of power From this data, the motor impedances can be derived (Cotton, 1967). For the load flow, the following simplification is often sufficient: [ 8.77 ] with: P
elektrisch opgenomen actief vermogen | electrically consumed active power | function of power From this data, the motor impedances can be derived (Cotton, 1967). For the load flow, the following simplification is often sufficient: [ 8.77 ] with: P M
Q | Q | this data, the motor impedances can be derived (Cotton, 1967). For the load flow, the following simplification is often sufficient: [ 8.77 ] with: P M electrically consumed active power
M | M | data, the motor impedances can be derived (Cotton, 1967). For the load flow, the following simplification is often sufficient: [ 8.77 ] with: P M electrically consumed active power Q
opgenomen blindvermogen voor het gekozen werkpunt | reactive power consumed for the chosen operating point | the motor impedances can be derived (Cotton, 1967). For the load flow, the following simplification is often sufficient: [ 8.77 ] with: P M electrically consumed active power Q M
cos(φ) | cos(φ) | For the load flow, the following simplification is often sufficient: [ 8.77 ] with: P M electrically consumed active power Q M reactive power consumed for the chosen operating point
arbeidsfactor voor het gekozen werkpunt | power factor for the chosen operating point | the load flow, the following simplification is often sufficient: [ 8.77 ] with: P M electrically consumed active power Q M reactive power consumed for the chosen operating point cos(φ)
α | alpha | often sufficient: [ 8.77 ] with: P M electrically consumed active power Q M reactive power consumed for the chosen operating point cos(φ) power factor for the chosen operating point
verdeling tussen het constant vermogens- en constante impedantiedeel | distribution between the constant power and constant impedance part | sufficient: [ 8.77 ] with: P M electrically consumed active power Q M reactive power consumed for the chosen operating point cos(φ) power factor for the chosen operating point alpha
Uit bovenstaande blijkt dat het actieve elektrische vermogen afhankelijk is van het gevraagde mechanische vermogen en dat het blindvermogen afhangt van het gevraagde mechanische vermogen en de spanning. Voor de verdeling a tussen het constant vermogens- en constante impedantiedeel kan een waarde van 0,5 gekozen worden. | From the above, it is evident that the active electrical power depends on the requested mechanical power and that the reactive power depends on the requested mechanical power and the voltage. For the distribution α between the constant power and constant impedance part, a value of 0.5 can be chosen. | active power Q M reactive power consumed for the chosen operating point cos(φ) power factor for the chosen operating point alpha distribution between the constant power and constant impedance part
Starten van de asynchrone motor | Starting the asynchronous motor | reactive power depends on the requested mechanical power and the voltage. For the distribution α between the constant power and constant impedance part, a value of 0.5 can be chosen.
Een asynchrone machine kan beschouwd worden als een bijzonder soort transformator met een kleine luchtspleet in het magnetische circuit. Daarom kan een kortsluitankermotor gezien worden als een permanent aan secundaire zijde kortgesloten transformator, waarvan de weerstand in het secundaire circuit afhangt van het toerental. Bij het aanlopen van de motor vanuit stilstand is de slip | An asynchronous machine can be considered a special type of transformer with a small air gap in the magnetic circuit. Therefore, a squirrel-cage motor can be seen as a transformer permanently short-circuited on the secondary side, where the resistance in the secondary circuit depends on the rotational speed. When starting the motor from a standstill, the slip is | the requested mechanical power and the voltage. For the distribution α between the constant power and constant impedance part, a value of 0.5 can be chosen. Starting the asynchronous motor
s | s | a transformer permanently short-circuited on the secondary side, where the resistance in the secondary circuit depends on the rotational speed. When starting the motor from a standstill, the slip is
gelijk aan 1. Hierdoor is de weerstand | equal to 1. As a result, the resistance | transformer permanently short-circuited on the secondary side, where the resistance in the secondary circuit depends on the rotational speed. When starting the motor from a standstill, the slip is s
R | R | the resistance in the secondary circuit depends on the rotational speed. When starting the motor from a standstill, the slip is s equal to 1. As a result, the resistance
rotor | rotor | resistance in the secondary circuit depends on the rotational speed. When starting the motor from a standstill, the slip is s equal to 1. As a result, the resistance R
in het rotorcircuit klein en is de aanloopstroom groot. De aanloopstroom van een asynchrone motor is altijd gespecificeerd en ligt in de orde grootte van 6 tot 8 keer de nominale stroom. In de specificaties wordt hiervoor meestal de aanloopstroomverhouding | in the rotor circuit small and the starting current is large. The starting current of an asynchronous motor is always specified and is typically in the range of 6 to 8 times the nominal current. In the specifications, this is usually referred to as the starting current ratio | in the secondary circuit depends on the rotational speed. When starting the motor from a standstill, the slip is s equal to 1. As a result, the resistance R rotor
I | I | is always specified and is typically in the range of 6 to 8 times the nominal current. In the specifications, this is usually referred to as the starting current ratio
a | a | always specified and is typically in the range of 6 to 8 times the nominal current. In the specifications, this is usually referred to as the starting current ratio I
/I | /I | specified and is typically in the range of 6 to 8 times the nominal current. In the specifications, this is usually referred to as the starting current ratio I a
nom | nom | and is typically in the range of 6 to 8 times the nominal current. In the specifications, this is usually referred to as the starting current ratio I a /I
gespecificeerd. De arbeidsfactor bij aanloop is meestal klein en ligt in de orde grootte van 0,1. Soms is de | specified. The power factor at startup is usually small and is in the order of 0.1. Sometimes the | is typically in the range of 6 to 8 times the nominal current. In the specifications, this is usually referred to as the starting current ratio I a /I nom
cos(φ | cos(φ) | usually referred to as the starting current ratio I a /I nom specified. The power factor at startup is usually small and is in the order of 0.1. Sometimes the
a | a | referred to as the starting current ratio I a /I nom specified. The power factor at startup is usually small and is in the order of 0.1. Sometimes the cos(φ)
) gespecificeerd en soms de | ) specified and sometimes the | to as the starting current ratio I a /I nom specified. The power factor at startup is usually small and is in the order of 0.1. Sometimes the cos(φ) a
R | R | ratio I a /I nom specified. The power factor at startup is usually small and is in the order of 0.1. Sometimes the cos(φ) a ) specified and sometimes the
M | M | I a /I nom specified. The power factor at startup is usually small and is in the order of 0.1. Sometimes the cos(φ) a ) specified and sometimes the R
/X | /X | a /I nom specified. The power factor at startup is usually small and is in the order of 0.1. Sometimes the cos(φ) a ) specified and sometimes the R M
M | M | /I nom specified. The power factor at startup is usually small and is in the order of 0.1. Sometimes the cos(φ) a ) specified and sometimes the R M /X
verhouding bij aanloop. Hieronder is aangegeven hoe deze waardes in elkaar kunnen worden omgerekend. | ratio at startup. Below is an indication of how these values can be converted into each other. | nom specified. The power factor at startup is usually small and is in the order of 0.1. Sometimes the cos(φ) a ) specified and sometimes the R M /X M
[ | [ | Sometimes the cos(φ) a ) specified and sometimes the R M /X M ratio at startup. Below is an indication of how these values can be converted into each other.
8.78 | 8.78 | the cos(φ) a ) specified and sometimes the R M /X M ratio at startup. Below is an indication of how these values can be converted into each other. [
] | ] | cos(φ) a ) specified and sometimes the R M /X M ratio at startup. Below is an indication of how these values can be converted into each other. [ 8.78
Er zijn diverse manieren om de hoge aanloopstroom van een asynchrone motor te beperken. Deze manieren komen neer op het verlagen van de spanning op de statorwikkelingen: | There are several ways to limit the high inrush current of an asynchronous motor. These methods essentially involve reducing the voltage on the stator windings: | a ) specified and sometimes the R M /X M ratio at startup. Below is an indication of how these values can be converted into each other. [ 8.78 ]
DOL: Direct On Line. Bij deze methode wordt de aanloopstroom niet beperkt en direct op het net ingeschakeld. | DOL: Direct On Line. In this method, the starting current is not limited and is directly connected to the grid. | each other. [ 8.78 ] There are several ways to limit the high inrush current of an asynchronous motor. These methods essentially involve reducing the voltage on the stator windings:
Ster-Driehoekschakeling. Bij deze methode worden de statorwikkelingen tijdens het aanlopen eerst in ster geschakeld en na het aanlopen worden zij in driehoek geschakeld. De spanning waarop de motorspoelen worden ingeschakeld ligt in de aanloopsituatie (sterschakeling) een factor √3 lager dan in de eindsituatie (driehoekschakeling). Hierdoor is de aanloopstroom door de statorwikkelingen een factor √3 lager dan in de DOL-situatie. | Star-Delta Connection. In this method, the stator windings are initially connected in a star configuration during startup and are switched to a delta configuration after startup. The voltage applied to the motor coils in the startup situation (star connection) is a factor of √3 lower than in the final situation (delta connection). As a result, the starting current through the stator windings is a factor of √3 lower than in the DOL situation. | methods essentially involve reducing the voltage on the stator windings: DOL: Direct On Line. In this method, the starting current is not limited and is directly connected to the grid.
Autotransformator. Bij deze methode wordt tijdens het aanlopen met behulp van een autotransformator een gereduceerde spanning op de statorwikkelingen aangesloten. | Autotransformer. In this method, during startup, a reduced voltage is applied to the stator windings using an autotransformer. | √3 lower than in the final situation (delta connection). As a result, the starting current through the stator windings is a factor of √3 lower than in the DOL situation.
Softstarter. De motor loopt met behulp van een vermogenselektronische regelaar aan. De vermogenselektronica zorgt ervoor dat de spanning op de motorklemmen bij de start gereduceerd is, waardoor de aanloopstroom beperkt wordt. Een nadeel bij het gebruik van softstarters is dat het aanloopkoppel sterk gereduceerd wordt. | Soft starter. The motor starts with the help of a power electronic controller. The power electronics ensure that the voltage at the motor terminals is reduced during startup, thereby limiting the inrush current. A disadvantage of using soft starters is that the starting torque is significantly reduced. | windings is a factor of √3 lower than in the DOL situation. Autotransformer. In this method, during startup, a reduced voltage is applied to the stator windings using an autotransformer.
Gedrag bij kortsluiting | Behavior during a short circuit | that the voltage at the motor terminals is reduced during startup, thereby limiting the inrush current. A disadvantage of using soft starters is that the starting torque is significantly reduced.
Asynchrone motoren dragen bij aan de kortsluitstroom doordat zij op het moment dat de kortsluiting optreedt nog draaien met het nominale toerental. Vanaf dat moment zal de motor niet plotseling tot stilstand komen, maar nog enige korte tijd als generator werken. Totdat de motor stil staat draagt hij hierdoor bij aan de kortsluitstroom. De hoogte van de kortsluitstroombijdrage wordt bepaald door de kortsluitimpedantie van de motor, die wordt berekend uit de aanloopstroomverhouding | Asynchronous motors contribute to the short-circuit current because they are still running at nominal speed when the short circuit occurs. From that moment, the motor will not suddenly come to a stop but will continue to operate as a generator for a short period. Until the motor comes to a complete stop, it will thus contribute to the short-circuit current. The magnitude of the short-circuit current contribution is determined by the short-circuit impedance of the motor, which is calculated from the inrush current ratio. | motor terminals is reduced during startup, thereby limiting the inrush current. A disadvantage of using soft starters is that the starting torque is significantly reduced. Behavior during a short circuit
I | I | thus contribute to the short-circuit current. The magnitude of the short-circuit current contribution is determined by the short-circuit impedance of the motor, which is calculated from the inrush current ratio.
a | a | contribute to the short-circuit current. The magnitude of the short-circuit current contribution is determined by the short-circuit impedance of the motor, which is calculated from the inrush current ratio. I
/I | /I | to the short-circuit current. The magnitude of the short-circuit current contribution is determined by the short-circuit impedance of the motor, which is calculated from the inrush current ratio. I a
nom | nom | the short-circuit current. The magnitude of the short-circuit current contribution is determined by the short-circuit impedance of the motor, which is calculated from the inrush current ratio. I a /I
: | : | short-circuit current. The magnitude of the short-circuit current contribution is determined by the short-circuit impedance of the motor, which is calculated from the inrush current ratio. I a /I nom
[ | [ | current. The magnitude of the short-circuit current contribution is determined by the short-circuit impedance of the motor, which is calculated from the inrush current ratio. I a /I nom :
8.79 | 8.79 | The magnitude of the short-circuit current contribution is determined by the short-circuit impedance of the motor, which is calculated from the inrush current ratio. I a /I nom : [
] | ] | magnitude of the short-circuit current contribution is determined by the short-circuit impedance of the motor, which is calculated from the inrush current ratio. I a /I nom : [ 8.79
Met behulp van de | With the help of the | of the short-circuit current contribution is determined by the short-circuit impedance of the motor, which is calculated from the inrush current ratio. I a /I nom : [ 8.79 ]
R | R | is determined by the short-circuit impedance of the motor, which is calculated from the inrush current ratio. I a /I nom : [ 8.79 ] With the help of the
M | M | determined by the short-circuit impedance of the motor, which is calculated from the inrush current ratio. I a /I nom : [ 8.79 ] With the help of the R
/X | /X | by the short-circuit impedance of the motor, which is calculated from the inrush current ratio. I a /I nom : [ 8.79 ] With the help of the R M
M | M | the short-circuit impedance of the motor, which is calculated from the inrush current ratio. I a /I nom : [ 8.79 ] With the help of the R M /X
verhouding of de | ratio of the | short-circuit impedance of the motor, which is calculated from the inrush current ratio. I a /I nom : [ 8.79 ] With the help of the R M /X M
cos(φ | cos(φ) | the motor, which is calculated from the inrush current ratio. I a /I nom : [ 8.79 ] With the help of the R M /X M ratio of the
a | a | motor, which is calculated from the inrush current ratio. I a /I nom : [ 8.79 ] With the help of the R M /X M ratio of the cos(φ)
) tijdens aanloop wordt de verdeling tussen | ) during startup, the distribution between | which is calculated from the inrush current ratio. I a /I nom : [ 8.79 ] With the help of the R M /X M ratio of the cos(φ) a
R | R | current ratio. I a /I nom : [ 8.79 ] With the help of the R M /X M ratio of the cos(φ) a ) during startup, the distribution between
M | M | ratio. I a /I nom : [ 8.79 ] With the help of the R M /X M ratio of the cos(φ) a ) during startup, the distribution between R
en | en | I a /I nom : [ 8.79 ] With the help of the R M /X M ratio of the cos(φ) a ) during startup, the distribution between R M
X | X | a /I nom : [ 8.79 ] With the help of the R M /X M ratio of the cos(φ) a ) during startup, the distribution between R M en
M | M | /I nom : [ 8.79 ] With the help of the R M /X M ratio of the cos(φ) a ) during startup, the distribution between R M en X
berekend: | calculated: | nom : [ 8.79 ] With the help of the R M /X M ratio of the cos(φ) a ) during startup, the distribution between R M en X M
[ | [ | : [ 8.79 ] With the help of the R M /X M ratio of the cos(φ) a ) during startup, the distribution between R M en X M calculated:
8.80 | 8.80 | [ 8.79 ] With the help of the R M /X M ratio of the cos(φ) a ) during startup, the distribution between R M en X M calculated: [
] | ] | 8.79 ] With the help of the R M /X M ratio of the cos(φ) a ) during startup, the distribution between R M en X M calculated: [ 8.80
Indien de | If the | ] With the help of the R M /X M ratio of the cos(φ) a ) during startup, the distribution between R M en X M calculated: [ 8.80 ]
R | R | the help of the R M /X M ratio of the cos(φ) a ) during startup, the distribution between R M en X M calculated: [ 8.80 ] If the
M | M | help of the R M /X M ratio of the cos(φ) a ) during startup, the distribution between R M en X M calculated: [ 8.80 ] If the R
/X | /X | of the R M /X M ratio of the cos(φ) a ) during startup, the distribution between R M en X M calculated: [ 8.80 ] If the R M
M | M | the R M /X M ratio of the cos(φ) a ) during startup, the distribution between R M en X M calculated: [ 8.80 ] If the R M /X
verhouding of de | ratio of the | R M /X M ratio of the cos(φ) a ) during startup, the distribution between R M en X M calculated: [ 8.80 ] If the R M /X M
cos(φ | cos(φ) | M ratio of the cos(φ) a ) during startup, the distribution between R M en X M calculated: [ 8.80 ] If the R M /X M ratio of the
a | a | ratio of the cos(φ) a ) during startup, the distribution between R M en X M calculated: [ 8.80 ] If the R M /X M ratio of the cos(φ)
) tijdens aanloop niet zijn gespecificeerd, kan volgens IEC 60909 worden uitgegaan van onderstaande aannames: | ) are not specified during startup, the following assumptions can be made according to IEC 60909: | of the cos(φ) a ) during startup, the distribution between R M en X M calculated: [ 8.80 ] If the R M /X M ratio of the cos(φ) a
Motortype | Motortype | [ 8.80 ] If the R M /X M ratio of the cos(φ) a ) are not specified during startup, the following assumptions can be made according to IEC 60909:
R | R | 8.80 ] If the R M /X M ratio of the cos(φ) a ) are not specified during startup, the following assumptions can be made according to IEC 60909: Motortype
M | M | ] If the R M /X M ratio of the cos(φ) a ) are not specified during startup, the following assumptions can be made according to IEC 60909: Motortype R
/X | /X | If the R M /X M ratio of the cos(φ) a ) are not specified during startup, the following assumptions can be made according to IEC 60909: Motortype R M
M | M | the R M /X M ratio of the cos(φ) a ) are not specified during startup, the following assumptions can be made according to IEC 60909: Motortype R M /X
Middenspanningsmotor; vermogen per poolpaar ≥ 1 MW | Medium voltage motor; power per pole pair ≥ 1 MW | R M /X M ratio of the cos(φ) a ) are not specified during startup, the following assumptions can be made according to IEC 60909: Motortype R M /X M
0,10 | 0.10 | are not specified during startup, the following assumptions can be made according to IEC 60909: Motortype R M /X M Medium voltage motor; power per pole pair ≥ 1 MW
Middenspanningsmotor; vermogen per poolpaar < 1 MW | Medium voltage motor; power per pole pair < 1 MW | not specified during startup, the following assumptions can be made according to IEC 60909: Motortype R M /X M Medium voltage motor; power per pole pair ≥ 1 MW 0.10
0,15 | 0.15 | according to IEC 60909: Motortype R M /X M Medium voltage motor; power per pole pair ≥ 1 MW 0.10 Medium voltage motor; power per pole pair < 1 MW
Laagspanningsmotor | Laagspanningsmotor | to IEC 60909: Motortype R M /X M Medium voltage motor; power per pole pair ≥ 1 MW 0.10 Medium voltage motor; power per pole pair < 1 MW 0.15
0,42 | 0.42 | IEC 60909: Motortype R M /X M Medium voltage motor; power per pole pair ≥ 1 MW 0.10 Medium voltage motor; power per pole pair < 1 MW 0.15 Laagspanningsmotor
De kortsluitimpedantie in het inverse stelsel wordt gelijk genomen aan die van het normale stelsel. Asynchrone motoren zijn meestal in driehoek geschakeld, waardoor de homopolaire impedantie oneindig is. Indien de statorwikkelingen van de motoren tijdens normaal bedrijf in ster zijn geschakeld met geaard sterpunt, moet de homopolaire impedantie door de fabrikant zijn gespecificeerd. | The short-circuit impedance in the inverse system is taken to be the same as that of the normal system. Asynchronous motors are usually connected in a delta configuration, resulting in an infinite homopolar impedance. If the stator windings of the motors are connected in a star configuration with a grounded neutral point during normal operation, the homopolar impedance must be specified by the manufacturer. | 60909: Motortype R M /X M Medium voltage motor; power per pole pair ≥ 1 MW 0.10 Medium voltage motor; power per pole pair < 1 MW 0.15 Laagspanningsmotor 0.42
Wel of geen kortsluitstroombijdrage | With or without short-circuit current contribution | If the stator windings of the motors are connected in a star configuration with a grounded neutral point during normal operation, the homopolar impedance must be specified by the manufacturer.
Motoren die tijdens normaal bedrijf direct op het net zijn aangesloten, zullen in kortsluitsituaties altijd bijdragen aan de kortsluitstroom. Indien de motor met behulp van een converter wordt geregeld, hangt het van de converter af of en hoeveel de kortsluitstroombijdrage is. De meeste converters staan niet toe dat de stroom in de omgekeerde richting vloeit en zullen dan ook niet bijdragen aan de kortsluitstroom. Er bestaan ook converters die wel teruglevering toestaan. Deze zogenaamde 'Reversible static converter-fed drives' zullen in mindere mate bijdragen aan de kortsluitstroom. De norm IEC 60909 gaat uit van onderstaande: | Motors that are directly connected to the grid during normal operation will always contribute to the short-circuit current in short-circuit situations. If the motor is controlled using a converter, it depends on the converter whether and how much it contributes to the short-circuit current. Most converters do not allow current to flow in the reverse direction and therefore will not contribute to the short-circuit current. There are also converters that do allow reverse flow. These so-called 'Reversible static converter-fed drives' will contribute to the short-circuit current to a lesser extent. The IEC 60909 standard assumes the following: | motors are connected in a star configuration with a grounded neutral point during normal operation, the homopolar impedance must be specified by the manufacturer. With or without short-circuit current contribution
I | I | also converters that do allow reverse flow. These so-called 'Reversible static converter-fed drives' will contribute to the short-circuit current to a lesser extent. The IEC 60909 standard assumes the following:
a | a | converters that do allow reverse flow. These so-called 'Reversible static converter-fed drives' will contribute to the short-circuit current to a lesser extent. The IEC 60909 standard assumes the following: I
/I | /I | that do allow reverse flow. These so-called 'Reversible static converter-fed drives' will contribute to the short-circuit current to a lesser extent. The IEC 60909 standard assumes the following: I a
nom | nom | do allow reverse flow. These so-called 'Reversible static converter-fed drives' will contribute to the short-circuit current to a lesser extent. The IEC 60909 standard assumes the following: I a /I
allow reverse flow. These so-called 'Reversible static converter-fed drives' will contribute to the short-circuit current to a lesser extent. The IEC 60909 standard assumes the following: I a /I nom
R | R | flow. These so-called 'Reversible static converter-fed drives' will contribute to the short-circuit current to a lesser extent. The IEC 60909 standard assumes the following: I a /I nom = 3
M | M | These so-called 'Reversible static converter-fed drives' will contribute to the short-circuit current to a lesser extent. The IEC 60909 standard assumes the following: I a /I nom = 3 R
/X | /X | so-called 'Reversible static converter-fed drives' will contribute to the short-circuit current to a lesser extent. The IEC 60909 standard assumes the following: I a /I nom = 3 R M
M | M | 'Reversible static converter-fed drives' will contribute to the short-circuit current to a lesser extent. The IEC 60909 standard assumes the following: I a /I nom = 3 R M /X
static converter-fed drives' will contribute to the short-circuit current to a lesser extent. The IEC 60909 standard assumes the following: I a /I nom = 3 R M /X M
8.10 Converters en gelijkrichters | 8.10 Converters and rectifiers | drives' will contribute to the short-circuit current to a lesser extent. The IEC 60909 standard assumes the following: I a /I nom = 3 R M /X M = 0.1
Converters voeden meestal motoren die met variabel toerental moeten draaien. Gelijkrichters voeden weer andere processen. Ook spoor- en tramwegen worden via gelijkrichters gevoed. Het elektrische gedrag vanuit het net bezien is daarom zeer divers. In de meeste loadflowberekeningen wordt daarom ook volstaan met een eenvoudig algemeen belastingsmodel, waarvan de belasting wordt bepaald door het achterliggende proces. Vaak wordt ook aangenomen dat de arbeidsfactor gelijk aan 1 is, waardoor geen blindvermogen wordt opgenomen. | Converters usually power motors that need to run at variable speeds. Rectifiers, on the other hand, power different processes. Railways and tramways are also powered via rectifiers. Therefore, the electrical behavior from the grid's perspective is very diverse. In most load flow calculations, a simple general load model is often sufficient, where the load is determined by the underlying process. It is also often assumed that the power factor is equal to 1, so no reactive power is consumed. | the short-circuit current to a lesser extent. The IEC 60909 standard assumes the following: I a /I nom = 3 R M /X M = 0.1 8.10 Converters and rectifiers
Gelijkrichters leveren geen bijdrage aan de kortsluitstroom. Converters leveren soms een kortsluitstroombijdrage. Hiervoor wordt meestal maximaal een waarde van 1,2 maal de nominale stroom aangenomen. | Rectifiers do not contribute to the short-circuit current. Converters sometimes provide a short-circuit current contribution. For this, a value of up to 1.2 times the nominal current is usually assumed. | often sufficient, where the load is determined by the underlying process. It is also often assumed that the power factor is equal to 1, so no reactive power is consumed.
8.11 Windturbinegeneratoren | 8.11 Wind Turbine Generators | Rectifiers do not contribute to the short-circuit current. Converters sometimes provide a short-circuit current contribution. For this, a value of up to 1.2 times the nominal current is usually assumed.
Het vermogen dat de windturbine levert, wordt geproduceerd door een synchrone of asynchrone generator of door een dubbelgevoede asynchrone generator, die direct of via een tandwielkast wordt aangedreven door de windturbinebladen. De generator is via een converter of rechtstreeks op het net aangesloten. Figuur 8.22 toont het geproduceerde vermogen als functie van de windsnelheid. Het vermogen is afhankelijk van de derde macht van de windsnelheid. Beneden een bepaalde lage windsnelheid is het vermogen nul, omdat de generator niet meer in staat is netto vermogen te produceren. Boven een bepaalde windsnelheid wordt het geleverde vermogen begrensd door het nominale vermogen van de generator. De karakteristiek vertoont dan een vlakke curve en het vermogen neemt niet meer toe met toenemende windsnelheid. Boven een zekere nog hogere windsnelheid wordt de windturbine uit bedrijf genomen om mechanische beschadiging te voorkomen. | The power generated by the wind turbine is produced by a synchronous or asynchronous generator or by a doubly-fed asynchronous generator, which is driven directly or via a gearbox by the wind turbine blades. The generator is connected to the grid either through a converter or directly. Figure 8.22 shows the generated power as a function of wind speed. The power depends on the cube of the wind speed. Below a certain low wind speed, the power is zero because the generator is no longer able to produce net power. Above a certain wind speed, the delivered power is limited by the nominal power of the generator. The characteristic then shows a flat curve, and the power no longer increases with increasing wind speed. Above an even higher wind speed, the wind turbine is taken out of operation to prevent mechanical damage. | to the short-circuit current. Converters sometimes provide a short-circuit current contribution. For this, a value of up to 1.2 times the nominal current is usually assumed. 8.11 Wind Turbine Generators
[ | [ | flat curve, and the power no longer increases with increasing wind speed. Above an even higher wind speed, the wind turbine is taken out of operation to prevent mechanical damage.
8.81 | 8.81 | curve, and the power no longer increases with increasing wind speed. Above an even higher wind speed, the wind turbine is taken out of operation to prevent mechanical damage. [
] | ] | and the power no longer increases with increasing wind speed. Above an even higher wind speed, the wind turbine is taken out of operation to prevent mechanical damage. [ 8.81
met: | with: | the power no longer increases with increasing wind speed. Above an even higher wind speed, the wind turbine is taken out of operation to prevent mechanical damage. [ 8.81 ]
P | P | power no longer increases with increasing wind speed. Above an even higher wind speed, the wind turbine is taken out of operation to prevent mechanical damage. [ 8.81 ] with:
nom | nom | no longer increases with increasing wind speed. Above an even higher wind speed, the wind turbine is taken out of operation to prevent mechanical damage. [ 8.81 ] with: P
nominaal generatorvermogen (MW) | nominal generator power (MW) | longer increases with increasing wind speed. Above an even higher wind speed, the wind turbine is taken out of operation to prevent mechanical damage. [ 8.81 ] with: P nom
V | V | wind speed. Above an even higher wind speed, the wind turbine is taken out of operation to prevent mechanical damage. [ 8.81 ] with: P nom nominal generator power (MW)
nom | nom | speed. Above an even higher wind speed, the wind turbine is taken out of operation to prevent mechanical damage. [ 8.81 ] with: P nom nominal generator power (MW) V
nominale windsnelheid (m/s) | nominal wind speed (m/s) | Above an even higher wind speed, the wind turbine is taken out of operation to prevent mechanical damage. [ 8.81 ] with: P nom nominal generator power (MW) V nom
V | V | wind speed, the wind turbine is taken out of operation to prevent mechanical damage. [ 8.81 ] with: P nom nominal generator power (MW) V nom nominal wind speed (m/s)
act | act | speed, the wind turbine is taken out of operation to prevent mechanical damage. [ 8.81 ] with: P nom nominal generator power (MW) V nom nominal wind speed (m/s) V
actuele windsnelheid (m/s) | actual wind speed (m/s) | the wind turbine is taken out of operation to prevent mechanical damage. [ 8.81 ] with: P nom nominal generator power (MW) V nom nominal wind speed (m/s) V act
Bij asynchrone generatoren is sprake van 'slip'. Dit is de afwijking van het generatortoerental ten opzichte van de synchrone toerental. Deze wordt berekend volgens: | In asynchronous generators, there is 'slip'. This is the deviation of the generator speed relative to the synchronous speed. It is calculated as follows: | taken out of operation to prevent mechanical damage. [ 8.81 ] with: P nom nominal generator power (MW) V nom nominal wind speed (m/s) V act actual wind speed (m/s)
[ | [ | V act actual wind speed (m/s) In asynchronous generators, there is 'slip'. This is the deviation of the generator speed relative to the synchronous speed. It is calculated as follows:
8.82 | 8.82 | act actual wind speed (m/s) In asynchronous generators, there is 'slip'. This is the deviation of the generator speed relative to the synchronous speed. It is calculated as follows: [
] | ] | actual wind speed (m/s) In asynchronous generators, there is 'slip'. This is the deviation of the generator speed relative to the synchronous speed. It is calculated as follows: [ 8.82
Figuur 8.22 Vermogenskarakteristiek van een windturbine | Figure 8.22 Power characteristic of a wind turbine | wind speed (m/s) In asynchronous generators, there is 'slip'. This is the deviation of the generator speed relative to the synchronous speed. It is calculated as follows: [ 8.82 ]
Figuur 8.23 Slip als functie van de windsnelheid | Figure 8.23 Slip as a function of wind speed | 'slip'. This is the deviation of the generator speed relative to the synchronous speed. It is calculated as follows: [ 8.82 ] Figure 8.22 Power characteristic of a wind turbine
In het voorbeeld van figuur 8.23 correspondeert een slip van +35% met 975 omw/min en een slip van –35% met 2025 omw/min. Een hoger toerental wordt niet toegestaan om beschadiging te voorkomen. De relatie tussen toerental en windsnelheid is een eigenschap van de windturbine. | In the example of figure 8.23, a slip of +35% corresponds to 975 RPM and a slip of -35% corresponds to 2025 RPM. A higher rotational speed is not allowed to prevent damage. The relationship between rotational speed and wind speed is a characteristic of the wind turbine. | relative to the synchronous speed. It is calculated as follows: [ 8.82 ] Figure 8.22 Power characteristic of a wind turbine Figure 8.23 Slip as a function of wind speed
De omwentelsnelheid van de rotor is veel lager dan de elektrische frequentie. Daarom worden vaak een versnellingsbak en meerpolige machines toegepast. Er zijn vier belangrijke soorten windturbinesystemen: | The rotational speed of the rotor is much lower than the electrical frequency. Therefore, a gearbox and multipole machines are often used. There are four main types of wind turbine systems: | -35% corresponds to 2025 RPM. A higher rotational speed is not allowed to prevent damage. The relationship between rotational speed and wind speed is a characteristic of the wind turbine.
vast toerental windturbine met een asynchrone machine | fixed-speed wind turbine with an asynchronous machine | rotational speed of the rotor is much lower than the electrical frequency. Therefore, a gearbox and multipole machines are often used. There are four main types of wind turbine systems:
variabel toerental windturbine met een asynchrone machine of met een synchrone machine | variable speed wind turbine with an asynchronous machine or with a synchronous machine | lower than the electrical frequency. Therefore, a gearbox and multipole machines are often used. There are four main types of wind turbine systems: fixed-speed wind turbine with an asynchronous machine
variabel toerental windturbine met een meerpolige synchrone generator of een meerpolige permanent-magneet synchrone generator | variable speed wind turbine with a multipole synchronous generator or a multipole permanent magnet synchronous generator | used. There are four main types of wind turbine systems: fixed-speed wind turbine with an asynchronous machine variable speed wind turbine with an asynchronous machine or with a synchronous machine
variabel toerental windturbine met een dubbelgevoede asynchrone generator | variable speed wind turbine with a doubly-fed asynchronous generator | machine variable speed wind turbine with an asynchronous machine or with a synchronous machine variable speed wind turbine with a multipole synchronous generator or a multipole permanent magnet synchronous generator
Vast toerental windturbine | Fixed speed wind turbine | or with a synchronous machine variable speed wind turbine with a multipole synchronous generator or a multipole permanent magnet synchronous generator variable speed wind turbine with a doubly-fed asynchronous generator
De asynchrone machine in een windturbine met vast toerental is direct gekoppeld aan het net. De rotorsnelheid wordt in principe bepaald door de versnellingsbak en het poolpaartal van de generator. Dit soort windturbines heeft vaak twee vaste toerentallen: een voor lage en een voor hoge windsnelheid. Hierdoor kan de windturbine vaker rond een optimaal koppel werken. Dit systeem is tussen 1980 en 1990 veelvuldig toegepast. | The asynchronous machine in a fixed-speed wind turbine is directly connected to the grid. The rotor speed is essentially determined by the gearbox and the number of pole pairs of the generator. This type of wind turbine often has two fixed speeds: one for low wind speed and one for high wind speed. This allows the wind turbine to operate more frequently around an optimal torque. This system was widely used between 1980 and 1990. | machine variable speed wind turbine with a multipole synchronous generator or a multipole permanent magnet synchronous generator variable speed wind turbine with a doubly-fed asynchronous generator Fixed speed wind turbine
Figuur 8.24 Vast toerental windturbine met een asynchrone generator | Figure 8.24 Fixed-speed wind turbine with an asynchronous generator | wind speed and one for high wind speed. This allows the wind turbine to operate more frequently around an optimal torque. This system was widely used between 1980 and 1990.
De asynchrone machine in deze windturbine levert actief vermogen en neemt blindvermogen op. Het actieve vermogen hangt af van de windsnelheid. Het blindvermogen wordt bepaald door de machine­parameters. In de windturbine is een condensatorbank opgenomen ter compensatie van het blindvermogen. In veel gevallen worden de condensatoren afhankelijk van het geleverde vermogen automatisch ingeschakeld. In geval van een kortsluiting levert de windturbine een bijdrage aan de kortsluitstroom. | The asynchronous machine in this wind turbine delivers active power and absorbs reactive power. The active power depends on the wind speed. The reactive power is determined by the machine parameters. A capacitor bank is included in the wind turbine to compensate for the reactive power. In many cases, the capacitors are automatically switched on depending on the delivered power. In the event of a short circuit, the wind turbine contributes to the short-circuit current. | allows the wind turbine to operate more frequently around an optimal torque. This system was widely used between 1980 and 1990. Figure 8.24 Fixed-speed wind turbine with an asynchronous generator
Figuur 8.25 toont een model van deze windturbine. De asynchrone generator is in de gondel aangesloten via een aantal parallelle kabels. Hierbij is aangenomen dat de transformator zich in de mastvoet bevindt. Indien de transformator zich in de gondel zou bevinden, zouden de parallelle kabels vervallen. De condensatoren voor de blindvermogencompensatie zijn gemodelleerd als een condensator, die is aangesloten op de secundaire zijde van de transformator. De capaciteit van de condensator hangt af van het geproduceerde actieve vermogen. Duidelijk zichtbaar is dat de asynchrone generator actief vermogen produceert en blindvermogen opneemt. Dit blindvermogen wordt gecompenseerd door de condensator. | Figure 8.25 shows a model of this wind turbine. The asynchronous generator is connected in the nacelle via several parallel cables. It is assumed that the transformer is located at the base of the mast. If the transformer were located in the nacelle, the parallel cables would be unnecessary. The capacitors for reactive power compensation are modeled as a single capacitor connected to the secondary side of the transformer. The capacity of the capacitor depends on the produced active power. It is clearly visible that the asynchronous generator produces active power and absorbs reactive power. This reactive power is compensated by the capacitor. | power. In many cases, the capacitors are automatically switched on depending on the delivered power. In the event of a short circuit, the wind turbine contributes to the short-circuit current.
Figuur 8.25 Model van een vast toerental wind turbine met een asynchrone generator | Figure 8.25 Model of a fixed-speed wind turbine with an asynchronous generator | capacitor depends on the produced active power. It is clearly visible that the asynchronous generator produces active power and absorbs reactive power. This reactive power is compensated by the capacitor.
Variabel toerental windturbine met een converter | Variable speed wind turbine with a converter | the asynchronous generator produces active power and absorbs reactive power. This reactive power is compensated by the capacitor. Figure 8.25 Model of a fixed-speed wind turbine with an asynchronous generator
In het windturbinesysteem in figuur 8.26 is de stator van de generator via een converter gekoppeld met het net. De generator kan een asynchrone kortsluitankergenerator zijn of een synchrone generator. De versnellingsbak is zodanig ontworpen dat de maximale rotorsnelheid overeenkomt met het nominale toerental van de generator. | In the wind turbine system in figure 8.26, the stator of the generator is connected to the grid via a converter. The generator can be an asynchronous squirrel-cage generator or a synchronous generator. The gearbox is designed such that the maximum rotor speed corresponds to the nominal speed of the generator. | absorbs reactive power. This reactive power is compensated by the capacitor. Figure 8.25 Model of a fixed-speed wind turbine with an asynchronous generator Variable speed wind turbine with a converter
Figuur 8.26 Variabel toerental windturbine met een synchrone/asynchrone generator | Figure 8.26 Variable speed wind turbine with a synchronous/asynchronous generator | The generator can be an asynchronous squirrel-cage generator or a synchronous generator. The gearbox is designed such that the maximum rotor speed corresponds to the nominal speed of the generator.
In geval van een synchrone generator kan deze met een groter poolpaartal worden uitgerust, zodat een versnellingsbak niet nodig is (Figuur 8.27). Aangezien er veel ervaring is met de toepassing van deze 'full-power' converter/generator systemen, is het concept goed uitontwikkeld. | In the case of a synchronous generator, it can be equipped with a higher number of pole pairs, making a gearbox unnecessary (Figure 8.27). Since there is extensive experience with the application of these 'full-power' converter/generator systems, the concept is well-developed. | synchronous generator. The gearbox is designed such that the maximum rotor speed corresponds to the nominal speed of the generator. Figure 8.26 Variable speed wind turbine with a synchronous/asynchronous generator
Figuur 8.27 Variabel toerental windturbine met een synchrone generator zonder versnellingsbak | Figure 8.27 Variable speed wind turbine with a synchronous generator without a gearbox | with a higher number of pole pairs, making a gearbox unnecessary (Figure 8.27). Since there is extensive experience with the application of these 'full-power' converter/generator systems, the concept is well-developed.
De windturbine levert actief vermogen. De uitwisseling van blindvermogen met het net wordt geregeld door de converter. In geval van een kortsluiting levert de windturbine geen of geringe bijdrage aan de kortsluitstroom. | The wind turbine delivers active power. The exchange of reactive power with the grid is regulated by the converter. In the event of a short circuit, the wind turbine provides little to no contribution to the short-circuit current. | Since there is extensive experience with the application of these 'full-power' converter/generator systems, the concept is well-developed. Figure 8.27 Variable speed wind turbine with a synchronous generator without a gearbox
Figuur 8.28 toont een model van deze windturbine. De generator is in de gondel aangesloten via een aantal parallelle kabels. Hierbij is aangenomen dat de transformator zich in de mastvoet bevindt. Indien de transformator zich in de gondel zou bevinden, zouden de parallelle kabels vervallen. Aangezien de generator zich achter een converter bevindt, is deze samen met de converter gemodelleerd als een synchrone generator met een vaste cos(φ). In het voorbeeld is de cos(φ) gelijk aan 0,9835. | Figure 8.28 shows a model of this wind turbine. The generator is connected in the nacelle via several parallel cables. It is assumed that the transformer is located at the base of the tower. If the transformer were located in the nacelle, the parallel cables would be unnecessary. Since the generator is positioned behind a converter, it is modeled together with the converter as a synchronous generator with a fixed cos(φ). In the example, the cos(φ) is equal to 0.9835. | of reactive power with the grid is regulated by the converter. In the event of a short circuit, the wind turbine provides little to no contribution to the short-circuit current.
Figuur 8.28 Model van een variabel toerental windturbine met een converter | Figure 8.28 Model of a variable speed wind turbine with a converter | generator is positioned behind a converter, it is modeled together with the converter as a synchronous generator with a fixed cos(φ). In the example, the cos(φ) is equal to 0.9835.
Om de maximale kortsluitbijdrage van de generator met converter te beperken tot 1,2 maal de nominale generatorstroom, wordt de subtransiënte reactantie | To limit the maximum short-circuit contribution of the generator with converter to 1.2 times the nominal generator current, the subtransient reactance | converter as a synchronous generator with a fixed cos(φ). In the example, the cos(φ) is equal to 0.9835. Figure 8.28 Model of a variable speed wind turbine with a converter
X | X | of a variable speed wind turbine with a converter To limit the maximum short-circuit contribution of the generator with converter to 1.2 times the nominal generator current, the subtransient reactance
d | d | a variable speed wind turbine with a converter To limit the maximum short-circuit contribution of the generator with converter to 1.2 times the nominal generator current, the subtransient reactance X
" | " | variable speed wind turbine with a converter To limit the maximum short-circuit contribution of the generator with converter to 1.2 times the nominal generator current, the subtransient reactance X d
van de synchrone generator als volgt berekend: | of the synchronous generator is calculated as follows: | speed wind turbine with a converter To limit the maximum short-circuit contribution of the generator with converter to 1.2 times the nominal generator current, the subtransient reactance X d "
[ | [ | the maximum short-circuit contribution of the generator with converter to 1.2 times the nominal generator current, the subtransient reactance X d " of the synchronous generator is calculated as follows:
8.83 | 8.83 | maximum short-circuit contribution of the generator with converter to 1.2 times the nominal generator current, the subtransient reactance X d " of the synchronous generator is calculated as follows: [
] | ] | short-circuit contribution of the generator with converter to 1.2 times the nominal generator current, the subtransient reactance X d " of the synchronous generator is calculated as follows: [ 8.83
met: | with: | contribution of the generator with converter to 1.2 times the nominal generator current, the subtransient reactance X d " of the synchronous generator is calculated as follows: [ 8.83 ]
[ | [ | of the generator with converter to 1.2 times the nominal generator current, the subtransient reactance X d " of the synchronous generator is calculated as follows: [ 8.83 ] with:
8.84 | 8.84 | the generator with converter to 1.2 times the nominal generator current, the subtransient reactance X d " of the synchronous generator is calculated as follows: [ 8.83 ] with: [
] | ] | generator with converter to 1.2 times the nominal generator current, the subtransient reactance X d " of the synchronous generator is calculated as follows: [ 8.83 ] with: [ 8.84
Voorbeeld: | Example: | with converter to 1.2 times the nominal generator current, the subtransient reactance X d " of the synchronous generator is calculated as follows: [ 8.83 ] with: [ 8.84 ]
S | S | converter to 1.2 times the nominal generator current, the subtransient reactance X d " of the synchronous generator is calculated as follows: [ 8.83 ] with: [ 8.84 ] Example:
G,nom | G,nom | to 1.2 times the nominal generator current, the subtransient reactance X d " of the synchronous generator is calculated as follows: [ 8.83 ] with: [ 8.84 ] Example: S
1.2 times the nominal generator current, the subtransient reactance X d " of the synchronous generator is calculated as follows: [ 8.83 ] with: [ 8.84 ] Example: S G,nom
U | U | nominal generator current, the subtransient reactance X d " of the synchronous generator is calculated as follows: [ 8.83 ] with: [ 8.84 ] Example: S G,nom = 3 MVA
G,nom | G,nom | generator current, the subtransient reactance X d " of the synchronous generator is calculated as follows: [ 8.83 ] with: [ 8.84 ] Example: S G,nom = 3 MVA U
current, the subtransient reactance X d " of the synchronous generator is calculated as follows: [ 8.83 ] with: [ 8.84 ] Example: S G,nom = 3 MVA U G,nom
I | I | reactance X d " of the synchronous generator is calculated as follows: [ 8.83 ] with: [ 8.84 ] Example: S G,nom = 3 MVA U G,nom = 0.96 kV
Gnom | Gnom | X d " of the synchronous generator is calculated as follows: [ 8.83 ] with: [ 8.84 ] Example: S G,nom = 3 MVA U G,nom = 0.96 kV I
d " of the synchronous generator is calculated as follows: [ 8.83 ] with: [ 8.84 ] Example: S G,nom = 3 MVA U G,nom = 0.96 kV I Gnom
I | I | the synchronous generator is calculated as follows: [ 8.83 ] with: [ 8.84 ] Example: S G,nom = 3 MVA U G,nom = 0.96 kV I Gnom = 1.8 kA
k | k | synchronous generator is calculated as follows: [ 8.83 ] with: [ 8.84 ] Example: S G,nom = 3 MVA U G,nom = 0.96 kV I Gnom = 1.8 kA I
" = 2,2 kA | " = 2.2 kA | generator is calculated as follows: [ 8.83 ] with: [ 8.84 ] Example: S G,nom = 3 MVA U G,nom = 0.96 kV I Gnom = 1.8 kA I k
Z | Z | follows: [ 8.83 ] with: [ 8.84 ] Example: S G,nom = 3 MVA U G,nom = 0.96 kV I Gnom = 1.8 kA I k " = 2.2 kA
G | G | [ 8.83 ] with: [ 8.84 ] Example: S G,nom = 3 MVA U G,nom = 0.96 kV I Gnom = 1.8 kA I k " = 2.2 kA Z
8.83 ] with: [ 8.84 ] Example: S G,nom = 3 MVA U G,nom = 0.96 kV I Gnom = 1.8 kA I k " = 2.2 kA Z G
Bij verwaarlozing van de generatorweerstand volgt hieruit voor de subtransiënte reactantie: | Neglecting the generator resistance, this results in the following for the subtransient reactance: | [ 8.84 ] Example: S G,nom = 3 MVA U G,nom = 0.96 kV I Gnom = 1.8 kA I k " = 2.2 kA Z G = 0.256 Ω
x | x | kV I Gnom = 1.8 kA I k " = 2.2 kA Z G = 0.256 Ω Neglecting the generator resistance, this results in the following for the subtransient reactance:
d | d | I Gnom = 1.8 kA I k " = 2.2 kA Z G = 0.256 Ω Neglecting the generator resistance, this results in the following for the subtransient reactance: x
" = 0,83 pu | " = 0.83 pu | Gnom = 1.8 kA I k " = 2.2 kA Z G = 0.256 Ω Neglecting the generator resistance, this results in the following for the subtransient reactance: x d
. | . | I k " = 2.2 kA Z G = 0.256 Ω Neglecting the generator resistance, this results in the following for the subtransient reactance: x d " = 0.83 pu
Variabel toerental windturbine met een dubbelgevoede inductiegenerator (DFIG) | Variable speed wind turbine with a doubly-fed induction generator (DFIG) | k " = 2.2 kA Z G = 0.256 Ω Neglecting the generator resistance, this results in the following for the subtransient reactance: x d " = 0.83 pu .
Het windturbinesysteem van figuur 8.29 is voorzien van een dubbelgevoede synchrone generator (DFIG). Dit houdt in dat de stator direct gekoppeld is met het net en dat de rotorwikkeling via sleepringen is verbonden met een converter. Met name doordat de vermogenselektronische omzetter maar ongeveer een kwart van het totale vermogen hoeft te voeden, is dit concept erg populair geworden voor variabel toerental windturbines, want de verliezen in de converter zijn veel minder dan bij een systeem met een 'full-power' converter. Bovendien is de converter goedkoper. | The wind turbine system in figure 8.29 is equipped with a doubly-fed induction generator (DFIG). This means that the stator is directly connected to the grid and the rotor winding is connected to a converter via slip rings. Particularly because the power electronic converter only needs to supply about a quarter of the total power, this concept has become very popular for variable speed wind turbines, as the losses in the converter are much less than in a system with a 'full-power' converter. Additionally, the converter is cheaper. | Neglecting the generator resistance, this results in the following for the subtransient reactance: x d " = 0.83 pu . Variable speed wind turbine with a doubly-fed induction generator (DFIG)
Figuur 8.29 Variabel toerental windturbine met een dubbelgevoede synchrone generator | Figure 8.29 Variable speed wind turbine with a doubly-fed synchronous generator | become very popular for variable speed wind turbines, as the losses in the converter are much less than in a system with a 'full-power' converter. Additionally, the converter is cheaper.
De omzetter is een 'back-to-back' converter en bestaat uit twee converters met een gelijkstroomverbinding ertussen. De converter die is aangesloten op de rotorwikkelingen regelt het koppel, het toerental en de arbeidsfactor aan de statorklemmen. | The converter is a 'back-to-back' converter and consists of two converters with a direct current link between them. The converter connected to the rotor windings controls the torque, speed, and power factor at the stator terminals. | in the converter are much less than in a system with a 'full-power' converter. Additionally, the converter is cheaper. Figure 8.29 Variable speed wind turbine with a doubly-fed synchronous generator
Tijdens normaal bedrijf gedraagt de windturbine zich als een synchrone machine. Door regeling van de frequentie van de stroom door de rotorwikkeling kan de generator bij elke gewenst rotortoerental toch synchroon draaien. De rotorwikkeling wordt met een zodanige wisselstroom gevoed, dat het elektro­magnetisch veld in de luchtspleet het verschil tussen het rotor- en statorveld compenseert. | During normal operation, the wind turbine behaves like a synchronous machine. By regulating the frequency of the current through the rotor winding, the generator can still run synchronously at any desired rotor speed. The rotor winding is supplied with an alternating current in such a way that the electromagnetic field in the air gap compensates for the difference between the rotor and stator fields. | and consists of two converters with a direct current link between them. The converter connected to the rotor windings controls the torque, speed, and power factor at the stator terminals.
Figuur 8.30 Vermogensbalans windturbine met DFIG | Figure 8.30 Power balance of wind turbine with DFIG | rotor winding is supplied with an alternating current in such a way that the electromagnetic field in the air gap compensates for the difference between the rotor and stator fields.
Het mechanische vermogen wordt analoog aan vergelijking 8.81 berekend als functie van de windsnelheid. Onderstaande vergelijking beschrijft de relatie tussen het mechanische en het totale elektrische vermogen. | The mechanical power is calculated analogously to equation 8.81 as a function of wind speed. The following equation describes the relationship between the mechanical and the total electrical power. | such a way that the electromagnetic field in the air gap compensates for the difference between the rotor and stator fields. Figure 8.30 Power balance of wind turbine with DFIG
[ | [ | DFIG The mechanical power is calculated analogously to equation 8.81 as a function of wind speed. The following equation describes the relationship between the mechanical and the total electrical power.
8.85 | 8.85 | The mechanical power is calculated analogously to equation 8.81 as a function of wind speed. The following equation describes the relationship between the mechanical and the total electrical power. [
] | ] | mechanical power is calculated analogously to equation 8.81 as a function of wind speed. The following equation describes the relationship between the mechanical and the total electrical power. [ 8.85
In deze vergelijking vertegenwoordigt het rendement de omzetting van het totale systeem, waaronder de versnellingsbak, de generator en de converter. Het elektrische vermogen van de windturbine is gelijk aan het verschil van het statorvermogen en het rotorvermogen, ervan uitgaande dat bij positieve waarden de stator elektrisch vermogen levert en de rotor elektrisch vermogen opneemt: | In this equation, the efficiency represents the conversion of the entire system, including the gearbox, the generator, and the converter. The electrical power of the wind turbine is equal to the difference between the stator power and the rotor power, assuming that for positive values, the stator supplies electrical power and the rotor absorbs electrical power: | power is calculated analogously to equation 8.81 as a function of wind speed. The following equation describes the relationship between the mechanical and the total electrical power. [ 8.85 ]
[ | [ | turbine is equal to the difference between the stator power and the rotor power, assuming that for positive values, the stator supplies electrical power and the rotor absorbs electrical power:
8.86 | 8.86 | is equal to the difference between the stator power and the rotor power, assuming that for positive values, the stator supplies electrical power and the rotor absorbs electrical power: [
] | ] | equal to the difference between the stator power and the rotor power, assuming that for positive values, the stator supplies electrical power and the rotor absorbs electrical power: [ 8.86
De verdeling tussen het statorvermogen en het rotorvermogen wordt bepaald door de slip | The distribution between the stator power and the rotor power is determined by the slip. | to the difference between the stator power and the rotor power, assuming that for positive values, the stator supplies electrical power and the rotor absorbs electrical power: [ 8.86 ]
s | s | values, the stator supplies electrical power and the rotor absorbs electrical power: [ 8.86 ] The distribution between the stator power and the rotor power is determined by the slip.
. | . | the stator supplies electrical power and the rotor absorbs electrical power: [ 8.86 ] The distribution between the stator power and the rotor power is determined by the slip. s
[ | [ | stator supplies electrical power and the rotor absorbs electrical power: [ 8.86 ] The distribution between the stator power and the rotor power is determined by the slip. s .
8.87 | 8.87 | supplies electrical power and the rotor absorbs electrical power: [ 8.86 ] The distribution between the stator power and the rotor power is determined by the slip. s . [
] | ] | electrical power and the rotor absorbs electrical power: [ 8.86 ] The distribution between the stator power and the rotor power is determined by the slip. s . [ 8.87
Bij een door voldoende wind aangedreven windturbine draait de generator 'boven-synchroon' en is de slip negatief. Bijvoorbeeld bij een slip van –0,3 (–30%) is de rotorsnelheid 1,3 maal het synchrone toerental. Het statorvermogen is dan 0,77 maal | In a wind turbine driven by sufficient wind, the generator operates 'above synchronous' and the slip is negative. For example, with a slip of -0.3 (-30%), the rotor speed is 1.3 times the synchronous speed. The stator power is then 0.77 times | power and the rotor absorbs electrical power: [ 8.86 ] The distribution between the stator power and the rotor power is determined by the slip. s . [ 8.87 ]
P | P | synchronous' and the slip is negative. For example, with a slip of -0.3 (-30%), the rotor speed is 1.3 times the synchronous speed. The stator power is then 0.77 times
el | el | and the slip is negative. For example, with a slip of -0.3 (-30%), the rotor speed is 1.3 times the synchronous speed. The stator power is then 0.77 times P
en het rotorvermogen is dan –0,23 maal | and the rotor power is then -0.23 times | the slip is negative. For example, with a slip of -0.3 (-30%), the rotor speed is 1.3 times the synchronous speed. The stator power is then 0.77 times P el
P | P | slip of -0.3 (-30%), the rotor speed is 1.3 times the synchronous speed. The stator power is then 0.77 times P el and the rotor power is then -0.23 times
el | el | of -0.3 (-30%), the rotor speed is 1.3 times the synchronous speed. The stator power is then 0.77 times P el and the rotor power is then -0.23 times P
. Dat betekent dus dat bij vol vermogen ongeveer drie kwart van het windturbinevermogen uit het statorcircuit komt en een kwart uit het rotorcircuit. In nullast is de slip nul en is zowel het stator- als het rotorvermogen nul. | That means that at full power, approximately three-quarters of the wind turbine power comes from the stator circuit and one-quarter from the rotor circuit. At no load, the slip is zero, and both the stator and rotor power are zero. | -0.3 (-30%), the rotor speed is 1.3 times the synchronous speed. The stator power is then 0.77 times P el and the rotor power is then -0.23 times P el
In geval van een kortsluiting in het net draagt de windturbine bij aan deze kortsluiting en is de statorstroom groot. Als gevolg zal ook de rotorstroom groot worden. Ter bescherming van de vermogenselektronica in de converter wordt onmiddellijk het rotorcircuit kortgesloten. Als gevolg gedraagt de generator zich tijdens kortsluiting als een asynchrone machine. | In the event of a short circuit in the grid, the wind turbine contributes to this short circuit, and the stator current becomes large. Consequently, the rotor current will also become large. To protect the power electronics in the converter, the rotor circuit is immediately short-circuited. As a result, the generator behaves as an asynchronous machine during the short circuit. | wind turbine power comes from the stator circuit and one-quarter from the rotor circuit. At no load, the slip is zero, and both the stator and rotor power are zero.
Figuur 8.31 Model van een variabel toerental windturbine met een dubbelgevoede inductiegenerator | Figure 8.31 Model of a variable speed wind turbine with a doubly-fed induction generator | become large. To protect the power electronics in the converter, the rotor circuit is immediately short-circuited. As a result, the generator behaves as an asynchronous machine during the short circuit.
Figuur 8.31 toont een model van deze windturbine. De generator is in de gondel aangesloten via een aantal parallelle kabels: separaat voor het statorcircuit en voor het rotorcircuit. Hierbij is aangenomen dat de transformator zich in de mastvoet bevindt. Indien de transformator zich in de gondel zou bevinden, zouden de parallelle kabels vervallen. De transformator is een niet-regelbare driewikkelingstransformator (Dyn5yn5) die het rotor- en statorcircuit van de dubbelgevoede asynchrone generator voedt. De generator is in het model gesplitst in het rotor- en de statorcircuit. De stator is gemodelleerd met het model van een synchrone generator. De rotor is aangesloten via een converter. Het rotorvermogen is gemodelleerd met een belasting van constant vermogen. | Figure 8.31 shows a model of this wind turbine. The generator is connected in the nacelle via several parallel cables: separately for the stator circuit and the rotor circuit. It is assumed that the transformer is located at the base of the mast. If the transformer were located in the nacelle, the parallel cables would be unnecessary. The transformer is a non-regulable three-winding transformer (Dyn5yn5) that feeds the rotor and stator circuits of the doubly-fed asynchronous generator. In the model, the generator is split into the rotor and stator circuits. The stator is modeled with the model of a synchronous generator. The rotor is connected via a converter. The rotor power is modeled with a constant power load. | immediately short-circuited. As a result, the generator behaves as an asynchronous machine during the short circuit. Figure 8.31 Model of a variable speed wind turbine with a doubly-fed induction generator
Het actieve vermogen dat de generator levert wordt berekend met vergelijkingen 8.81 en 8.85. De verdeling van de actieve vermogens die de stator en rotor leveren is functie van de slip (Figuur 8.23) en wordt berekend met vergelijking 8.87. | The active power delivered by the generator is calculated using equations 8.81 and 8.85. The distribution of the active powers delivered by the stator and rotor depends on the slip (Figure 8.23) and is calculated using equation 8.87. | stator circuits. The stator is modeled with the model of a synchronous generator. The rotor is connected via a converter. The rotor power is modeled with a constant power load.
Aangenomen wordt dat de converter geen blindvermogen levert, zodat het totale blindvermogen wordt geleverd door de stator van de generator. De waarde volgt uit de cos(φ), ervan uitgaande dat de generator blindvermogen levert: | It is assumed that the converter does not supply reactive power, so the total reactive power is supplied by the stator of the generator. The value follows from the cos(φ), assuming that the generator supplies reactive power: | calculated using equations 8.81 and 8.85. The distribution of the active powers delivered by the stator and rotor depends on the slip (Figure 8.23) and is calculated using equation 8.87.
[ | [ | not supply reactive power, so the total reactive power is supplied by the stator of the generator. The value follows from the cos(φ), assuming that the generator supplies reactive power:
8.88 | 8.88 | supply reactive power, so the total reactive power is supplied by the stator of the generator. The value follows from the cos(φ), assuming that the generator supplies reactive power: [
] | ] | reactive power, so the total reactive power is supplied by the stator of the generator. The value follows from the cos(φ), assuming that the generator supplies reactive power: [ 8.88
Tijdens een kortsluiting schakelt een beveiliging (crow bar) direct het rotorcircuit van de generator kort, waardoor het karakter van de machine overgaat van een dubbelgevoede naar een normale asynchrone generator, die bijdraagt aan de kortsluitstroom. De converter zal niet bijdragen aan de kortsluitstroom. Het gedrag tijdens kortsluiting wordt voornamelijk bepaald door de subtransiënte impedantie | During a short circuit, a protection device (crowbar) directly shorts the rotor circuit of the generator, causing the machine's character to change from a doubly-fed to a normal asynchronous generator, which contributes to the short-circuit current. The converter will not contribute to the short-circuit current. The behavior during a short circuit is primarily determined by the subtransient impedance. | power, so the total reactive power is supplied by the stator of the generator. The value follows from the cos(φ), assuming that the generator supplies reactive power: [ 8.88 ]
z | z | asynchronous generator, which contributes to the short-circuit current. The converter will not contribute to the short-circuit current. The behavior during a short circuit is primarily determined by the subtransient impedance.
d | d | generator, which contributes to the short-circuit current. The converter will not contribute to the short-circuit current. The behavior during a short circuit is primarily determined by the subtransient impedance. z
" | " | which contributes to the short-circuit current. The converter will not contribute to the short-circuit current. The behavior during a short circuit is primarily determined by the subtransient impedance. z d
, waarvan de waarde kan worden berekend uit de maximale kortsluitstroombijdrage: | , the value of which can be calculated from the maximum short-circuit current contribution: | contributes to the short-circuit current. The converter will not contribute to the short-circuit current. The behavior during a short circuit is primarily determined by the subtransient impedance. z d "
[ | [ | The behavior during a short circuit is primarily determined by the subtransient impedance. z d " , the value of which can be calculated from the maximum short-circuit current contribution:
8.89 | 8.89 | behavior during a short circuit is primarily determined by the subtransient impedance. z d " , the value of which can be calculated from the maximum short-circuit current contribution: [
] | ] | during a short circuit is primarily determined by the subtransient impedance. z d " , the value of which can be calculated from the maximum short-circuit current contribution: [ 8.89
Hierna wordt de verdeling over | Hereafter, the distribution over | a short circuit is primarily determined by the subtransient impedance. z d " , the value of which can be calculated from the maximum short-circuit current contribution: [ 8.89 ]
r | r | primarily determined by the subtransient impedance. z d " , the value of which can be calculated from the maximum short-circuit current contribution: [ 8.89 ] Hereafter, the distribution over
g | g | determined by the subtransient impedance. z d " , the value of which can be calculated from the maximum short-circuit current contribution: [ 8.89 ] Hereafter, the distribution over r
en | en | by the subtransient impedance. z d " , the value of which can be calculated from the maximum short-circuit current contribution: [ 8.89 ] Hereafter, the distribution over r g
x | x | the subtransient impedance. z d " , the value of which can be calculated from the maximum short-circuit current contribution: [ 8.89 ] Hereafter, the distribution over r g en
d | d | subtransient impedance. z d " , the value of which can be calculated from the maximum short-circuit current contribution: [ 8.89 ] Hereafter, the distribution over r g en x
" | " | impedance. z d " , the value of which can be calculated from the maximum short-circuit current contribution: [ 8.89 ] Hereafter, the distribution over r g en x d
volgens vergelijking 8.80 berekend uit de R/X-verhouding van de generator. | according to equation 8.80 calculated from the R/X ratio of the generator. | z d " , the value of which can be calculated from the maximum short-circuit current contribution: [ 8.89 ] Hereafter, the distribution over r g en x d "