## Sheet1
Original Text | Translated Text | Previous Context
Netcomponenten | Netcomponenten
In hoofdstuk 4 worden de meest gebruikte componenten in de MS- en LS-netten beschreven. Hieronder vallen onder andere kabels, moffen, transformatoren, smoorspoelen, vermogenschakelaars, schakelinstallaties en smeltveiligheden. | Chapter 4 describes the most commonly used components in the medium-voltage (MV) and low-voltage (LV) networks. These include cables, joints, transformers, reactors, circuit breakers, switchgear, and fuses. | Netcomponenten
4 Netcomponenten | 4 Network Components | Netcomponenten Chapter 4 describes the most commonly used components in the medium-voltage (MV) and low-voltage (LV) networks. These include cables, joints, transformers, reactors, circuit breakers, switchgear, and fuses.
4.1 Kabels | 4.1 Cables | Chapter 4 describes the most commonly used components in the medium-voltage (MV) and low-voltage (LV) networks. These include cables, joints, transformers, reactors, circuit breakers, switchgear, and fuses. 4 Network Components
4.1.1 Constructie MS-kabels | 4.1.1 Construction of MV Cables | describes the most commonly used components in the medium-voltage (MV) and low-voltage (LV) networks. These include cables, joints, transformers, reactors, circuit breakers, switchgear, and fuses. 4 Network Components 4.1 Cables
4.1.2 Constructie LS-kabels | 4.1.2 Construction of LV Cables | components in the medium-voltage (MV) and low-voltage (LV) networks. These include cables, joints, transformers, reactors, circuit breakers, switchgear, and fuses. 4 Network Components 4.1 Cables 4.1.1 Construction of MV Cables
4.1.3 Verbinden van de afschermingen van enkeladerige MS-kabels | 4.1.3 Connecting the shields of single-core MV cables | and low-voltage (LV) networks. These include cables, joints, transformers, reactors, circuit breakers, switchgear, and fuses. 4 Network Components 4.1 Cables 4.1.1 Construction of MV Cables 4.1.2 Construction of LV Cables
4.1.4 Impedanties van kabels | 4.1.4 Impedances of cables | transformers, reactors, circuit breakers, switchgear, and fuses. 4 Network Components 4.1 Cables 4.1.1 Construction of MV Cables 4.1.2 Construction of LV Cables 4.1.3 Connecting the shields of single-core MV cables
4.1.5 Stroombelastbaarheid | 4.1.5 Current Carrying Capacity | switchgear, and fuses. 4 Network Components 4.1 Cables 4.1.1 Construction of MV Cables 4.1.2 Construction of LV Cables 4.1.3 Connecting the shields of single-core MV cables 4.1.4 Impedances of cables
4.1.6 Belastbaarheid bij kortsluitstromen | 4.1.6 Short-Circuit Current Carrying Capacity | Network Components 4.1 Cables 4.1.1 Construction of MV Cables 4.1.2 Construction of LV Cables 4.1.3 Connecting the shields of single-core MV cables 4.1.4 Impedances of cables 4.1.5 Current Carrying Capacity
4.2 Moffen | 4.2 Splices | Construction of MV Cables 4.1.2 Construction of LV Cables 4.1.3 Connecting the shields of single-core MV cables 4.1.4 Impedances of cables 4.1.5 Current Carrying Capacity 4.1.6 Short-Circuit Current Carrying Capacity
4.3 Transformatoren | 4.3 Transformers | MV Cables 4.1.2 Construction of LV Cables 4.1.3 Connecting the shields of single-core MV cables 4.1.4 Impedances of cables 4.1.5 Current Carrying Capacity 4.1.6 Short-Circuit Current Carrying Capacity 4.2 Splices
4.4 Smoorspoelen | 4.4 Chokes | 4.1.2 Construction of LV Cables 4.1.3 Connecting the shields of single-core MV cables 4.1.4 Impedances of cables 4.1.5 Current Carrying Capacity 4.1.6 Short-Circuit Current Carrying Capacity 4.2 Splices 4.3 Transformers
4.5 Vermogenschakelaars | 4.5 Circuit Breakers | of LV Cables 4.1.3 Connecting the shields of single-core MV cables 4.1.4 Impedances of cables 4.1.5 Current Carrying Capacity 4.1.6 Short-Circuit Current Carrying Capacity 4.2 Splices 4.3 Transformers 4.4 Chokes
4.6 Schakelinstallaties | 4.6 Switchgear | 4.1.3 Connecting the shields of single-core MV cables 4.1.4 Impedances of cables 4.1.5 Current Carrying Capacity 4.1.6 Short-Circuit Current Carrying Capacity 4.2 Splices 4.3 Transformers 4.4 Chokes 4.5 Circuit Breakers
4.7 Smeltveiligheden | 4.7 Fuses | the shields of single-core MV cables 4.1.4 Impedances of cables 4.1.5 Current Carrying Capacity 4.1.6 Short-Circuit Current Carrying Capacity 4.2 Splices 4.3 Transformers 4.4 Chokes 4.5 Circuit Breakers 4.6 Switchgear
4.8 I | 4.8 Instruments | of single-core MV cables 4.1.4 Impedances of cables 4.1.5 Current Carrying Capacity 4.1.6 Short-Circuit Current Carrying Capacity 4.2 Splices 4.3 Transformers 4.4 Chokes 4.5 Circuit Breakers 4.6 Switchgear 4.7 Fuses
s | s | MV cables 4.1.4 Impedances of cables 4.1.5 Current Carrying Capacity 4.1.6 Short-Circuit Current Carrying Capacity 4.2 Splices 4.3 Transformers 4.4 Chokes 4.5 Circuit Breakers 4.6 Switchgear 4.7 Fuses 4.8 Instruments
-begrenzers | -limiters | cables 4.1.4 Impedances of cables 4.1.5 Current Carrying Capacity 4.1.6 Short-Circuit Current Carrying Capacity 4.2 Splices 4.3 Transformers 4.4 Chokes 4.5 Circuit Breakers 4.6 Switchgear 4.7 Fuses 4.8 Instruments s
4.9 Toepassing van vermogenselektronica | 4.9 Application of Power Electronics | 4.1.4 Impedances of cables 4.1.5 Current Carrying Capacity 4.1.6 Short-Circuit Current Carrying Capacity 4.2 Splices 4.3 Transformers 4.4 Chokes 4.5 Circuit Breakers 4.6 Switchgear 4.7 Fuses 4.8 Instruments s -limiters
4 Netcomponenten | 4 Network Components | Current Carrying Capacity 4.1.6 Short-Circuit Current Carrying Capacity 4.2 Splices 4.3 Transformers 4.4 Chokes 4.5 Circuit Breakers 4.6 Switchgear 4.7 Fuses 4.8 Instruments s -limiters 4.9 Application of Power Electronics
De belangrijkste componenten in MS- en LS-netten zijn kabels, transformatoren en schakelinstallaties. Bovengrondse lijnen komen in Nederland op deze spanningsniveaus bijna niet voor en worden daarom niet behandeld. Dit hoofdstuk geeft een overzicht van deze meest gebruikte componenten. De modellering en het gedrag in loadflow- en kortsluitberekeningen komt in latere hoofdstukken aan de orde. | The main components in medium-voltage (MV) and low-voltage (LV) networks are cables, transformers, and switchgear. Overhead lines are almost non-existent at these voltage levels in the Netherlands and are therefore not covered. This chapter provides an overview of these most commonly used components. The modeling and behavior in load flow and short-circuit calculations will be discussed in later chapters. | 4.1.6 Short-Circuit Current Carrying Capacity 4.2 Splices 4.3 Transformers 4.4 Chokes 4.5 Circuit Breakers 4.6 Switchgear 4.7 Fuses 4.8 Instruments s -limiters 4.9 Application of Power Electronics 4 Network Components
4.1 Kabels | 4.1 Cables | therefore not covered. This chapter provides an overview of these most commonly used components. The modeling and behavior in load flow and short-circuit calculations will be discussed in later chapters.
Kabels zijn in vele typen en uitvoeringsvormen verkrijgbaar. Alle kabels bestaan uit 1, 3 of 4 aders (geleiders met isolatie), een afscherming en een buitenmantel. Afhankelijk van het spanningsniveau en de toepassing zijn er grote verschillen in de constructie van de kabel. Dit hoofdstuk behandelt de meest toegepaste kabels voor LS- distributienetten en voor MS-transport- en -distributienetten. | Cables are available in many types and configurations. All cables consist of 1, 3, or 4 cores (conductors with insulation), a shielding, and an outer sheath. Depending on the voltage level and application, there are significant differences in the construction of the cable. This chapter covers the most commonly used cables for low-voltage distribution networks and medium-voltage transport and distribution networks. | covered. This chapter provides an overview of these most commonly used components. The modeling and behavior in load flow and short-circuit calculations will be discussed in later chapters. 4.1 Cables
4.1.1 Constructie MS-kabels | 4.1.1 Construction of MV Cables | and application, there are significant differences in the construction of the cable. This chapter covers the most commonly used cables for low-voltage distribution networks and medium-voltage transport and distribution networks.
In de MS-netten worden meestal kabels met drie aders toegepast. Een ader bestaat uit een geleider van koper of aluminium, die wordt omgeven door geleiderscherm, isolatie en aderscherm. | In the MV networks, cables with three conductors are usually used. A conductor consists of a copper or aluminum conductor, which is surrounded by a conductor screen, insulation, and a conductor shield. | differences in the construction of the cable. This chapter covers the most commonly used cables for low-voltage distribution networks and medium-voltage transport and distribution networks. 4.1.1 Construction of MV Cables
Figuur 4.1 Het samenslaan van een koperen geleider | Figure 4.1 The splicing of a copper conductor | MV networks, cables with three conductors are usually used. A conductor consists of a copper or aluminum conductor, which is surrounded by a conductor screen, insulation, and a conductor shield.
De geleider kan zijn opgebouwd uit meerdere draden van kleine doorsnede, die compact zijn ‘geslagen’ tot een dikke geleider van de gewenste geleiderdoorsnede. Indien de geleider van aluminium is, wordt deze ook wel ‘massief’ uitgevoerd met een enkele geleider van de gewenste geleiderdoorsnede. Vanwege de buigzaamheid worden massieve geleiders in drieaderige kabels tot een geleiderdoorsnede 240 mm | The conductor can be composed of multiple small cross-section wires, which are compactly 'stranded' into a thick conductor of the desired cross-section. If the conductor is made of aluminum, it is often 'solid' with a single conductor of the desired cross-section. Due to flexibility, solid conductors in three-core cables are used up to a conductor cross-section of 240 mm. | used. A conductor consists of a copper or aluminum conductor, which is surrounded by a conductor screen, insulation, and a conductor shield. Figure 4.1 The splicing of a copper conductor
2 | 2 | it is often 'solid' with a single conductor of the desired cross-section. Due to flexibility, solid conductors in three-core cables are used up to a conductor cross-section of 240 mm.
toegepast. Bij enkeladerige kabels worden massieve geleiders tot een geleiderdoorsnede 800 mm | applied. In single-core cables, solid conductors are used up to a conductor cross-section of 800 mm. | is often 'solid' with a single conductor of the desired cross-section. Due to flexibility, solid conductors in three-core cables are used up to a conductor cross-section of 240 mm. 2
2 | 2 | in three-core cables are used up to a conductor cross-section of 240 mm. 2 applied. In single-core cables, solid conductors are used up to a conductor cross-section of 800 mm.
toegepast. Bij grotere geleiderdoorsneden worden geslagen geleiders toegepast. | applied. For larger conductor cross-sections, stranded conductors are used. | three-core cables are used up to a conductor cross-section of 240 mm. 2 applied. In single-core cables, solid conductors are used up to a conductor cross-section of 800 mm. 2
Figuur 4.2 Voorbeeld van een GPLK kabel (links) en een XLPE kabel (rechts) | Figure 4.2 Example of a GPLK cable (left) and an XLPE cable (right) | of 240 mm. 2 applied. In single-core cables, solid conductors are used up to a conductor cross-section of 800 mm. 2 applied. For larger conductor cross-sections, stranded conductors are used.
Het geleiderscherm en het aderscherm worden bij kabels voor MS-niveau en hoger toegepast om het elektrische veld in de isolatie homogeen te verdelen. Er kunnen namelijk oneffenheden voorkomen op de geleider of de afscherming, waardoor het elektrische veld lokaal vrij groot kan worden. Dit kan kleine ontladingen veroorzaken, waardoor de kabel snel veroudert. Om die oneffenheden op te heffen wordt een scherm, bestaande uit een halfgeleidende laag, om de geleider en om de isolatie aangebracht, zodat het veld zich in de isolatie homogeen zal verdelen. De aldus geïsoleerde geleiders worden aders genoemd en deze worden samengeslagen tot drie compact gebundelde aders. | The conductor screen and the insulation screen are applied in cables for medium voltage (MV) level and higher to evenly distribute the electric field in the insulation. Irregularities can occur on the conductor or the shielding, causing the electric field to become locally quite large. This can cause small discharges, leading to rapid aging of the cable. To eliminate these irregularities, a screen consisting of a semiconductive layer is applied around the conductor and the insulation, ensuring the field is evenly distributed within the insulation. The thus insulated conductors are called cores, and these are twisted together into three compactly bundled cores. | to a conductor cross-section of 800 mm. 2 applied. For larger conductor cross-sections, stranded conductors are used. Figure 4.2 Example of a GPLK cable (left) and an XLPE cable (right)
De samengeslagen aders zijn afgeschermd met een scherm dat in staat is om langdurig kleine vereffeningstromen en kortstondig een kortsluitstroom te voeren. | The twisted cores are shielded with a screen that is capable of carrying small equalizing currents for extended periods and short-circuit currents for brief periods. | conductor and the insulation, ensuring the field is evenly distributed within the insulation. The thus insulated conductors are called cores, and these are twisted together into three compactly bundled cores.
De meest gebruikte typen hebben een massa-geïmpregneerde papierisolatie of een kunststofisolatie. Een voorbeeld van een massa-geïmpregneerde kabel is het type GPLK (Gepantserde Papier-Lood Kabel) voor geleiderdoorsneden tot 300 mm | The most commonly used types have mass-impregnated paper insulation or plastic insulation. An example of a mass-impregnated cable is the type GPLK (Armored Paper-Lead Cable) for conductor cross-sections up to 300 mm². | into three compactly bundled cores. The twisted cores are shielded with a screen that is capable of carrying small equalizing currents for extended periods and short-circuit currents for brief periods.
2 | 2 | commonly used types have mass-impregnated paper insulation or plastic insulation. An example of a mass-impregnated cable is the type GPLK (Armored Paper-Lead Cable) for conductor cross-sections up to 300 mm².
. Deze kabels worden niet meer gebruikt bij aanpassingen in het MS-net. De productie ervan is gestopt in 2005. Tegenwoordig worden kabels met kunststof isolatie van XLPE (Cross-Linked Poly-Etylene, vernet polyetheen) gebruikt. De belangrijkste kenmerken van beide typen zijn (de nummering verwijst naar figuur 4.2): | These cables are no longer used in modifications to the medium voltage network. Their production was stopped in 2005. Nowadays, cables with plastic insulation made of XLPE (Cross-Linked Polyethylene) are used. The main characteristics of both types are (the numbering refers to figure 4.2): | used types have mass-impregnated paper insulation or plastic insulation. An example of a mass-impregnated cable is the type GPLK (Armored Paper-Lead Cable) for conductor cross-sections up to 300 mm². 2
GPLK | GPLK | production was stopped in 2005. Nowadays, cables with plastic insulation made of XLPE (Cross-Linked Polyethylene) are used. The main characteristics of both types are (the numbering refers to figure 4.2):
XLPE | XLPE | was stopped in 2005. Nowadays, cables with plastic insulation made of XLPE (Cross-Linked Polyethylene) are used. The main characteristics of both types are (the numbering refers to figure 4.2): GPLK
1. koperen of aluminium geleiders | 1. copper or aluminum conductors | stopped in 2005. Nowadays, cables with plastic insulation made of XLPE (Cross-Linked Polyethylene) are used. The main characteristics of both types are (the numbering refers to figure 4.2): GPLK XLPE
2. aderisolatie (massa-geïmpregneerd) | 2. core insulation (mass-impregnated) | with plastic insulation made of XLPE (Cross-Linked Polyethylene) are used. The main characteristics of both types are (the numbering refers to figure 4.2): GPLK XLPE 1. copper or aluminum conductors
3. gordelisolatie (massa-geïmpregneerd) | 3. belt insulation (mass-impregnated) | of XLPE (Cross-Linked Polyethylene) are used. The main characteristics of both types are (the numbering refers to figure 4.2): GPLK XLPE 1. copper or aluminum conductors 2. core insulation (mass-impregnated)
4. afscherming van lood (geëxtrudeerd) | 4. lead shielding (extruded) | are used. The main characteristics of both types are (the numbering refers to figure 4.2): GPLK XLPE 1. copper or aluminum conductors 2. core insulation (mass-impregnated) 3. belt insulation (mass-impregnated)
5. tussenlaag van gebitumeerd papier | 5. intermediate layer of bituminized paper | characteristics of both types are (the numbering refers to figure 4.2): GPLK XLPE 1. copper or aluminum conductors 2. core insulation (mass-impregnated) 3. belt insulation (mass-impregnated) 4. lead shielding (extruded)
6. tussenlaag van kunststofgaren of jute | 6. intermediate layer of synthetic yarn or jute | numbering refers to figure 4.2): GPLK XLPE 1. copper or aluminum conductors 2. core insulation (mass-impregnated) 3. belt insulation (mass-impregnated) 4. lead shielding (extruded) 5. intermediate layer of bituminized paper
7. wapening van verzinkt staalband | 7. reinforcement of galvanized steel tape | copper or aluminum conductors 2. core insulation (mass-impregnated) 3. belt insulation (mass-impregnated) 4. lead shielding (extruded) 5. intermediate layer of bituminized paper 6. intermediate layer of synthetic yarn or jute
8. buitenmantel van kunststofgaren of jute en bitumen of PVC of PE | 8. outer sheath of synthetic yarn or jute and bitumen or PVC or PE | insulation (mass-impregnated) 3. belt insulation (mass-impregnated) 4. lead shielding (extruded) 5. intermediate layer of bituminized paper 6. intermediate layer of synthetic yarn or jute 7. reinforcement of galvanized steel tape
1. koperen of aluminium geleiders, geslagen of massief | 1. copper or aluminum conductors, stranded or solid | bituminized paper 6. intermediate layer of synthetic yarn or jute 7. reinforcement of galvanized steel tape 8. outer sheath of synthetic yarn or jute and bitumen or PVC or PE
2. aderscherm (halfgeleidende laag) | 2. conductor screen (semiconductive layer) | or jute 7. reinforcement of galvanized steel tape 8. outer sheath of synthetic yarn or jute and bitumen or PVC or PE 1. copper or aluminum conductors, stranded or solid
3. cross-linked polyethyleen isolatie | 3. cross-linked polyethylene insulation | galvanized steel tape 8. outer sheath of synthetic yarn or jute and bitumen or PVC or PE 1. copper or aluminum conductors, stranded or solid 2. conductor screen (semiconductive layer)
4. aderscherm (halfgeleidende laag) | 4. conductor screen (semiconductive layer) | outer sheath of synthetic yarn or jute and bitumen or PVC or PE 1. copper or aluminum conductors, stranded or solid 2. conductor screen (semiconductive layer) 3. cross-linked polyethylene insulation
5. afscherming van koperdraden | 5. shielding of copper wires | or jute and bitumen or PVC or PE 1. copper or aluminum conductors, stranded or solid 2. conductor screen (semiconductive layer) 3. cross-linked polyethylene insulation 4. conductor screen (semiconductive layer)
6. zwelband tegen indringing van vocht | 6. swelling tape against moisture ingress | PVC or PE 1. copper or aluminum conductors, stranded or solid 2. conductor screen (semiconductive layer) 3. cross-linked polyethylene insulation 4. conductor screen (semiconductive layer) 5. shielding of copper wires
7. polyethyleen of PVC buitenmantel | 7. polyethylene or PVC outer sheath | aluminum conductors, stranded or solid 2. conductor screen (semiconductive layer) 3. cross-linked polyethylene insulation 4. conductor screen (semiconductive layer) 5. shielding of copper wires 6. swelling tape against moisture ingress
De GPLK kabels zijn in het verleden veel toegepast en zijn nog alom tegenwoordig in de MS-transport- en distributienetten. De aders in GPLK-kabels hebben een isolatie die is opgebouwd uit papierlagen die geïmpregneerd zijn met een mengsel van olie, hars en was (de massa). Bij hoge temperaturen wordt dit mengsel vloeibaar, waardoor de geleidertemperatuur gelimiteerd is op 50 °C om beschadiging en versnelde veroudering van de isolatie te voorkomen. De aders van GPLK-kabels zijn omsloten door een loodmantel. De kabels zijn versterkt (gewapend) met verzinkt staalband en tenslotte voorzien van een buitenmantel. | The GPLK cables have been widely used in the past and are still prevalent in medium voltage (MV) transport and distribution networks. The conductors in GPLK cables have insulation made up of layers of paper impregnated with a mixture of oil, resin, and wax (the mass). At high temperatures, this mixture becomes liquid, which limits the conductor temperature to 50°C to prevent damage and accelerated aging of the insulation. The conductors of GPLK cables are enclosed by a lead sheath. The cables are reinforced (armored) with galvanized steel tape and finally provided with an outer sheath. | conductor screen (semiconductive layer) 3. cross-linked polyethylene insulation 4. conductor screen (semiconductive layer) 5. shielding of copper wires 6. swelling tape against moisture ingress 7. polyethylene or PVC outer sheath
De isolatie van de aders van kunststof MS-kabels bestaat uit vaste XLPE met een halfgeleidende laag aan geleider- en afschermingzijde. De halfgeleidende laag zorgt voor veldsturing om een homogeen elektrisch veld te verkrijgen. Kunststof kabels hebben een koperdraadscherm voor het voeren van kleine vereffeningstromen en kortstondige kortsluitstromen en het fungeert tevens als wapening. Kabels met XLPE-isolatie mogen tot een geleidertemperatuur van 90 °C belast worden, waardoor deze kabel redelijk goed bestand is tegen zware belastingen. Ondergronds gelegde XLPE-kabels worden echter meestal niet langdurig op hun maximum geleidertemperatuur belast, omdat dan de buitenmanteltemperatuur te hoog zou worden, waardoor uitdroging van de bodem optreedt. Dit wordt in paragraaf 4.1.5 over de stroombelastbaarheid behandeld. Bovengronds gemonteerde kabels hebben het probleem van gronduitdroging niet en kunnen tot hun maximum temperatuur belast worden. Door de materiaaleigenschappen van de kunststof isolatie is deze kabel minder goed bestand tegen transiënte overspanningen dan de papiergeïsoleerde kabel. | The insulation of the cores of plastic medium-voltage cables consists of solid XLPE with a semiconducting layer on both the conductor and shielding sides. The semiconducting layer ensures field control to achieve a homogeneous electric field. Plastic cables have a copper wire screen for carrying small equalization currents and short-term short-circuit currents, and it also serves as reinforcement. Cables with XLPE insulation can be loaded up to a conductor temperature of 90°C, making these cables fairly resistant to heavy loads. However, underground XLPE cables are usually not loaded to their maximum conductor temperature for extended periods, as the outer sheath temperature would become too high, leading to soil drying. This is addressed in section 4.1.5 on current-carrying capacity. Overhead-mounted cables do not have the issue of soil drying and can be loaded to their maximum temperature. Due to the material properties of the plastic insulation, these cables are less resistant to transient overvoltages than paper-insulated cables. | of the insulation. The conductors of GPLK cables are enclosed by a lead sheath. The cables are reinforced (armored) with galvanized steel tape and finally provided with an outer sheath.
Kabels worden beschreven met een typeaanduiding die is opgebouwd uit een aantal codes, die in een vaste volgorde achter elkaar worden geplaatst. De opbouw van de aanduiding is weergegeven in tabel 4.1. | Cables are described with a type designation that is composed of several codes, which are placed in a fixed order. The structure of the designation is shown in Table 4.1. | soil drying and can be loaded to their maximum temperature. Due to the material properties of the plastic insulation, these cables are less resistant to transient overvoltages than paper-insulated cables.
Tabel 4.1 Codering typeaanduiding kabels | Table 4.1 Coding of cable type designation | Cables are described with a type designation that is composed of several codes, which are placed in a fixed order. The structure of the designation is shown in Table 4.1.
Onderdeel | Onderdeel | that is composed of several codes, which are placed in a fixed order. The structure of the designation is shown in Table 4.1. Table 4.1 Coding of cable type designation
Code | Code | is composed of several codes, which are placed in a fixed order. The structure of the designation is shown in Table 4.1. Table 4.1 Coding of cable type designation Onderdeel
Betekenis | Betekenis | composed of several codes, which are placed in a fixed order. The structure of the designation is shown in Table 4.1. Table 4.1 Coding of cable type designation Onderdeel Code
Niet-metalen omhulsel | Non-metallic sheath | of several codes, which are placed in a fixed order. The structure of the designation is shown in Table 4.1. Table 4.1 Coding of cable type designation Onderdeel Code Betekenis
E | E | codes, which are placed in a fixed order. The structure of the designation is shown in Table 4.1. Table 4.1 Coding of cable type designation Onderdeel Code Betekenis Non-metallic sheath
V | V | which are placed in a fixed order. The structure of the designation is shown in Table 4.1. Table 4.1 Coding of cable type designation Onderdeel Code Betekenis Non-metallic sheath E
PE-mantel | PE sheath | are placed in a fixed order. The structure of the designation is shown in Table 4.1. Table 4.1 Coding of cable type designation Onderdeel Code Betekenis Non-metallic sheath E V
PVC-mantel | PVC sheath | in a fixed order. The structure of the designation is shown in Table 4.1. Table 4.1 Coding of cable type designation Onderdeel Code Betekenis Non-metallic sheath E V PE sheath
Mechanische bescherming | Mechanical protection | fixed order. The structure of the designation is shown in Table 4.1. Table 4.1 Coding of cable type designation Onderdeel Code Betekenis Non-metallic sheath E V PE sheath PVC sheath
G | G | The structure of the designation is shown in Table 4.1. Table 4.1 Coding of cable type designation Onderdeel Code Betekenis Non-metallic sheath E V PE sheath PVC sheath Mechanical protection
O | O | structure of the designation is shown in Table 4.1. Table 4.1 Coding of cable type designation Onderdeel Code Betekenis Non-metallic sheath E V PE sheath PVC sheath Mechanical protection G
armering | armering | of the designation is shown in Table 4.1. Table 4.1 Coding of cable type designation Onderdeel Code Betekenis Non-metallic sheath E V PE sheath PVC sheath Mechanical protection G O
omvlochten | omvlochten | the designation is shown in Table 4.1. Table 4.1 Coding of cable type designation Onderdeel Code Betekenis Non-metallic sheath E V PE sheath PVC sheath Mechanical protection G O armering
Isolatiemateriaal | Isolatiemateriaal | designation is shown in Table 4.1. Table 4.1 Coding of cable type designation Onderdeel Code Betekenis Non-metallic sheath E V PE sheath PVC sheath Mechanical protection G O armering omvlochten
E | E | is shown in Table 4.1. Table 4.1 Coding of cable type designation Onderdeel Code Betekenis Non-metallic sheath E V PE sheath PVC sheath Mechanical protection G O armering omvlochten Isolatiemateriaal
P | P | shown in Table 4.1. Table 4.1 Coding of cable type designation Onderdeel Code Betekenis Non-metallic sheath E V PE sheath PVC sheath Mechanical protection G O armering omvlochten Isolatiemateriaal E
V | V | in Table 4.1. Table 4.1 Coding of cable type designation Onderdeel Code Betekenis Non-metallic sheath E V PE sheath PVC sheath Mechanical protection G O armering omvlochten Isolatiemateriaal E P
Y | Y | Table 4.1. Table 4.1 Coding of cable type designation Onderdeel Code Betekenis Non-metallic sheath E V PE sheath PVC sheath Mechanical protection G O armering omvlochten Isolatiemateriaal E P V
PE-isolatie | PE insulation | 4.1. Table 4.1 Coding of cable type designation Onderdeel Code Betekenis Non-metallic sheath E V PE sheath PVC sheath Mechanical protection G O armering omvlochten Isolatiemateriaal E P V Y
papier-isolatie | paper insulation | 4.1 Coding of cable type designation Onderdeel Code Betekenis Non-metallic sheath E V PE sheath PVC sheath Mechanical protection G O armering omvlochten Isolatiemateriaal E P V Y PE insulation
PVC-isolatie | PVC insulation | of cable type designation Onderdeel Code Betekenis Non-metallic sheath E V PE sheath PVC sheath Mechanical protection G O armering omvlochten Isolatiemateriaal E P V Y PE insulation paper insulation
XLPE-isolatie (vernet polyetheen) | XLPE insulation (cross-linked polyethylene) | type designation Onderdeel Code Betekenis Non-metallic sheath E V PE sheath PVC sheath Mechanical protection G O armering omvlochten Isolatiemateriaal E P V Y PE insulation paper insulation PVC insulation
Mantel | Mantel | Betekenis Non-metallic sheath E V PE sheath PVC sheath Mechanical protection G O armering omvlochten Isolatiemateriaal E P V Y PE insulation paper insulation PVC insulation XLPE insulation (cross-linked polyethylene)
LK | LK | Non-metallic sheath E V PE sheath PVC sheath Mechanical protection G O armering omvlochten Isolatiemateriaal E P V Y PE insulation paper insulation PVC insulation XLPE insulation (cross-linked polyethylene) Mantel
MvK | MvK | sheath E V PE sheath PVC sheath Mechanical protection G O armering omvlochten Isolatiemateriaal E P V Y PE insulation paper insulation PVC insulation XLPE insulation (cross-linked polyethylene) Mantel LK
MeK | MeK | E V PE sheath PVC sheath Mechanical protection G O armering omvlochten Isolatiemateriaal E P V Y PE insulation paper insulation PVC insulation XLPE insulation (cross-linked polyethylene) Mantel LK MvK
loodmantel | loodmantel | V PE sheath PVC sheath Mechanical protection G O armering omvlochten Isolatiemateriaal E P V Y PE insulation paper insulation PVC insulation XLPE insulation (cross-linked polyethylene) Mantel LK MvK MeK
PVC-mantel | PVC sheath | PE sheath PVC sheath Mechanical protection G O armering omvlochten Isolatiemateriaal E P V Y PE insulation paper insulation PVC insulation XLPE insulation (cross-linked polyethylene) Mantel LK MvK MeK loodmantel
PE-mantel | PE sheath | PVC sheath Mechanical protection G O armering omvlochten Isolatiemateriaal E P V Y PE insulation paper insulation PVC insulation XLPE insulation (cross-linked polyethylene) Mantel LK MvK MeK loodmantel PVC sheath
Bijzonderheden | Bijzonderheden | Mechanical protection G O armering omvlochten Isolatiemateriaal E P V Y PE insulation paper insulation PVC insulation XLPE insulation (cross-linked polyethylene) Mantel LK MvK MeK loodmantel PVC sheath PE sheath
rv | rv | protection G O armering omvlochten Isolatiemateriaal E P V Y PE insulation paper insulation PVC insulation XLPE insulation (cross-linked polyethylene) Mantel LK MvK MeK loodmantel PVC sheath PE sheath Bijzonderheden
h | h | G O armering omvlochten Isolatiemateriaal E P V Y PE insulation paper insulation PVC insulation XLPE insulation (cross-linked polyethylene) Mantel LK MvK MeK loodmantel PVC sheath PE sheath Bijzonderheden rv
as | as | O armering omvlochten Isolatiemateriaal E P V Y PE insulation paper insulation PVC insulation XLPE insulation (cross-linked polyethylene) Mantel LK MvK MeK loodmantel PVC sheath PE sheath Bijzonderheden rv h
sas | sas | armering omvlochten Isolatiemateriaal E P V Y PE insulation paper insulation PVC insulation XLPE insulation (cross-linked polyethylene) Mantel LK MvK MeK loodmantel PVC sheath PE sheath Bijzonderheden rv h as
lwd | lwd | omvlochten Isolatiemateriaal E P V Y PE insulation paper insulation PVC insulation XLPE insulation (cross-linked polyethylene) Mantel LK MvK MeK loodmantel PVC sheath PE sheath Bijzonderheden rv h as sas
dlwd | dlwd | Isolatiemateriaal E P V Y PE insulation paper insulation PVC insulation XLPE insulation (cross-linked polyethylene) Mantel LK MvK MeK loodmantel PVC sheath PE sheath Bijzonderheden rv h as sas lwd
lqwd | lqwd | E P V Y PE insulation paper insulation PVC insulation XLPE insulation (cross-linked polyethylene) Mantel LK MvK MeK loodmantel PVC sheath PE sheath Bijzonderheden rv h as sas lwd dlwd
mb | mb | P V Y PE insulation paper insulation PVC insulation XLPE insulation (cross-linked polyethylene) Mantel LK MvK MeK loodmantel PVC sheath PE sheath Bijzonderheden rv h as sas lwd dlwd lqwd
zh | zh | V Y PE insulation paper insulation PVC insulation XLPE insulation (cross-linked polyethylene) Mantel LK MvK MeK loodmantel PVC sheath PE sheath Bijzonderheden rv h as sas lwd dlwd lqwd mb
radiaal veld | radial field | Y PE insulation paper insulation PVC insulation XLPE insulation (cross-linked polyethylene) Mantel LK MvK MeK loodmantel PVC sheath PE sheath Bijzonderheden rv h as sas lwd dlwd lqwd mb zh
hulpaders | hulpaders | insulation paper insulation PVC insulation XLPE insulation (cross-linked polyethylene) Mantel LK MvK MeK loodmantel PVC sheath PE sheath Bijzonderheden rv h as sas lwd dlwd lqwd mb zh radial field
aardscherm | aardscherm | paper insulation PVC insulation XLPE insulation (cross-linked polyethylene) Mantel LK MvK MeK loodmantel PVC sheath PE sheath Bijzonderheden rv h as sas lwd dlwd lqwd mb zh radial field hulpaders
S-vormig aardscherm | S-shaped earth shield | insulation PVC insulation XLPE insulation (cross-linked polyethylene) Mantel LK MvK MeK loodmantel PVC sheath PE sheath Bijzonderheden rv h as sas lwd dlwd lqwd mb zh radial field hulpaders aardscherm
langswaterdicht | langswaterdicht | XLPE insulation (cross-linked polyethylene) Mantel LK MvK MeK loodmantel PVC sheath PE sheath Bijzonderheden rv h as sas lwd dlwd lqwd mb zh radial field hulpaders aardscherm S-shaped earth shield
dwars- en langswaterdicht | transverse and longitudinally watertight | insulation (cross-linked polyethylene) Mantel LK MvK MeK loodmantel PVC sheath PE sheath Bijzonderheden rv h as sas lwd dlwd lqwd mb zh radial field hulpaders aardscherm S-shaped earth shield langswaterdicht
langs- en quasi-dwarswaterdicht | longitudinally and quasi-transversely watertight | LK MvK MeK loodmantel PVC sheath PE sheath Bijzonderheden rv h as sas lwd dlwd lqwd mb zh radial field hulpaders aardscherm S-shaped earth shield langswaterdicht transverse and longitudinally watertight
moeilijk brandbare mantel | flame-retardant sheath | PVC sheath PE sheath Bijzonderheden rv h as sas lwd dlwd lqwd mb zh radial field hulpaders aardscherm S-shaped earth shield langswaterdicht transverse and longitudinally watertight longitudinally and quasi-transversely watertight
zonder halogeen | halogen-free | PE sheath Bijzonderheden rv h as sas lwd dlwd lqwd mb zh radial field hulpaders aardscherm S-shaped earth shield langswaterdicht transverse and longitudinally watertight longitudinally and quasi-transversely watertight flame-retardant sheath
Toegekende spanning | Rated voltage | sheath Bijzonderheden rv h as sas lwd dlwd lqwd mb zh radial field hulpaders aardscherm S-shaped earth shield langswaterdicht transverse and longitudinally watertight longitudinally and quasi-transversely watertight flame-retardant sheath halogen-free
… | … | rv h as sas lwd dlwd lqwd mb zh radial field hulpaders aardscherm S-shaped earth shield langswaterdicht transverse and longitudinally watertight longitudinally and quasi-transversely watertight flame-retardant sheath halogen-free Rated voltage
fasespanning en/of gekoppelde spanning (kV) | phase voltage and/or coupled voltage (kV) | h as sas lwd dlwd lqwd mb zh radial field hulpaders aardscherm S-shaped earth shield langswaterdicht transverse and longitudinally watertight longitudinally and quasi-transversely watertight flame-retardant sheath halogen-free Rated voltage …
Aantal aders, geleider-doorsnede, aardscherm | Number of cores, conductor cross-section, earth shield | mb zh radial field hulpaders aardscherm S-shaped earth shield langswaterdicht transverse and longitudinally watertight longitudinally and quasi-transversely watertight flame-retardant sheath halogen-free Rated voltage … phase voltage and/or coupled voltage (kV)
… | … | earth shield langswaterdicht transverse and longitudinally watertight longitudinally and quasi-transversely watertight flame-retardant sheath halogen-free Rated voltage … phase voltage and/or coupled voltage (kV) Number of cores, conductor cross-section, earth shield
doorsneden in mm | cross-sections in mm | shield langswaterdicht transverse and longitudinally watertight longitudinally and quasi-transversely watertight flame-retardant sheath halogen-free Rated voltage … phase voltage and/or coupled voltage (kV) Number of cores, conductor cross-section, earth shield …
2 | 2 | and longitudinally watertight longitudinally and quasi-transversely watertight flame-retardant sheath halogen-free Rated voltage … phase voltage and/or coupled voltage (kV) Number of cores, conductor cross-section, earth shield … cross-sections in mm
Bijzonderheden | Bijzonderheden | longitudinally watertight longitudinally and quasi-transversely watertight flame-retardant sheath halogen-free Rated voltage … phase voltage and/or coupled voltage (kV) Number of cores, conductor cross-section, earth shield … cross-sections in mm 2
van de geleider | of the conductor | watertight longitudinally and quasi-transversely watertight flame-retardant sheath halogen-free Rated voltage … phase voltage and/or coupled voltage (kV) Number of cores, conductor cross-section, earth shield … cross-sections in mm 2 Bijzonderheden
Al | Al | quasi-transversely watertight flame-retardant sheath halogen-free Rated voltage … phase voltage and/or coupled voltage (kV) Number of cores, conductor cross-section, earth shield … cross-sections in mm 2 Bijzonderheden of the conductor
Cu | Cu | watertight flame-retardant sheath halogen-free Rated voltage … phase voltage and/or coupled voltage (kV) Number of cores, conductor cross-section, earth shield … cross-sections in mm 2 Bijzonderheden of the conductor Al
rm | rm | flame-retardant sheath halogen-free Rated voltage … phase voltage and/or coupled voltage (kV) Number of cores, conductor cross-section, earth shield … cross-sections in mm 2 Bijzonderheden of the conductor Al Cu
rs | rs | sheath halogen-free Rated voltage … phase voltage and/or coupled voltage (kV) Number of cores, conductor cross-section, earth shield … cross-sections in mm 2 Bijzonderheden of the conductor Al Cu rm
svs | svs | halogen-free Rated voltage … phase voltage and/or coupled voltage (kV) Number of cores, conductor cross-section, earth shield … cross-sections in mm 2 Bijzonderheden of the conductor Al Cu rm rs
aluminium | aluminium | Rated voltage … phase voltage and/or coupled voltage (kV) Number of cores, conductor cross-section, earth shield … cross-sections in mm 2 Bijzonderheden of the conductor Al Cu rm rs svs
koper | koper | voltage … phase voltage and/or coupled voltage (kV) Number of cores, conductor cross-section, earth shield … cross-sections in mm 2 Bijzonderheden of the conductor Al Cu rm rs svs aluminium
ronde massieve geleiders | round solid conductors | … phase voltage and/or coupled voltage (kV) Number of cores, conductor cross-section, earth shield … cross-sections in mm 2 Bijzonderheden of the conductor Al Cu rm rs svs aluminium koper
ronde geslagen geleiders | round stranded conductors | and/or coupled voltage (kV) Number of cores, conductor cross-section, earth shield … cross-sections in mm 2 Bijzonderheden of the conductor Al Cu rm rs svs aluminium koper round solid conductors
sectorvormige geslagen geleiders | sector-shaped stranded conductors | (kV) Number of cores, conductor cross-section, earth shield … cross-sections in mm 2 Bijzonderheden of the conductor Al Cu rm rs svs aluminium koper round solid conductors round stranded conductors
Voor geleiderdoorsneden tot 300 mm | For conductor cross-sections up to 300 mm | cores, conductor cross-section, earth shield … cross-sections in mm 2 Bijzonderheden of the conductor Al Cu rm rs svs aluminium koper round solid conductors round stranded conductors sector-shaped stranded conductors
2 | 2 | in mm 2 Bijzonderheden of the conductor Al Cu rm rs svs aluminium koper round solid conductors round stranded conductors sector-shaped stranded conductors For conductor cross-sections up to 300 mm
worden in het algemeen drieaderige kabels toegepast. Voor de grotere geleiderdoorsneden worden meestal drie enkeladerige kabels per circuit toegepast. Met name worden enkeladerige kabels toegepast in MS-transportnetten en om zware industriële belastingen en grote decentrale opwekeenheden aan te sluiten. Gebruikelijke geleiderdoorsneden zijn: | generally, three-core cables are used. For larger conductor cross-sections, three single-core cables per circuit are usually applied. Specifically, single-core cables are used in medium voltage (MV) transmission networks and for connecting heavy industrial loads and large decentralized generation units. Common conductor cross-sections are: | mm 2 Bijzonderheden of the conductor Al Cu rm rs svs aluminium koper round solid conductors round stranded conductors sector-shaped stranded conductors For conductor cross-sections up to 300 mm 2
MS-distributie: 16 tot 240 mm | MV distribution: 16 to 240 mm | circuit are usually applied. Specifically, single-core cables are used in medium voltage (MV) transmission networks and for connecting heavy industrial loads and large decentralized generation units. Common conductor cross-sections are:
2 | 2 | cables are used in medium voltage (MV) transmission networks and for connecting heavy industrial loads and large decentralized generation units. Common conductor cross-sections are: MV distribution: 16 to 240 mm
MS-transport: 240 tot 630 mm | MV transport: 240 to 630 mm | are used in medium voltage (MV) transmission networks and for connecting heavy industrial loads and large decentralized generation units. Common conductor cross-sections are: MV distribution: 16 to 240 mm 2
2 | 2 | transmission networks and for connecting heavy industrial loads and large decentralized generation units. Common conductor cross-sections are: MV distribution: 16 to 240 mm 2 MV transport: 240 to 630 mm
Tabel 4.2 Voorbeelden van driefasige kunststofkabels | Table 4.2 Examples of Three-Phase Plastic Cables | networks and for connecting heavy industrial loads and large decentralized generation units. Common conductor cross-sections are: MV distribution: 16 to 240 mm 2 MV transport: 240 to 630 mm 2
Distributiekabel 3 aderig | Three-core distribution cable | and large decentralized generation units. Common conductor cross-sections are: MV distribution: 16 to 240 mm 2 MV transport: 240 to 630 mm 2 Table 4.2 Examples of Three-Phase Plastic Cables
Transportkabel 1 aderig | Transport cable single-core | generation units. Common conductor cross-sections are: MV distribution: 16 to 240 mm 2 MV transport: 240 to 630 mm 2 Table 4.2 Examples of Three-Phase Plastic Cables Three-core distribution cable
10 kV: | 10 kV: | conductor cross-sections are: MV distribution: 16 to 240 mm 2 MV transport: 240 to 630 mm 2 Table 4.2 Examples of Three-Phase Plastic Cables Three-core distribution cable Transport cable single-core
YMeKrvaslqwd 6/10kV 3x240 Alrm as70 | YMeKrvaslqwd 6/10kV 3x240 Alrm as70 | are: MV distribution: 16 to 240 mm 2 MV transport: 240 to 630 mm 2 Table 4.2 Examples of Three-Phase Plastic Cables Three-core distribution cable Transport cable single-core 10 kV:
YMeKrvaslqwd 6/10kV 3x150 Alrm as70 | YMeKrvaslqwd 6/10kV 3x150 Alrm as70 | 240 mm 2 MV transport: 240 to 630 mm 2 Table 4.2 Examples of Three-Phase Plastic Cables Three-core distribution cable Transport cable single-core 10 kV: YMeKrvaslqwd 6/10kV 3x240 Alrm as70
YMeKrvaslqwd 6/10kV 3x95 Alrm as70 | YMeKrvaslqwd 6/10kV 3x95 Alrm as70 | 240 to 630 mm 2 Table 4.2 Examples of Three-Phase Plastic Cables Three-core distribution cable Transport cable single-core 10 kV: YMeKrvaslqwd 6/10kV 3x240 Alrm as70 YMeKrvaslqwd 6/10kV 3x150 Alrm as70
20 kV: | 20 kV: | Table 4.2 Examples of Three-Phase Plastic Cables Three-core distribution cable Transport cable single-core 10 kV: YMeKrvaslqwd 6/10kV 3x240 Alrm as70 YMeKrvaslqwd 6/10kV 3x150 Alrm as70 YMeKrvaslqwd 6/10kV 3x95 Alrm as70
YMeKrvaslqwd 12/20kV 3x240 Alrm as70 | YMeKrvaslqwd 12/20kV 3x240 Alrm as70 | Examples of Three-Phase Plastic Cables Three-core distribution cable Transport cable single-core 10 kV: YMeKrvaslqwd 6/10kV 3x240 Alrm as70 YMeKrvaslqwd 6/10kV 3x150 Alrm as70 YMeKrvaslqwd 6/10kV 3x95 Alrm as70 20 kV:
10 kV: | 10 kV: | Three-core distribution cable Transport cable single-core 10 kV: YMeKrvaslqwd 6/10kV 3x240 Alrm as70 YMeKrvaslqwd 6/10kV 3x150 Alrm as70 YMeKrvaslqwd 6/10kV 3x95 Alrm as70 20 kV: YMeKrvaslqwd 12/20kV 3x240 Alrm as70
YMeKrvaslqwd 6/10kV 1x630 Alrm as70 | YMeKrvaslqwd 6/10kV 1x630 Alrm as70 | cable Transport cable single-core 10 kV: YMeKrvaslqwd 6/10kV 3x240 Alrm as70 YMeKrvaslqwd 6/10kV 3x150 Alrm as70 YMeKrvaslqwd 6/10kV 3x95 Alrm as70 20 kV: YMeKrvaslqwd 12/20kV 3x240 Alrm as70 10 kV:
YMeKrvaslqwd 6/10kV 1x400 Alrm as70 | YMeKrvaslqwd 6/10kV 1x400 Alrm as70 | kV: YMeKrvaslqwd 6/10kV 3x240 Alrm as70 YMeKrvaslqwd 6/10kV 3x150 Alrm as70 YMeKrvaslqwd 6/10kV 3x95 Alrm as70 20 kV: YMeKrvaslqwd 12/20kV 3x240 Alrm as70 10 kV: YMeKrvaslqwd 6/10kV 1x630 Alrm as70
20 kV: | 20 kV: | as70 YMeKrvaslqwd 6/10kV 3x150 Alrm as70 YMeKrvaslqwd 6/10kV 3x95 Alrm as70 20 kV: YMeKrvaslqwd 12/20kV 3x240 Alrm as70 10 kV: YMeKrvaslqwd 6/10kV 1x630 Alrm as70 YMeKrvaslqwd 6/10kV 1x400 Alrm as70
YMeKrvaslqwd 12/20kV 1x630 Alrm as70 | YMeKrvaslqwd 12/20kV 1x630 Alrm as70 | 6/10kV 3x150 Alrm as70 YMeKrvaslqwd 6/10kV 3x95 Alrm as70 20 kV: YMeKrvaslqwd 12/20kV 3x240 Alrm as70 10 kV: YMeKrvaslqwd 6/10kV 1x630 Alrm as70 YMeKrvaslqwd 6/10kV 1x400 Alrm as70 20 kV:
YMeKrvaslqwd 12/20kV 1x400 Alrm as70 | YMeKrvaslqwd 12/20kV 1x400 Alrm as70 | 6/10kV 3x95 Alrm as70 20 kV: YMeKrvaslqwd 12/20kV 3x240 Alrm as70 10 kV: YMeKrvaslqwd 6/10kV 1x630 Alrm as70 YMeKrvaslqwd 6/10kV 1x400 Alrm as70 20 kV: YMeKrvaslqwd 12/20kV 1x630 Alrm as70
Enkele veelgebruikte typen kunststofkabels zijn in tabel 4.2 genoemd. Deze kabels hebben ronde massieve aluminium geleiders en XLPE-isolatie voor een gekoppelde spanning van 10 kV (6 kV fasespanning) of voor 20 kV (12 kV fasespanning). De kabels zijn langs- en quasi-waterdicht, hebben een radiaal elektrisch veld in de isolatie en hebben een aardscherm met een doorsnede van 70 mm | Some commonly used types of plastic cables are listed in table 4.2. These cables have round solid aluminum conductors and XLPE insulation for a rated voltage of 10 kV (6 kV phase voltage) or 20 kV (12 kV phase voltage). The cables are longitudinally and quasi-waterproof, have a radial electric field in the insulation, and have a grounding screen with a cross-section of 70 mm². | kV: YMeKrvaslqwd 12/20kV 3x240 Alrm as70 10 kV: YMeKrvaslqwd 6/10kV 1x630 Alrm as70 YMeKrvaslqwd 6/10kV 1x400 Alrm as70 20 kV: YMeKrvaslqwd 12/20kV 1x630 Alrm as70 YMeKrvaslqwd 12/20kV 1x400 Alrm as70
2 | 2 | kV (12 kV phase voltage). The cables are longitudinally and quasi-waterproof, have a radial electric field in the insulation, and have a grounding screen with a cross-section of 70 mm².
. De kabel is omgeven met een PE-mantel. De distributiekabels met geleideredoorsnedes tot 240 mm | The cable is surrounded by a PE sheath. The distribution cables with conductor cross-sections up to 240 mm² | (12 kV phase voltage). The cables are longitudinally and quasi-waterproof, have a radial electric field in the insulation, and have a grounding screen with a cross-section of 70 mm². 2
2 | 2 | and have a grounding screen with a cross-section of 70 mm². 2 The cable is surrounded by a PE sheath. The distribution cables with conductor cross-sections up to 240 mm²
in deze tabel zijn drieaderig en de transportkabels met geleiderdoorsnedes vanaf 400 mm | in this table are three-core and transport cables with conductor cross-sections starting from 400 mm² | have a grounding screen with a cross-section of 70 mm². 2 The cable is surrounded by a PE sheath. The distribution cables with conductor cross-sections up to 240 mm² 2
2 | 2 | by a PE sheath. The distribution cables with conductor cross-sections up to 240 mm² 2 in this table are three-core and transport cables with conductor cross-sections starting from 400 mm²
enkeladerig. | single-core. | a PE sheath. The distribution cables with conductor cross-sections up to 240 mm² 2 in this table are three-core and transport cables with conductor cross-sections starting from 400 mm² 2
4.1.2 Constructie LS-kabels | 4.1.2 Construction of Low-Voltage Cables | PE sheath. The distribution cables with conductor cross-sections up to 240 mm² 2 in this table are three-core and transport cables with conductor cross-sections starting from 400 mm² 2 single-core.
De meeste LS-kabels zijn uitgevoerd met 4 aders: drie voor de fasen en één voor de nul. Ongeveer 40% van alle LS-kabels in Nederland zijn van het GPLK-type met koperen geleiders. De overige 60% bestaat uit kunststof kabels met koperen of aluminium geleiders en kunststof isolatie. De meest gebruikte kunststofkabels zijn van het type Aluminium Kunststof Distributie- en Aansluitkabel (ALKUDIA). | Most low-voltage cables are equipped with 4 conductors: three for the phases and one for the neutral. Approximately 40% of all low-voltage cables in the Netherlands are of the GPLK type with copper conductors. The remaining 60% consists of plastic cables with copper or aluminum conductors and plastic insulation. The most commonly used plastic cables are of the Aluminum Plastic Distribution and Connection Cable (ALKUDIA) type. | with conductor cross-sections up to 240 mm² 2 in this table are three-core and transport cables with conductor cross-sections starting from 400 mm² 2 single-core. 4.1.2 Construction of Low-Voltage Cables
De isolatie van de aders van kunststof LS-kabels bestaat uit vaste PVC of XLPE. Vanwege de lage veldsterkte is geen halfgeleidende laag nodig voor de veldsturing. Kunststof kabels hebben een koperdraadscherm voor het voeren van vereffeningstromen en voor het voeren van kortstondige kortsluitstromen. Kabels met PVC-isolatie mogen tot een geleidertemperatuur van 65 °C belast worden. Kabels met XLPE-isolatie mogen tot een geleidertemperatuur van 90 °C belast worden. | The insulation of the cores of plastic low-voltage (LV) cables consists of solid PVC or XLPE. Due to the low field strength, no semiconducting layer is needed for field control. Plastic cables have a copper wire screen for carrying equalization currents and for carrying short-term short-circuit currents. Cables with PVC insulation can be loaded up to a conductor temperature of 65°C. Cables with XLPE insulation can be loaded up to a conductor temperature of 90°C. | 60% consists of plastic cables with copper or aluminum conductors and plastic insulation. The most commonly used plastic cables are of the Aluminum Plastic Distribution and Connection Cable (ALKUDIA) type.
In veel gevallen hebben de kabels een scherm van koperdraden die meanderend over de samengeslagen aders zijn aangebracht: een zogenaamd S-vormig aardscherm (zie figuur 4.3). Het voordeel van het meanderen is dat de aftak- en aansluitmoffen kunnen worden aangebracht zonder het scherm te onderbreken. | In many cases, the cables have a shield of copper wires that are applied in a meandering pattern over the twisted conductors: a so-called S-shaped ground shield (see figure 4.3). The advantage of the meandering is that branch and connection joints can be installed without interrupting the shield. | short-circuit currents. Cables with PVC insulation can be loaded up to a conductor temperature of 65°C. Cables with XLPE insulation can be loaded up to a conductor temperature of 90°C.
Figuur 4.3 Voorbeeld van een vieraderige kunststof LS-kabel | Figure 4.3 Example of a four-core plastic low-voltage cable | over the twisted conductors: a so-called S-shaped ground shield (see figure 4.3). The advantage of the meandering is that branch and connection joints can be installed without interrupting the shield.
Gebruikelijke geleiderdoorsneden zijn: | Common conductor cross-sections are: | (see figure 4.3). The advantage of the meandering is that branch and connection joints can be installed without interrupting the shield. Figure 4.3 Example of a four-core plastic low-voltage cable
huisaansluitkabel: 6 tot 16 mm | house connection cable: 6 to 16 mm | advantage of the meandering is that branch and connection joints can be installed without interrupting the shield. Figure 4.3 Example of a four-core plastic low-voltage cable Common conductor cross-sections are:
2 | 2 | and connection joints can be installed without interrupting the shield. Figure 4.3 Example of a four-core plastic low-voltage cable Common conductor cross-sections are: house connection cable: 6 to 16 mm
LS-hoofdkabel: 16 tot 240 mm | LS main cable: 16 to 240 mm² | connection joints can be installed without interrupting the shield. Figure 4.3 Example of a four-core plastic low-voltage cable Common conductor cross-sections are: house connection cable: 6 to 16 mm 2
2 | 2 | the shield. Figure 4.3 Example of a four-core plastic low-voltage cable Common conductor cross-sections are: house connection cable: 6 to 16 mm 2 LS main cable: 16 to 240 mm²
Laagspanningskabels zijn verkrijgbaar met hulpaders en worden dan ook wel combikabels genoemd. Hulpaders hebben geleiders van 2,5 of 6 mm | Low-voltage cables are available with auxiliary cores and are therefore also called combo cables. Auxiliary cores have conductors of 2.5 or 6 mm². | shield. Figure 4.3 Example of a four-core plastic low-voltage cable Common conductor cross-sections are: house connection cable: 6 to 16 mm 2 LS main cable: 16 to 240 mm² 2
2 | 2 | main cable: 16 to 240 mm² 2 Low-voltage cables are available with auxiliary cores and are therefore also called combo cables. Auxiliary cores have conductors of 2.5 or 6 mm².
doorsnede en zijn tussen de hoofdaders aangebracht. Figuur 4.3 geeft een voorbeeld van een laagspanningskabel met aluminium sectorvormige geleiders en met hulpaders. De hulpaders zijn zichtbaar als dunne koperen geleiders tussen de dikke aluminium hoofdaders. In praktijk voeden de hulpaders meestal de openbare verlichting. | cross-section and are placed between the main conductors. Figure 4.3 provides an example of a low-voltage cable with aluminum sector-shaped conductors and auxiliary cores. The auxiliary cores are visible as thin copper conductors between the thick aluminum main conductors. In practice, the auxiliary cores usually power public lighting. | cable: 16 to 240 mm² 2 Low-voltage cables are available with auxiliary cores and are therefore also called combo cables. Auxiliary cores have conductors of 2.5 or 6 mm². 2
De ader voor de nul is nodig voor het voeren van de retourstroom vanwege de asymmetrie in de driefasige belasting. De norm NEN 1010 voorziet in de mogelijkheid in laagspanningskabels een kleinere nulgeleider toe te passen, waarvan de doorsnede de helft bedraagt van de doorsnede van een fasegeleider. Deze zogenaamde halve nul wordt tegenwoordig niet meer toegepast maar komt sporadisch in oude LS-netten nog voor (bijvoorbeeld 3x35/25). Bij een éénfasige belasting is de stroom door de nul altijd net zo groot als de stroom door de fase. Daarom dienen aan de nulgeleider dezelfde eisen te worden gesteld als aan de fasegeleider. In een driefasen 50-Hz net dat symmetrisch wordt belast en waar geen hogere harmonische stromen vloeien, is de stroom door de nul ook echt nul. In situaties waarin de fasen asymmetrisch worden belast is de som van de fasestromen niet nul en loopt er een stroom door de nulgeleider. Bij de aanwezigheid van derde orde harmonische stromen in de fasen ontstaat eveneens een stroom door de nulgeleider, want de derde orde harmonische stromen compenseren elkaar niet. Dit wordt nader uitgelegd in hoofdstuk 11 over Power Quality. De derde orde harmonische stroom door de nulgeleider kan in sommige gevallen even groot worden als de stroom door de fasegeleiders. Een ader voor de nul met kleinere geleiderdoorsnede zal dan niet volstaan. | The neutral conductor is necessary for carrying the return current due to the asymmetry in the three-phase load. The NEN 1010 standard allows for the use of a smaller neutral conductor in low-voltage cables, with a cross-section that is half the size of a phase conductor. This so-called half neutral is no longer used today but can still be found sporadically in old low-voltage networks (for example, 3x35/25). In a single-phase load, the current through the neutral is always as large as the current through the phase. Therefore, the same requirements should be applied to the neutral conductor as to the phase conductor. In a three-phase 50-Hz network that is symmetrically loaded and where no higher harmonic currents flow, the current through the neutral is indeed zero. In situations where the phases are asymmetrically loaded, the sum of the phase currents is not zero, and a current flows through the neutral conductor. The presence of third-order harmonic currents in the phases also results in a current through the neutral conductor because the third-order harmonic currents do not cancel each other out. This is further explained in Chapter 11 on Power Quality. The third-order harmonic current through the neutral conductor can, in some cases, be as large as the current through the phase conductors. A neutral conductor with a smaller cross-section will then not suffice. | aluminum sector-shaped conductors and auxiliary cores. The auxiliary cores are visible as thin copper conductors between the thick aluminum main conductors. In practice, the auxiliary cores usually power public lighting.
4.1.3 Verbinden van de afschermingen van enkeladerige MS-kabels | 4.1.3 Connecting the shields of single-core medium voltage cables | current through the neutral conductor can, in some cases, be as large as the current through the phase conductors. A neutral conductor with a smaller cross-section will then not suffice.
De afschermingen van enkeladerige kabels kunnen op diverse manieren met elkaar worden verbonden. Zo kunnen aan één kant van het circuit de afschermingen worden verbonden, maar ook aan beide kanten. De stromen door de aders veroorzaken door inductie een spanning in elk van de afschermingen van de drie kabels. Indien deze afschermingen aan beide kabeleinden met elkaar zijn verbonden, kunnen door deze spanningen in de afschermingen vereffeningstromen gaan lopen. De grootte van de stromen is afhankelijk van de wijze waarop de afschermingen met elkaar zijn verbonden. Onderstaande configuraties zijn mogelijk: | The shields of single-core cables can be connected in various ways. For instance, the shields can be connected at one end of the circuit or at both ends. The currents through the conductors induce a voltage in each of the shields of the three cables. If these shields are connected at both cable ends, these voltages can cause equalizing currents to flow through the shields. The magnitude of these currents depends on how the shields are connected. The following configurations are possible: | be as large as the current through the phase conductors. A neutral conductor with a smaller cross-section will then not suffice. 4.1.3 Connecting the shields of single-core medium voltage cables
Eenzijdig | Eenzijdig | cable ends, these voltages can cause equalizing currents to flow through the shields. The magnitude of these currents depends on how the shields are connected. The following configurations are possible:
Tweezijdig | Tweezijdig | ends, these voltages can cause equalizing currents to flow through the shields. The magnitude of these currents depends on how the shields are connected. The following configurations are possible: Eenzijdig
Cross-bonding | Cross-bonding | these voltages can cause equalizing currents to flow through the shields. The magnitude of these currents depends on how the shields are connected. The following configurations are possible: Eenzijdig Tweezijdig
Figuur 4.4 Configuraties voor het verbinden van afschermingen van MS-kabels | Figure 4.4 Configurations for connecting shields of MV cables | voltages can cause equalizing currents to flow through the shields. The magnitude of these currents depends on how the shields are connected. The following configurations are possible: Eenzijdig Tweezijdig Cross-bonding
Eenzijdig: | Single-sided: | shields. The magnitude of these currents depends on how the shields are connected. The following configurations are possible: Eenzijdig Tweezijdig Cross-bonding Figure 4.4 Configurations for connecting shields of MV cables
Bij het verbinden van de afschermingen aan één zijde zullen geen vereffeningstromen lopen, omdat er geen gesloten circuit is tussen de afschermingen. Het nadeel is dat er aan de andere kant van de kabel grote potentiaalverschillen kunnen ontstaan tussen de afschermingen. | When connecting the shields on one side, no equalizing currents will flow because there is no closed circuit between the shields. The disadvantage is that large potential differences can arise between the shields on the other side of the cable. | The magnitude of these currents depends on how the shields are connected. The following configurations are possible: Eenzijdig Tweezijdig Cross-bonding Figure 4.4 Configurations for connecting shields of MV cables Single-sided:
Tweezijdig: | Two-sided: | will flow because there is no closed circuit between the shields. The disadvantage is that large potential differences can arise between the shields on the other side of the cable.
Een potentiaalverschil wordt vermeden door de afschermingen aan beide kanten met elkaar te verbinden. Er ontstaat dan een gesloten circuit tussen de afschermingen waardoor vereffeningstromen gaan vloeien. De hierbij optredende verliezen zijn (door de inductie) voor de drie kabels van een circuit niet gelijk. Indien de kabels in een plat vlak zijn gelegd, zullen de grootste verliezen optreden in één van de buitenste kabels. | A potential difference is avoided by connecting the shields on both sides. This creates a closed circuit between the shields, allowing equalizing currents to flow. The losses that occur in this process (due to induction) are not the same for the three cables of a circuit. If the cables are laid in a flat plane, the greatest losses will occur in one of the outer cables. | flow because there is no closed circuit between the shields. The disadvantage is that large potential differences can arise between the shields on the other side of the cable. Two-sided:
Kruislings (cross-bonding): | Cross-bonding: | not the same for the three cables of a circuit. If the cables are laid in a flat plane, the greatest losses will occur in one of the outer cables.
Om de vereffeningstromen bij tweezijdige verbinding op te heffen kan ervoor gekozen worden om het circuit in drie gelijke stukken op te delen. Na elk deel worden de afschermingen kruislinks met elkaar verbonden. Dit leidt ertoe dat de potentialen aan het begin en aan het eind van het circuit gelijk zijn en er dus geen vereffeningstromen vloeien. | To eliminate the equalization currents in a two-sided connection, the circuit can be divided into three equal sections. After each section, the shields are cross-bonded with each other. This ensures that the potentials at the beginning and end of the circuit are equal, and thus no equalization currents flow. | the same for the three cables of a circuit. If the cables are laid in a flat plane, the greatest losses will occur in one of the outer cables. Cross-bonding:
Kabels worden geleverd met een bepaalde (soms de maximale productie-)lengte. Een langere verbinding kan dus alleen met meerdere lengtes worden gemaakt. Als bij de bestelling, in overleg met de fabrikant, de juiste lengtes worden geleverd leidt ‘cross bonding’ tot minimale vereffeningstromen. | Cables are supplied in a certain (sometimes the maximum production) length. Therefore, a longer connection can only be made with multiple lengths. If the correct lengths are provided at the time of order, in consultation with the manufacturer, 'cross bonding' leads to minimal equalization currents. | each section, the shields are cross-bonded with each other. This ensures that the potentials at the beginning and end of the circuit are equal, and thus no equalization currents flow.
4.1.4 Impedanties van kabels | 4.1.4 Impedances of cables | can only be made with multiple lengths. If the correct lengths are provided at the time of order, in consultation with the manufacturer, 'cross bonding' leads to minimal equalization currents.
De impedantie van een kabel bestaat uit de weerstand en de reactantie. De weerstand wordt voornamelijk bepaald door de diameter en het materiaal van de geleider. De weerstand is bovendien afhankelijk van de geleidertemperatuur. De reactantie wordt berekend vanuit de zelfinductie, die afhangt van de geleiderdiameter, de diameter van de afscherming en de ligging van de aders van de drie fasen ten opzichte van elkaar. Hoofdstuk 8 over modellen behandelt de berekening van de weerstand en de reactantie. | The impedance of a cable consists of resistance and reactance. The resistance is primarily determined by the diameter and material of the conductor. Additionally, the resistance depends on the conductor temperature. The reactance is calculated from the self-inductance, which depends on the conductor diameter, the diameter of the shielding, and the positioning of the cores of the three phases relative to each other. Chapter 8 on models addresses the calculation of resistance and reactance. | with multiple lengths. If the correct lengths are provided at the time of order, in consultation with the manufacturer, 'cross bonding' leads to minimal equalization currents. 4.1.4 Impedances of cables
De R/X-verhouding (de verhouding van de weerstand tot de reactantie) heeft invloed op het gedrag van het net ten aanzien van de loadflow en bij kortsluitingen. Vanwege de compacte opbouw van de kabels is de zelfinductie laag, vergeleken met bovengrondse verbindingen. Hierdoor is de R/X-verhouding van kabels groter dan van bovengrondse verbindingen. Omdat MS-kabels een dikkere isolatie hebben dan LS-kabels, is de reactantie van MS-kabels groter dan van LS-kabels van dezelfde geleiderdoorsnede. Tabel 4.3 geeft een voorbeeld voor enkele drieaderige LS- en MS-kabels. | The R/X ratio (the ratio of resistance to reactance) affects the behavior of the network regarding load flow and during short circuits. Due to the compact construction of the cables, the self-inductance is low compared to overhead lines. As a result, the R/X ratio of cables is higher than that of overhead lines. Because medium voltage (MV) cables have thicker insulation than low voltage (LV) cables, the reactance of MV cables is greater than that of LV cables of the same conductor cross-section. Table 4.3 provides an example for some three-core LV and MV cables. | the diameter of the shielding, and the positioning of the cores of the three phases relative to each other. Chapter 8 on models addresses the calculation of resistance and reactance.
Tabel 4.3 Impedanties van LS- en MS-kabels | Table 4.3 Impedances of LV and MV Cables | cables, the reactance of MV cables is greater than that of LV cables of the same conductor cross-section. Table 4.3 provides an example for some three-core LV and MV cables.
Type | Type | than that of LV cables of the same conductor cross-section. Table 4.3 provides an example for some three-core LV and MV cables. Table 4.3 Impedances of LV and MV Cables
Spanning | Spanning | that of LV cables of the same conductor cross-section. Table 4.3 provides an example for some three-core LV and MV cables. Table 4.3 Impedances of LV and MV Cables Type
R (Ω/km) | R (Ω/km) | of LV cables of the same conductor cross-section. Table 4.3 provides an example for some three-core LV and MV cables. Table 4.3 Impedances of LV and MV Cables Type Spanning
X (Ω/km) | X (Ω/km) | cables of the same conductor cross-section. Table 4.3 provides an example for some three-core LV and MV cables. Table 4.3 Impedances of LV and MV Cables Type Spanning R (Ω/km)
R/X | R/X | the same conductor cross-section. Table 4.3 provides an example for some three-core LV and MV cables. Table 4.3 Impedances of LV and MV Cables Type Spanning R (Ω/km) X (Ω/km)
50 Al | 50 Al | same conductor cross-section. Table 4.3 provides an example for some three-core LV and MV cables. Table 4.3 Impedances of LV and MV Cables Type Spanning R (Ω/km) X (Ω/km) R/X
LS | LS | cross-section. Table 4.3 provides an example for some three-core LV and MV cables. Table 4.3 Impedances of LV and MV Cables Type Spanning R (Ω/km) X (Ω/km) R/X 50 Al
0,64 | 0.64 | Table 4.3 provides an example for some three-core LV and MV cables. Table 4.3 Impedances of LV and MV Cables Type Spanning R (Ω/km) X (Ω/km) R/X 50 Al LS
0,085 | 0.085 | 4.3 provides an example for some three-core LV and MV cables. Table 4.3 Impedances of LV and MV Cables Type Spanning R (Ω/km) X (Ω/km) R/X 50 Al LS 0.64
7,5 | 7.5 | provides an example for some three-core LV and MV cables. Table 4.3 Impedances of LV and MV Cables Type Spanning R (Ω/km) X (Ω/km) R/X 50 Al LS 0.64 0.085
150 Al | 150 Al | an example for some three-core LV and MV cables. Table 4.3 Impedances of LV and MV Cables Type Spanning R (Ω/km) X (Ω/km) R/X 50 Al LS 0.64 0.085 7.5
LS | LS | for some three-core LV and MV cables. Table 4.3 Impedances of LV and MV Cables Type Spanning R (Ω/km) X (Ω/km) R/X 50 Al LS 0.64 0.085 7.5 150 Al
0,21 | 0.21 | some three-core LV and MV cables. Table 4.3 Impedances of LV and MV Cables Type Spanning R (Ω/km) X (Ω/km) R/X 50 Al LS 0.64 0.085 7.5 150 Al LS
0,079 | 0.079 | three-core LV and MV cables. Table 4.3 Impedances of LV and MV Cables Type Spanning R (Ω/km) X (Ω/km) R/X 50 Al LS 0.64 0.085 7.5 150 Al LS 0.21
2,6 | 2.6 | LV and MV cables. Table 4.3 Impedances of LV and MV Cables Type Spanning R (Ω/km) X (Ω/km) R/X 50 Al LS 0.64 0.085 7.5 150 Al LS 0.21 0.079
50 Cu | 50 Cu | and MV cables. Table 4.3 Impedances of LV and MV Cables Type Spanning R (Ω/km) X (Ω/km) R/X 50 Al LS 0.64 0.085 7.5 150 Al LS 0.21 0.079 2.6
LS | LS | cables. Table 4.3 Impedances of LV and MV Cables Type Spanning R (Ω/km) X (Ω/km) R/X 50 Al LS 0.64 0.085 7.5 150 Al LS 0.21 0.079 2.6 50 Cu
0,39 | 0.39 | Table 4.3 Impedances of LV and MV Cables Type Spanning R (Ω/km) X (Ω/km) R/X 50 Al LS 0.64 0.085 7.5 150 Al LS 0.21 0.079 2.6 50 Cu LS
0,085 | 0.085 | 4.3 Impedances of LV and MV Cables Type Spanning R (Ω/km) X (Ω/km) R/X 50 Al LS 0.64 0.085 7.5 150 Al LS 0.21 0.079 2.6 50 Cu LS 0.39
4,6 | 4.6 | Impedances of LV and MV Cables Type Spanning R (Ω/km) X (Ω/km) R/X 50 Al LS 0.64 0.085 7.5 150 Al LS 0.21 0.079 2.6 50 Cu LS 0.39 0.085
150 Cu | 150 Cu | of LV and MV Cables Type Spanning R (Ω/km) X (Ω/km) R/X 50 Al LS 0.64 0.085 7.5 150 Al LS 0.21 0.079 2.6 50 Cu LS 0.39 0.085 4.6
LS | LS | and MV Cables Type Spanning R (Ω/km) X (Ω/km) R/X 50 Al LS 0.64 0.085 7.5 150 Al LS 0.21 0.079 2.6 50 Cu LS 0.39 0.085 4.6 150 Cu
0,13 | 0.13 | MV Cables Type Spanning R (Ω/km) X (Ω/km) R/X 50 Al LS 0.64 0.085 7.5 150 Al LS 0.21 0.079 2.6 50 Cu LS 0.39 0.085 4.6 150 Cu LS
0,063 | 0.063 | Cables Type Spanning R (Ω/km) X (Ω/km) R/X 50 Al LS 0.64 0.085 7.5 150 Al LS 0.21 0.079 2.6 50 Cu LS 0.39 0.085 4.6 150 Cu LS 0.13
2,0 | 2.0 | Type Spanning R (Ω/km) X (Ω/km) R/X 50 Al LS 0.64 0.085 7.5 150 Al LS 0.21 0.079 2.6 50 Cu LS 0.39 0.085 4.6 150 Cu LS 0.13 0.063
50 Al | 50 Al | Spanning R (Ω/km) X (Ω/km) R/X 50 Al LS 0.64 0.085 7.5 150 Al LS 0.21 0.079 2.6 50 Cu LS 0.39 0.085 4.6 150 Cu LS 0.13 0.063 2.0
MS | MS | (Ω/km) X (Ω/km) R/X 50 Al LS 0.64 0.085 7.5 150 Al LS 0.21 0.079 2.6 50 Cu LS 0.39 0.085 4.6 150 Cu LS 0.13 0.063 2.0 50 Al
0,64 | 0.64 | X (Ω/km) R/X 50 Al LS 0.64 0.085 7.5 150 Al LS 0.21 0.079 2.6 50 Cu LS 0.39 0.085 4.6 150 Cu LS 0.13 0.063 2.0 50 Al MS
0,105 | 0.105 | (Ω/km) R/X 50 Al LS 0.64 0.085 7.5 150 Al LS 0.21 0.079 2.6 50 Cu LS 0.39 0.085 4.6 150 Cu LS 0.13 0.063 2.0 50 Al MS 0.64
6,1 | 6.1 | R/X 50 Al LS 0.64 0.085 7.5 150 Al LS 0.21 0.079 2.6 50 Cu LS 0.39 0.085 4.6 150 Cu LS 0.13 0.063 2.0 50 Al MS 0.64 0.105
150 Al | 150 Al | 50 Al LS 0.64 0.085 7.5 150 Al LS 0.21 0.079 2.6 50 Cu LS 0.39 0.085 4.6 150 Cu LS 0.13 0.063 2.0 50 Al MS 0.64 0.105 6.1
MS | MS | LS 0.64 0.085 7.5 150 Al LS 0.21 0.079 2.6 50 Cu LS 0.39 0.085 4.6 150 Cu LS 0.13 0.063 2.0 50 Al MS 0.64 0.105 6.1 150 Al
0,21 | 0.21 | 0.64 0.085 7.5 150 Al LS 0.21 0.079 2.6 50 Cu LS 0.39 0.085 4.6 150 Cu LS 0.13 0.063 2.0 50 Al MS 0.64 0.105 6.1 150 Al MS
0,093 | 0.093 | 0.085 7.5 150 Al LS 0.21 0.079 2.6 50 Cu LS 0.39 0.085 4.6 150 Cu LS 0.13 0.063 2.0 50 Al MS 0.64 0.105 6.1 150 Al MS 0.21
2,2 | 2.2 | 7.5 150 Al LS 0.21 0.079 2.6 50 Cu LS 0.39 0.085 4.6 150 Cu LS 0.13 0.063 2.0 50 Al MS 0.64 0.105 6.1 150 Al MS 0.21 0.093
50 Cu | 50 Cu | 150 Al LS 0.21 0.079 2.6 50 Cu LS 0.39 0.085 4.6 150 Cu LS 0.13 0.063 2.0 50 Al MS 0.64 0.105 6.1 150 Al MS 0.21 0.093 2.2
MS | MS | LS 0.21 0.079 2.6 50 Cu LS 0.39 0.085 4.6 150 Cu LS 0.13 0.063 2.0 50 Al MS 0.64 0.105 6.1 150 Al MS 0.21 0.093 2.2 50 Cu
0,39 | 0.39 | 0.21 0.079 2.6 50 Cu LS 0.39 0.085 4.6 150 Cu LS 0.13 0.063 2.0 50 Al MS 0.64 0.105 6.1 150 Al MS 0.21 0.093 2.2 50 Cu MS
0,125 | 0.125 | 0.079 2.6 50 Cu LS 0.39 0.085 4.6 150 Cu LS 0.13 0.063 2.0 50 Al MS 0.64 0.105 6.1 150 Al MS 0.21 0.093 2.2 50 Cu MS 0.39
3,1 | 3.1 | 2.6 50 Cu LS 0.39 0.085 4.6 150 Cu LS 0.13 0.063 2.0 50 Al MS 0.64 0.105 6.1 150 Al MS 0.21 0.093 2.2 50 Cu MS 0.39 0.125
150 Cu | 150 Cu | 50 Cu LS 0.39 0.085 4.6 150 Cu LS 0.13 0.063 2.0 50 Al MS 0.64 0.105 6.1 150 Al MS 0.21 0.093 2.2 50 Cu MS 0.39 0.125 3.1
MS | MS | LS 0.39 0.085 4.6 150 Cu LS 0.13 0.063 2.0 50 Al MS 0.64 0.105 6.1 150 Al MS 0.21 0.093 2.2 50 Cu MS 0.39 0.125 3.1 150 Cu
0,13 | 0.13 | 0.39 0.085 4.6 150 Cu LS 0.13 0.063 2.0 50 Al MS 0.64 0.105 6.1 150 Al MS 0.21 0.093 2.2 50 Cu MS 0.39 0.125 3.1 150 Cu MS
0,105 | 0.105 | 0.085 4.6 150 Cu LS 0.13 0.063 2.0 50 Al MS 0.64 0.105 6.1 150 Al MS 0.21 0.093 2.2 50 Cu MS 0.39 0.125 3.1 150 Cu MS 0.13
1,2 | 1.2 | 4.6 150 Cu LS 0.13 0.063 2.0 50 Al MS 0.64 0.105 6.1 150 Al MS 0.21 0.093 2.2 50 Cu MS 0.39 0.125 3.1 150 Cu MS 0.13 0.105
4.1.5 Stroombelastbaarheid | 4.1.5 Current Carrying Capacity | 150 Cu LS 0.13 0.063 2.0 50 Al MS 0.64 0.105 6.1 150 Al MS 0.21 0.093 2.2 50 Cu MS 0.39 0.125 3.1 150 Cu MS 0.13 0.105 1.2
De maximale stroombelastbaarheid van een kabel wordt berekend met de internationaal erkende norm IEC 60287. De berekende waarde is de maximale stroom die continu door de kabel mag lopen zonder dat deze beschadigt. De norm beschrijft de berekening van de verliezen in de kabel en de thermische weerstanden van de kabel en de omgeving. De methode gaat uit van warmteproductie in de kabel en de mogelijkheid dat deze warmte wordt afgevoerd naar de omgeving. De methode is in principe gelijk voor LS- en MS-kabels. De norm NEN 1010 is van IEC 60287 afgeleid en beschrijft de stroombelastbaarheid specifiek voor LS-kabels. | The maximum current carrying capacity of a cable is calculated using the internationally recognized standard IEC 60287. The calculated value is the maximum current that can continuously flow through the cable without causing damage. The standard describes the calculation of losses in the cable and the thermal resistances of the cable and its surroundings. The method is based on heat production in the cable and the ability of this heat to be dissipated into the environment. The method is essentially the same for low voltage (LV) and medium voltage (MV) cables. The NEN 1010 standard is derived from IEC 60287 and specifically describes the current carrying capacity for LV cables. | 0.063 2.0 50 Al MS 0.64 0.105 6.1 150 Al MS 0.21 0.093 2.2 50 Cu MS 0.39 0.125 3.1 150 Cu MS 0.13 0.105 1.2 4.1.5 Current Carrying Capacity
Bij het projecteren van een kabelverbinding krijgt de elektrotechnicus te maken met een aantal randvoorwaarden en omgevingscondities. Van de grond waar de kabel in gelegd wordt, moet hij onder andere weten hoe hoog de bodemtemperatuur is, of er gevaar van uitdrogen van de bodem bestaat, hoe hoog het grondwaterpeil staat en hoe groot de thermische weerstand van de bodem om de in bedrijf zijnde kabel zal zijn. Onderstaande aandachtspunten zijn van invloed op de kabelbelastbaarheid: | When designing a cable connection, the electrical engineer must deal with several boundary conditions and environmental factors. For the soil where the cable will be laid, he needs to know, among other things, the soil temperature, whether there is a risk of soil drying out, the groundwater level, and the thermal resistance of the soil around the operational cable. The following points of attention affect the cable's current carrying capacity: | the same for low voltage (LV) and medium voltage (MV) cables. The NEN 1010 standard is derived from IEC 60287 and specifically describes the current carrying capacity for LV cables.
thermische weerstand van de grond | thermal resistance of the soil | risk of soil drying out, the groundwater level, and the thermal resistance of the soil around the operational cable. The following points of attention affect the cable's current carrying capacity:
neerslag | neerslag | the groundwater level, and the thermal resistance of the soil around the operational cable. The following points of attention affect the cable's current carrying capacity: thermal resistance of the soil
grondwaterstand | grondwaterstand | groundwater level, and the thermal resistance of the soil around the operational cable. The following points of attention affect the cable's current carrying capacity: thermal resistance of the soil neerslag
bodemmateriaal | bodemmateriaal | level, and the thermal resistance of the soil around the operational cable. The following points of attention affect the cable's current carrying capacity: thermal resistance of the soil neerslag grondwaterstand
materiaal van de kabelbedding | material of the cable bedding | and the thermal resistance of the soil around the operational cable. The following points of attention affect the cable's current carrying capacity: thermal resistance of the soil neerslag grondwaterstand bodemmateriaal
uitdroging | uitdroging | the soil around the operational cable. The following points of attention affect the cable's current carrying capacity: thermal resistance of the soil neerslag grondwaterstand bodemmateriaal material of the cable bedding
bodemtemperatuur | bodemtemperatuur | soil around the operational cable. The following points of attention affect the cable's current carrying capacity: thermal resistance of the soil neerslag grondwaterstand bodemmateriaal material of the cable bedding uitdroging
De thermische weerstand | The thermal resistance | around the operational cable. The following points of attention affect the cable's current carrying capacity: thermal resistance of the soil neerslag grondwaterstand bodemmateriaal material of the cable bedding uitdroging bodemtemperatuur
De thermische weerstand is een maat voor het vermogen van de omgeving om de geproduceerde warmte af te voeren. Hoe lager de thermische weerstand van de grond, des te beter voert de grond de in de kabel geproduceerde warmte af. Van alle parameters die nodig zijn om de maximaal toelaatbare continu stroom van een ondergrondse kabel te berekenen is de parameter ρ | The thermal resistance is a measure of the environment's ability to dissipate the generated heat. The lower the thermal resistance of the soil, the better the soil dissipates the heat produced in the cable. Of all the parameters needed to calculate the maximum allowable continuous current of an underground cable, the parameter ρ | cable. The following points of attention affect the cable's current carrying capacity: thermal resistance of the soil neerslag grondwaterstand bodemmateriaal material of the cable bedding uitdroging bodemtemperatuur The thermal resistance
T | T | the better the soil dissipates the heat produced in the cable. Of all the parameters needed to calculate the maximum allowable continuous current of an underground cable, the parameter ρ
, de thermische weerstand in K·m/W, van de bodem de moeilijkste om correct te bepalen. De ρ | , the thermal resistivity in K·m/W, of the soil is the most difficult to determine accurately. The ρ | better the soil dissipates the heat produced in the cable. Of all the parameters needed to calculate the maximum allowable continuous current of an underground cable, the parameter ρ T
T | T | maximum allowable continuous current of an underground cable, the parameter ρ T , the thermal resistivity in K·m/W, of the soil is the most difficult to determine accurately. The ρ
-waarde die toegepast moet worden, is de stabiele waarde die optreedt na een langdurige periode van bedrijf van de kabel(s), waarbij de maximaal toelaatbare continue stroom door de kabel loopt. Deze waarde kan echter niet vooraf gemeten worden. Wel kan de ρ | -value that must be applied is the stable value that occurs after a prolonged period of operation of the cable(s), during which the maximum allowable continuous current flows through the cable. However, this value cannot be measured in advance. The ρ | allowable continuous current of an underground cable, the parameter ρ T , the thermal resistivity in K·m/W, of the soil is the most difficult to determine accurately. The ρ T
T | T | after a prolonged period of operation of the cable(s), during which the maximum allowable continuous current flows through the cable. However, this value cannot be measured in advance. The ρ
-waarde van de ‘maagdelijke’ grond vóór installatie van de kabel(s) door specialisten gemeten worden. Daarnaast zijn het jaarlijks verloop van de vochtigheid, het grondwaterpeil en de temperatuur op de vereiste diepte belangrijk. De metingen moeten bijvoorkeur uitgevoerd worden na de zomer (op het noordelijk halfrond rond het midden van november), omdat dit de meest conservatieve waarde voor ρ | -value of the 'virgin' soil before the installation of the cable(s) should be measured by specialists. Additionally, the annual variation in moisture, groundwater level, and temperature at the required depth are important. Measurements should preferably be carried out after the summer (in the northern hemisphere around mid-November), as this provides the most conservative value for ρ. | a prolonged period of operation of the cable(s), during which the maximum allowable continuous current flows through the cable. However, this value cannot be measured in advance. The ρ T
T | T | at the required depth are important. Measurements should preferably be carried out after the summer (in the northern hemisphere around mid-November), as this provides the most conservative value for ρ.
zal opleveren. Als de ‘maagdelijke’ grond, waar de kabel in wordt gelegd, geen zand is, maar bijvoorbeeld bestaat uit klei of veen, dan zijn de temperatuur, de vochtigheid en het grondwaterpeil relevant. De kabels dienen bij voorkeur in verdicht zand liggen. De actuele ρ | will yield. If the 'virgin' soil where the cable is laid is not sand but, for example, consists of clay or peat, then temperature, humidity, and groundwater level are relevant. The cables should preferably be laid in compacted sand. The actual ρ | the required depth are important. Measurements should preferably be carried out after the summer (in the northern hemisphere around mid-November), as this provides the most conservative value for ρ. T
T | T | not sand but, for example, consists of clay or peat, then temperature, humidity, and groundwater level are relevant. The cables should preferably be laid in compacted sand. The actual ρ
-waarde van het verdichte zand kan echter drastisch afwijken van de eerder geschatte waarde omdat de hoeveelheid vocht in het zand door seizoensinvloeden of door andere externe factoren kan variëren. Zo kan de vochtigheid bijvoorbeeld veranderen indien neerslag niet meer kan binnendringen in de kabelsleuf of indien de grondwaterstand wijzigt. Ook vegetatie kan in open veld de vochtigheid van de bodem beïnvloeden. | -value of the compacted sand can, however, drastically differ from the previously estimated value because the amount of moisture in the sand can vary due to seasonal influences or other external factors. For instance, the moisture level can change if precipitation can no longer penetrate the cable trench or if the groundwater level changes. Vegetation in open fields can also affect the soil's moisture content. | sand but, for example, consists of clay or peat, then temperature, humidity, and groundwater level are relevant. The cables should preferably be laid in compacted sand. The actual ρ T
Neerslagverschillen | Neerslagverschillen | moisture level can change if precipitation can no longer penetrate the cable trench or if the groundwater level changes. Vegetation in open fields can also affect the soil's moisture content.
Ervan uitgaande dat de kabels liggen in een omgeving waarin de neerslag volledig kan penetreren in de kabelsleuf, heeft de IEC 60287-3-1 de volgende definities gegeven voor de relatie tussen vochtigheid en thermische weerstand. De waarden in tabel 4.4 mogen alleen gebruikt worden indien er verder geen gegevens over de lokale omstandigheden bekend zijn. | Assuming that the cables are located in an environment where precipitation can fully penetrate the cable trench, the IEC 60287-3-1 has provided the following definitions for the relationship between moisture and thermal resistance. The values in Table 4.4 should only be used if no further information about the local conditions is available. | level can change if precipitation can no longer penetrate the cable trench or if the groundwater level changes. Vegetation in open fields can also affect the soil's moisture content. Neerslagverschillen
De norm IEC 60287 definieert de vochtigheid uitsluitend door de hoeveelheid neerslag. Aangenomen wordt dat de neerslag ongehinderd door de toplaag kan wegzakken. Beïnvloeding van de vochtigheid door mogelijk aanwezig grondwater wordt terecht niet door de norm genoemd behalve dan in de gegevens voor Nederland: ‘sub-soil water level near to cables’. | The IEC 60287 standard defines moisture solely by the amount of precipitation. It is assumed that the precipitation can seep through the top layer without obstruction. The influence of moisture by potentially present groundwater is rightly not mentioned by the standard, except in the data for the Netherlands: 'sub-soil water level near to cables'. | the following definitions for the relationship between moisture and thermal resistance. The values in Table 4.4 should only be used if no further information about the local conditions is available.
Tabel 4.4 Relatie tussen thermische weerstand en vochtigheid | Table 4.4 Relationship between thermal resistance and humidity | without obstruction. The influence of moisture by potentially present groundwater is rightly not mentioned by the standard, except in the data for the Netherlands: 'sub-soil water level near to cables'.
Thermische weerstand | Thermal resistance | present groundwater is rightly not mentioned by the standard, except in the data for the Netherlands: 'sub-soil water level near to cables'. Table 4.4 Relationship between thermal resistance and humidity
K·m/W | K·m/W | is rightly not mentioned by the standard, except in the data for the Netherlands: 'sub-soil water level near to cables'. Table 4.4 Relationship between thermal resistance and humidity Thermal resistance
Bodemconditie | Bodemconditie | rightly not mentioned by the standard, except in the data for the Netherlands: 'sub-soil water level near to cables'. Table 4.4 Relationship between thermal resistance and humidity Thermal resistance K·m/W
Weersconditie | Weersconditie | not mentioned by the standard, except in the data for the Netherlands: 'sub-soil water level near to cables'. Table 4.4 Relationship between thermal resistance and humidity Thermal resistance K·m/W Bodemconditie
0,7 | 0.7 | mentioned by the standard, except in the data for the Netherlands: 'sub-soil water level near to cables'. Table 4.4 Relationship between thermal resistance and humidity Thermal resistance K·m/W Bodemconditie Weersconditie
Zeer vochtig | Very moist | by the standard, except in the data for the Netherlands: 'sub-soil water level near to cables'. Table 4.4 Relationship between thermal resistance and humidity Thermal resistance K·m/W Bodemconditie Weersconditie 0.7
Continu vochtig | Continuously moist | standard, except in the data for the Netherlands: 'sub-soil water level near to cables'. Table 4.4 Relationship between thermal resistance and humidity Thermal resistance K·m/W Bodemconditie Weersconditie 0.7 Very moist
1,0 | 1.0 | in the data for the Netherlands: 'sub-soil water level near to cables'. Table 4.4 Relationship between thermal resistance and humidity Thermal resistance K·m/W Bodemconditie Weersconditie 0.7 Very moist Continuously moist
Vochtig | Vochtig | the data for the Netherlands: 'sub-soil water level near to cables'. Table 4.4 Relationship between thermal resistance and humidity Thermal resistance K·m/W Bodemconditie Weersconditie 0.7 Very moist Continuously moist 1.0
Regelmatige regen | Regular rain | data for the Netherlands: 'sub-soil water level near to cables'. Table 4.4 Relationship between thermal resistance and humidity Thermal resistance K·m/W Bodemconditie Weersconditie 0.7 Very moist Continuously moist 1.0 Vochtig
2,0 | 2.0 | the Netherlands: 'sub-soil water level near to cables'. Table 4.4 Relationship between thermal resistance and humidity Thermal resistance K·m/W Bodemconditie Weersconditie 0.7 Very moist Continuously moist 1.0 Vochtig Regular rain
Droog | Droog | Netherlands: 'sub-soil water level near to cables'. Table 4.4 Relationship between thermal resistance and humidity Thermal resistance K·m/W Bodemconditie Weersconditie 0.7 Very moist Continuously moist 1.0 Vochtig Regular rain 2.0
Zelden regen | Rarely rain | 'sub-soil water level near to cables'. Table 4.4 Relationship between thermal resistance and humidity Thermal resistance K·m/W Bodemconditie Weersconditie 0.7 Very moist Continuously moist 1.0 Vochtig Regular rain 2.0 Droog
3,0 | 3.0 | level near to cables'. Table 4.4 Relationship between thermal resistance and humidity Thermal resistance K·m/W Bodemconditie Weersconditie 0.7 Very moist Continuously moist 1.0 Vochtig Regular rain 2.0 Droog Rarely rain
Zeer droog | Very dry | near to cables'. Table 4.4 Relationship between thermal resistance and humidity Thermal resistance K·m/W Bodemconditie Weersconditie 0.7 Very moist Continuously moist 1.0 Vochtig Regular rain 2.0 Droog Rarely rain 3.0
Weinig of geen regen | Little or no rain | cables'. Table 4.4 Relationship between thermal resistance and humidity Thermal resistance K·m/W Bodemconditie Weersconditie 0.7 Very moist Continuously moist 1.0 Vochtig Regular rain 2.0 Droog Rarely rain 3.0 Very dry
Grondwater | Grondwater | between thermal resistance and humidity Thermal resistance K·m/W Bodemconditie Weersconditie 0.7 Very moist Continuously moist 1.0 Vochtig Regular rain 2.0 Droog Rarely rain 3.0 Very dry Little or no rain
Wereldwijd gezien is het een grote uitzondering dat de diepte waarop het grondwaterpeil ligt van invloed is op de vochtigheid van het zand in de kabelsleuf. Dit komt omdat het maaiveld meestal veel hoger ligt dan het zeewaterniveau of hoger dan het niveau van bijvoorbeeld een rivier/kanaal of een (groot) meer in de omgeving. In de Sahara ligt het grondwater vaak dieper dan 25 m. In Nederland bestaan er zelfs plekken waar het grondwaterpeil nog veel dieper ligt. In de buurt van Hoog-Soeren op de Veluwe bijvoorbeeld is ooit een peil van meer dan 71 m gemeten en in Limburg is het eens op een diepte van 200 m onder het maaiveld gemeten. Er bestaan regionale Nederlandse kaarten waarop het grondwaterpeil op wordt aangegeven. | Globally, it is a rare exception that the depth at which the groundwater level lies affects the moisture content of the sand in the cable trench. This is because the ground level is usually much higher than sea level or higher than the level of, for example, a river/canal or a (large) lake in the vicinity. In the Sahara, the groundwater is often deeper than 25 meters. In the Netherlands, there are even places where the groundwater level is much deeper. Near Hoog-Soeren on the Veluwe, for example, a level of more than 71 meters has been measured, and in Limburg, it has once been measured at a depth of 200 meters below ground level. There are regional Dutch maps that indicate the groundwater level. | thermal resistance and humidity Thermal resistance K·m/W Bodemconditie Weersconditie 0.7 Very moist Continuously moist 1.0 Vochtig Regular rain 2.0 Droog Rarely rain 3.0 Very dry Little or no rain Grondwater
In permanent natte gebieden, dus daar waar het grondwaterpeil bijna permanent vlak onder het maaiveld ligt, is de invloed van neerslag groot. Indien het grondwaterpeil dieper ligt, kan het peil seizoensafhankelijk variëren. Bemaling van het gebied kan het grondwaterpeil permanent verlagen. Verstandig is om plaatselijk of in het kabeltracé metingen te doen en na te gaan of er plannen bestaan om het grondwaterpeil te veranderen. Voor kabels die op een installatiediepte blijvend onder het grond­water­peil liggen, in een goed gecompacteerde en met zand gevulde kabelsleuf, geldt: ρ | In permanently wet areas, where the groundwater level is almost permanently just below the surface, the influence of precipitation is significant. If the groundwater level is deeper, it can vary seasonally. Pumping the area can permanently lower the groundwater level. It is wise to conduct measurements locally or along the cable route and check if there are plans to change the groundwater level. For cables that are installed at a depth permanently below the groundwater level, in a well-compacted and sand-filled cable trench, the following applies: ρ | has been measured, and in Limburg, it has once been measured at a depth of 200 meters below ground level. There are regional Dutch maps that indicate the groundwater level.
T | T | plans to change the groundwater level. For cables that are installed at a depth permanently below the groundwater level, in a well-compacted and sand-filled cable trench, the following applies: ρ
≈ 0.5 K·m/W. | ≈ 0.5 K·m/W. | to change the groundwater level. For cables that are installed at a depth permanently below the groundwater level, in a well-compacted and sand-filled cable trench, the following applies: ρ T
De lokale grond | The local soil | groundwater level. For cables that are installed at a depth permanently below the groundwater level, in a well-compacted and sand-filled cable trench, the following applies: ρ T ≈ 0.5 K·m/W.
Een grove indeling van de bewerkbare grond is: | A rough classification of arable soil is: | cables that are installed at a depth permanently below the groundwater level, in a well-compacted and sand-filled cable trench, the following applies: ρ T ≈ 0.5 K·m/W. The local soil
Niet organisch materiaal: | Non-organic material: | permanently below the groundwater level, in a well-compacted and sand-filled cable trench, the following applies: ρ T ≈ 0.5 K·m/W. The local soil A rough classification of arable soil is:
Klei (leem = silt = löss = Limburgse klei) | Clay (loam = silt = loess = Limburg clay) | the groundwater level, in a well-compacted and sand-filled cable trench, the following applies: ρ T ≈ 0.5 K·m/W. The local soil A rough classification of arable soil is: Non-organic material:
Zand | Zand | trench, the following applies: ρ T ≈ 0.5 K·m/W. The local soil A rough classification of arable soil is: Non-organic material: Clay (loam = silt = loess = Limburg clay)
Organisch materiaal: | Organic material: | the following applies: ρ T ≈ 0.5 K·m/W. The local soil A rough classification of arable soil is: Non-organic material: Clay (loam = silt = loess = Limburg clay) Zand
Veen (laag en hoog) | Peat (low and high) | applies: ρ T ≈ 0.5 K·m/W. The local soil A rough classification of arable soil is: Non-organic material: Clay (loam = silt = loess = Limburg clay) Zand Organic material:
Materiaal dat na verwarming en verdampen van het aanwezige vocht uitdroogt en een onomkeerbare verandering van de permeabiliteit heeft, is niet acceptabel als ‘bedding’ materiaal. Klei/leem en veen zijn daarom niet geschikt om gebruikt te worden in kabelsleuven. Klei wordt namelijk ‘gebakken’ en vormt dan een voor water ondoordringbare schil om de kabel (ρ | Material that dries out after heating and evaporation of the present moisture and undergoes an irreversible change in permeability is not acceptable as 'bedding' material. Clay/loam and peat are therefore not suitable for use in cable trenches. Clay, for instance, gets 'baked' and then forms a water-impermeable shell around the cable (ρ | 0.5 K·m/W. The local soil A rough classification of arable soil is: Non-organic material: Clay (loam = silt = loess = Limburg clay) Zand Organic material: Peat (low and high)
T | T | as 'bedding' material. Clay/loam and peat are therefore not suitable for use in cable trenches. Clay, for instance, gets 'baked' and then forms a water-impermeable shell around the cable (ρ
≈ 7 K·m/W). Plantenresten (veen) hebben de zelfde eigenschap (ρ | ≈ 7 K·m/W). Plant residues (peat) have the same property (ρ | 'bedding' material. Clay/loam and peat are therefore not suitable for use in cable trenches. Clay, for instance, gets 'baked' and then forms a water-impermeable shell around the cable (ρ T
T | T | in cable trenches. Clay, for instance, gets 'baked' and then forms a water-impermeable shell around the cable (ρ T ≈ 7 K·m/W). Plant residues (peat) have the same property (ρ
≈ 4 K·m/W). | ≈ 4 K·m/W). | cable trenches. Clay, for instance, gets 'baked' and then forms a water-impermeable shell around the cable (ρ T ≈ 7 K·m/W). Plant residues (peat) have the same property (ρ T
Het ‘bedding’ materiaal | The 'bedding' material | for instance, gets 'baked' and then forms a water-impermeable shell around the cable (ρ T ≈ 7 K·m/W). Plant residues (peat) have the same property (ρ T ≈ 4 K·m/W).
Een bedding voor een kabel van samengestelde materiaalmengsels heeft thermische eigenschappen die goed bekend kunnen zijn. Dit is noodzakelijk bij thermisch zwaar belaste kabeltracés. Het enige juiste ‘bedding’ materiaal (backfill) voor de kabels is schoon kwarts zand. Dit zand is van alle bodemmineralen de beste warmtegeleider. De thermische weerstand is ondermeer afhankelijk van de samenstelling, korrelgrootte, compactheid, temperatuur en vochtpercentage. In laboratoriumproeven (Heinhold, 1999) zijn metingen uitgevoerd aan bodemsoorten. De metingen aan uitgedroogde grond resulteerde in thermische weerstanden tussen 1 en 4 Km/W. De verhouding tussen de hoeveelheid grote en kleine korrels geeft de diversiteit in korrelgrootte aan. Zand met een grote diversiteit in korrelgrootte heeft de kleinste thermische weerstand. Bij zand met een kleine diversiteit zijn waardes boven de 3 Km/W gemeten. Figuur 4.5 geeft in curven de thermische weerstand van zandmengsels met grote en kleine diversiteit van korrelgrootte als functie van het volumepercentage vocht. Ook is de thermische weerstand van leemhoudend zand weergegeven. | A bedding for a cable made of composite material mixtures has thermal properties that can be well known. This is necessary for thermally heavily loaded cable routes. The only correct 'bedding' material (backfill) for the cables is clean quartz sand. This sand is the best thermal conductor of all soil minerals. The thermal resistance depends, among other things, on the composition, grain size, compactness, temperature, and moisture content. In laboratory tests (Heinhold, 1999), measurements were conducted on soil types. The measurements on dried soil resulted in thermal resistances between 1 and 4 Km/W. The ratio between the amount of large and small grains indicates the diversity in grain size. Sand with a high diversity in grain size has the lowest thermal resistance. For sand with low diversity, values above 3 Km/W were measured. Figure 4.5 shows in curves the thermal resistance of sand mixtures with high and low diversity in grain size as a function of the volume percentage of moisture. The thermal resistance of loamy sand is also shown. | 'baked' and then forms a water-impermeable shell around the cable (ρ T ≈ 7 K·m/W). Plant residues (peat) have the same property (ρ T ≈ 4 K·m/W). The 'bedding' material
Figuur 4.5 Thermische weerstand van diverse zandmengsels | Figure 4.5 Thermal resistance of various sand mixtures | resistance of sand mixtures with high and low diversity in grain size as a function of the volume percentage of moisture. The thermal resistance of loamy sand is also shown.
Figuur 4.5 geeft tevens met gestreepte lijnen de niveaus weer van de relatie tussen vocht en thermische weerstand volgens tabel 4.4. Hiermee is te zien dat voor een vochtig gebied met regelmatig regen volgens IEC 60287-3-1 met een thermische weerstand van 1 Km/W gerekend mag worden, terwijl dit volgens de curven van figuur 4.5 toch duidelijk genuanceerder ligt. Bij zand met een kleine korreldiversiteit mag gerekend worden op waarden tussen 0,5 en 1,2 Km/W, maar bij zand met een grote korreldiversiteit op waarden tussen 1,0 en 3,8 Km/W. Hierom is het goed voor te stellen dat men, rekening houdend met de maximale buitenmanteltemperatuur en de uitdroging die dit als gevolg kan hebben, bij gebrek aan gegevens liever uitgaat van een waarde voor de thermische weerstand van uitgedroogd zand van 2,5 Km/W. | Figure 4.5 also shows the levels of the relationship between moisture and thermal resistance according to Table 4.4 with dashed lines. This shows that for a humid area with regular rain, according to IEC 60287-3-1, a thermal resistance of 1 Km/W can be assumed, while the curves in Figure 4.5 indicate a more nuanced situation. For sand with low grain diversity, values between 0.5 and 1.2 Km/W can be expected, but for sand with high grain diversity, values between 1.0 and 3.8 Km/W can be expected. Therefore, it is reasonable to assume, considering the maximum outer sheath temperature and the drying effect it can have, that in the absence of specific data, a thermal resistance value of 2.5 Km/W for dried sand is preferred. | diversity in grain size as a function of the volume percentage of moisture. The thermal resistance of loamy sand is also shown. Figure 4.5 Thermal resistance of various sand mixtures
De vochtigheid van zand hangt af van de hoeveelheid regen en van de hoeveelheid grondwater, die tot het kabelbed kunnen doordringen. Tabel 4.5 geeft een overzicht van de thermische weerstand van zand, klei en veen voor diverse vochtigheden. De tabel is afgeleid uit diverse tabellen van thermische geleidbaarheid van materialen (Engineering, 2011), (De Vries, 1963). Er is geen eenduidigheid in de internationaal gehanteerde waarden, zodat de waarden in de tabel indicatief zijn. Voor alle duidelijkheid: aarde, klei en veen zijn alleen in de tabel opgenomen ter vergelijking. | The moisture content of sand depends on the amount of rain and the amount of groundwater that can penetrate the cable bed. Table 4.5 provides an overview of the thermal resistance of sand, clay, and peat for various moisture levels. The table is derived from various tables of thermal conductivity of materials (Engineering, 2011), (De Vries, 1963). There is no consensus on the internationally used values, so the values in the table are indicative. For clarity: soil, clay, and peat are included in the table for comparison purposes only. | maximum outer sheath temperature and the drying effect it can have, that in the absence of specific data, a thermal resistance value of 2.5 Km/W for dried sand is preferred.
Tabel 4.5 Eigenschappen van bodemmateriaal | Table 4.5 Properties of Soil Material | no consensus on the internationally used values, so the values in the table are indicative. For clarity: soil, clay, and peat are included in the table for comparison purposes only.
Materiaal | Materiaal | values, so the values in the table are indicative. For clarity: soil, clay, and peat are included in the table for comparison purposes only. Table 4.5 Properties of Soil Material
Conditie | Conditie | so the values in the table are indicative. For clarity: soil, clay, and peat are included in the table for comparison purposes only. Table 4.5 Properties of Soil Material Materiaal
Minimale | Minimale | the values in the table are indicative. For clarity: soil, clay, and peat are included in the table for comparison purposes only. Table 4.5 Properties of Soil Material Materiaal Conditie
ρ | ρ | values in the table are indicative. For clarity: soil, clay, and peat are included in the table for comparison purposes only. Table 4.5 Properties of Soil Material Materiaal Conditie Minimale
T | T | in the table are indicative. For clarity: soil, clay, and peat are included in the table for comparison purposes only. Table 4.5 Properties of Soil Material Materiaal Conditie Minimale ρ
(K | (K) | the table are indicative. For clarity: soil, clay, and peat are included in the table for comparison purposes only. Table 4.5 Properties of Soil Material Materiaal Conditie Minimale ρ T
·m/W) | ·m/W) | table are indicative. For clarity: soil, clay, and peat are included in the table for comparison purposes only. Table 4.5 Properties of Soil Material Materiaal Conditie Minimale ρ T (K)
Maximale ρ | Maximum ρ | are indicative. For clarity: soil, clay, and peat are included in the table for comparison purposes only. Table 4.5 Properties of Soil Material Materiaal Conditie Minimale ρ T (K) ·m/W)
T | T | For clarity: soil, clay, and peat are included in the table for comparison purposes only. Table 4.5 Properties of Soil Material Materiaal Conditie Minimale ρ T (K) ·m/W) Maximum ρ
·m/W) | ·m/W) | clarity: soil, clay, and peat are included in the table for comparison purposes only. Table 4.5 Properties of Soil Material Materiaal Conditie Minimale ρ T (K) ·m/W) Maximum ρ T
Zand | Zand | soil, clay, and peat are included in the table for comparison purposes only. Table 4.5 Properties of Soil Material Materiaal Conditie Minimale ρ T (K) ·m/W) Maximum ρ T ·m/W)
Verzadigd met water | Saturated with water | clay, and peat are included in the table for comparison purposes only. Table 4.5 Properties of Soil Material Materiaal Conditie Minimale ρ T (K) ·m/W) Maximum ρ T ·m/W) Zand
0,25 | 0.25 | are included in the table for comparison purposes only. Table 4.5 Properties of Soil Material Materiaal Conditie Minimale ρ T (K) ·m/W) Maximum ρ T ·m/W) Zand Saturated with water
0,50 | 0.50 | included in the table for comparison purposes only. Table 4.5 Properties of Soil Material Materiaal Conditie Minimale ρ T (K) ·m/W) Maximum ρ T ·m/W) Zand Saturated with water 0.25
Zand | Zand | in the table for comparison purposes only. Table 4.5 Properties of Soil Material Materiaal Conditie Minimale ρ T (K) ·m/W) Maximum ρ T ·m/W) Zand Saturated with water 0.25 0.50
Vochtig | Vochtig | the table for comparison purposes only. Table 4.5 Properties of Soil Material Materiaal Conditie Minimale ρ T (K) ·m/W) Maximum ρ T ·m/W) Zand Saturated with water 0.25 0.50 Zand
0,50 | 0.50 | table for comparison purposes only. Table 4.5 Properties of Soil Material Materiaal Conditie Minimale ρ T (K) ·m/W) Maximum ρ T ·m/W) Zand Saturated with water 0.25 0.50 Zand Vochtig
1,00 | 1.00 | for comparison purposes only. Table 4.5 Properties of Soil Material Materiaal Conditie Minimale ρ T (K) ·m/W) Maximum ρ T ·m/W) Zand Saturated with water 0.25 0.50 Zand Vochtig 0.50
Zand | Zand | comparison purposes only. Table 4.5 Properties of Soil Material Materiaal Conditie Minimale ρ T (K) ·m/W) Maximum ρ T ·m/W) Zand Saturated with water 0.25 0.50 Zand Vochtig 0.50 1.00
Droog | Droog | purposes only. Table 4.5 Properties of Soil Material Materiaal Conditie Minimale ρ T (K) ·m/W) Maximum ρ T ·m/W) Zand Saturated with water 0.25 0.50 Zand Vochtig 0.50 1.00 Zand
1,00 | 1.00 | only. Table 4.5 Properties of Soil Material Materiaal Conditie Minimale ρ T (K) ·m/W) Maximum ρ T ·m/W) Zand Saturated with water 0.25 0.50 Zand Vochtig 0.50 1.00 Zand Droog
3,00 | 3.00 | Table 4.5 Properties of Soil Material Materiaal Conditie Minimale ρ T (K) ·m/W) Maximum ρ T ·m/W) Zand Saturated with water 0.25 0.50 Zand Vochtig 0.50 1.00 Zand Droog 1.00
Zand | Zand | 4.5 Properties of Soil Material Materiaal Conditie Minimale ρ T (K) ·m/W) Maximum ρ T ·m/W) Zand Saturated with water 0.25 0.50 Zand Vochtig 0.50 1.00 Zand Droog 1.00 3.00
Zeer droog | Very dry | Properties of Soil Material Materiaal Conditie Minimale ρ T (K) ·m/W) Maximum ρ T ·m/W) Zand Saturated with water 0.25 0.50 Zand Vochtig 0.50 1.00 Zand Droog 1.00 3.00 Zand
3,00 | 3.00 | Soil Material Materiaal Conditie Minimale ρ T (K) ·m/W) Maximum ρ T ·m/W) Zand Saturated with water 0.25 0.50 Zand Vochtig 0.50 1.00 Zand Droog 1.00 3.00 Zand Very dry
6,67 | 6.67 | Material Materiaal Conditie Minimale ρ T (K) ·m/W) Maximum ρ T ·m/W) Zand Saturated with water 0.25 0.50 Zand Vochtig 0.50 1.00 Zand Droog 1.00 3.00 Zand Very dry 3.00
Aarde | Aarde | Materiaal Conditie Minimale ρ T (K) ·m/W) Maximum ρ T ·m/W) Zand Saturated with water 0.25 0.50 Zand Vochtig 0.50 1.00 Zand Droog 1.00 3.00 Zand Very dry 3.00 6.67
Droog | Droog | Conditie Minimale ρ T (K) ·m/W) Maximum ρ T ·m/W) Zand Saturated with water 0.25 0.50 Zand Vochtig 0.50 1.00 Zand Droog 1.00 3.00 Zand Very dry 3.00 6.67 Aarde
0,67 | 0.67 | Minimale ρ T (K) ·m/W) Maximum ρ T ·m/W) Zand Saturated with water 0.25 0.50 Zand Vochtig 0.50 1.00 Zand Droog 1.00 3.00 Zand Very dry 3.00 6.67 Aarde Droog
Klei | Klei | ρ T (K) ·m/W) Maximum ρ T ·m/W) Zand Saturated with water 0.25 0.50 Zand Vochtig 0.50 1.00 Zand Droog 1.00 3.00 Zand Very dry 3.00 6.67 Aarde Droog 0.67
Verzadigd met water | Saturated with water | T (K) ·m/W) Maximum ρ T ·m/W) Zand Saturated with water 0.25 0.50 Zand Vochtig 0.50 1.00 Zand Droog 1.00 3.00 Zand Very dry 3.00 6.67 Aarde Droog 0.67 Klei
0,40 | 0.40 | Maximum ρ T ·m/W) Zand Saturated with water 0.25 0.50 Zand Vochtig 0.50 1.00 Zand Droog 1.00 3.00 Zand Very dry 3.00 6.67 Aarde Droog 0.67 Klei Saturated with water
1,67 | 1.67 | ρ T ·m/W) Zand Saturated with water 0.25 0.50 Zand Vochtig 0.50 1.00 Zand Droog 1.00 3.00 Zand Very dry 3.00 6.67 Aarde Droog 0.67 Klei Saturated with water 0.40
Klei | Klei | T ·m/W) Zand Saturated with water 0.25 0.50 Zand Vochtig 0.50 1.00 Zand Droog 1.00 3.00 Zand Very dry 3.00 6.67 Aarde Droog 0.67 Klei Saturated with water 0.40 1.67
Vochtig | Vochtig | ·m/W) Zand Saturated with water 0.25 0.50 Zand Vochtig 0.50 1.00 Zand Droog 1.00 3.00 Zand Very dry 3.00 6.67 Aarde Droog 0.67 Klei Saturated with water 0.40 1.67 Klei
0,56 | 0.56 | Zand Saturated with water 0.25 0.50 Zand Vochtig 0.50 1.00 Zand Droog 1.00 3.00 Zand Very dry 3.00 6.67 Aarde Droog 0.67 Klei Saturated with water 0.40 1.67 Klei Vochtig
6,67 | 6.67 | Saturated with water 0.25 0.50 Zand Vochtig 0.50 1.00 Zand Droog 1.00 3.00 Zand Very dry 3.00 6.67 Aarde Droog 0.67 Klei Saturated with water 0.40 1.67 Klei Vochtig 0.56
Veen | Veen | with water 0.25 0.50 Zand Vochtig 0.50 1.00 Zand Droog 1.00 3.00 Zand Very dry 3.00 6.67 Aarde Droog 0.67 Klei Saturated with water 0.40 1.67 Klei Vochtig 0.56 6.67
Verzadigd - vochtig | Saturated - moist | water 0.25 0.50 Zand Vochtig 0.50 1.00 Zand Droog 1.00 3.00 Zand Very dry 3.00 6.67 Aarde Droog 0.67 Klei Saturated with water 0.40 1.67 Klei Vochtig 0.56 6.67 Veen
0,25 | 0.25 | Zand Vochtig 0.50 1.00 Zand Droog 1.00 3.00 Zand Very dry 3.00 6.67 Aarde Droog 0.67 Klei Saturated with water 0.40 1.67 Klei Vochtig 0.56 6.67 Veen Saturated - moist
4,00 | 4.00 | Vochtig 0.50 1.00 Zand Droog 1.00 3.00 Zand Very dry 3.00 6.67 Aarde Droog 0.67 Klei Saturated with water 0.40 1.67 Klei Vochtig 0.56 6.67 Veen Saturated - moist 0.25
Omdat een bedding van zand ‘poreus’ blijft kan mogelijk verdampend vocht worden vervangen door neerslag en als het grondwaterpeil hoog genoeg is door grondwater. Vocht kan ook zijdelings uit de bestaande lokale bodem in de kabelsleuf binnendringen, mits de kabelsleuf geen gesloten zijwanden heeft. | Because a bed of sand remains 'porous,' evaporating moisture can potentially be replaced by precipitation and, if the groundwater level is high enough, by groundwater. Moisture can also laterally penetrate the cable trench from the existing local soil, provided the cable trench does not have closed sidewalls. | 0.50 1.00 Zand Droog 1.00 3.00 Zand Very dry 3.00 6.67 Aarde Droog 0.67 Klei Saturated with water 0.40 1.67 Klei Vochtig 0.56 6.67 Veen Saturated - moist 0.25 4.00
De meeste industrieterreinen zijn geëgaliseerd met zand of zijn met zand opgespoten terreinen. Het geheel terugvullen van de kabelsleuf met schoon zand is dan geen probleem. Kabels, geïnstalleerd buiten industrieterreinen, liggen meestal in andere grondsoorten zoals in veen of in klei. Het is ver­standig om altijd zand te gebruiken als bedding omdat zand de kleinste thermische weerstand heeft. | Most industrial areas are leveled with sand or are sand-filled sites. Completely backfilling the cable trench with clean sand is then not a problem. Cables installed outside industrial areas are usually in other types of soil, such as peat or clay. It is advisable to always use sand as bedding because sand has the lowest thermal resistance. | the groundwater level is high enough, by groundwater. Moisture can also laterally penetrate the cable trench from the existing local soil, provided the cable trench does not have closed sidewalls.
Figuur 4.6 Rivierzand | Figure 4.6 River Sand | industrial areas are usually in other types of soil, such as peat or clay. It is advisable to always use sand as bedding because sand has the lowest thermal resistance.
Figuur 4.7 Het leggen van een 10 kV-kabel | Figure 4.7 Laying a 10 kV cable | in other types of soil, such as peat or clay. It is advisable to always use sand as bedding because sand has the lowest thermal resistance. Figure 4.6 River Sand
Het zand kan een hoeveelheid water opnemen, terwijl het volume van het zand niet verandert. Het water moet de alleen ruimten tussen de zandkorrels opvullen. Als bijvoorbeeld 100 liter water door 1 m | The sand can absorb a certain amount of water without changing its volume. The water only needs to fill the spaces between the sand grains. For example, if 100 liters of water pass through 1 m | peat or clay. It is advisable to always use sand as bedding because sand has the lowest thermal resistance. Figure 4.6 River Sand Figure 4.7 Laying a 10 kV cable
3 | 3 | amount of water without changing its volume. The water only needs to fill the spaces between the sand grains. For example, if 100 liters of water pass through 1 m
zand opgenomen is, bevat dit 10 vol % vocht. Het maximum vol % vocht dat door zand met een droge dichtheid van ongeveer 1700 kg/m | sand is absorbed, it contains 10 vol % moisture. The maximum vol % moisture that can be absorbed by sand with a dry density of approximately 1700 kg/m | of water without changing its volume. The water only needs to fill the spaces between the sand grains. For example, if 100 liters of water pass through 1 m 3
3 | 3 | m 3 sand is absorbed, it contains 10 vol % moisture. The maximum vol % moisture that can be absorbed by sand with a dry density of approximately 1700 kg/m
kan worden opgenomen is ongeveer 15%. | can be absorbed is approximately 15%. | 3 sand is absorbed, it contains 10 vol % moisture. The maximum vol % moisture that can be absorbed by sand with a dry density of approximately 1700 kg/m 3
Bij een gegeven volumepercentage water heeft zand met een hoge dichtheid een lagere thermische weerstand dan zand met een lagere dichtheid. Daarom is naast de korrelgrootte van het zand ook het compacteren na het storten van het natte zand belangrijk. Bij gecompacteerd zand kan met een lager volumepercentage vocht worden volstaan om dezelfde thermische weerstand te bereiken dan bij niet gecompacteerd zand. Het inspoelen van het zand met water is overigens geen compacteer­methode, want waar water zit kunnen geen zandkorrels zijn en als het water na verloop van tijd wegzakt blijven er met lucht gevulde ruimtes over tussen de zandkorrels. | At a given volume percentage of water, sand with a high density has a lower thermal resistance than sand with a lower density. Therefore, in addition to the grain size of the sand, compacting the wet sand after pouring is also important. With compacted sand, a lower volume percentage of moisture is sufficient to achieve the same thermal resistance as with non-compacted sand. Washing the sand with water is not a compaction method, because where there is water, there cannot be sand grains, and as the water eventually drains away, air-filled spaces remain between the sand grains. | 10 vol % moisture. The maximum vol % moisture that can be absorbed by sand with a dry density of approximately 1700 kg/m 3 can be absorbed is approximately 15%.
Door het uitgraven van de kabelsleuf wordt de bodem verstoord. Het beddingmateriaal in de gehele kabelsleuf kan meestal niet zo goed worden gecompacteerd (verdicht) dat de oorspronkelijk gunstige eigenschappen van de ongestoorde bodem worden geëvenaard. Het kan zelfs zo zijn dat de kabelsleuf met beddingmateriaal een grotere thermische weerstand heeft dan de oorspronkelijke bodem. Toch wordt hiervoor gekozen om de kans op uitdroging van het oorspronkelijke bodemmateriaal te verkleinen en de nieuwe omgevingscondities hierdoor bekend zijn. Meer specifieke informatie is te vinden in de literatuur (Heinhold, 1999). | Excavating the cable trench disturbs the soil. The bedding material in the entire cable trench usually cannot be compacted (densified) to match the originally favorable properties of the undisturbed soil. It may even be that the cable trench with bedding material has a higher thermal resistance than the original soil. Nevertheless, this method is chosen to reduce the risk of drying out the original soil material and because the new environmental conditions are thus known. More specific information can be found in the literature (Heinhold, 1999). | water is not a compaction method, because where there is water, there cannot be sand grains, and as the water eventually drains away, air-filled spaces remain between the sand grains.
Uitdroging | Uitdroging | reduce the risk of drying out the original soil material and because the new environmental conditions are thus known. More specific information can be found in the literature (Heinhold, 1999).
Als van een continu vol belaste kabel op een diepte van 0,7 m en bij een grond temperatuur van 20 °C de temperatuur aan de omtrek van de buitenmantel ongeveer 35 °C is, begint het verdampingsproces van het vocht in het zand direct rondom de kabel (VDE 0298 Teil 2). Toen nog alleen papierisolatie werd gebruikt, waren problemen door uitdroging niet aan de orde omdat de adertemperatuur bij papierkabel begrensd was tot 50 °C en de mantel temperatuur lager was dan 35 °C. Zand en ook klei konden daardoor bijna niet uitdrogen. Met de komst van XLPE geïsoleerde kabel kan bij een maximale geleidertemperatuur van 90°C de mantel temperatuur oplopen naar ongeveer 75 °C, waardoor goed gelet moet worden op het gevaar van uitdroging van de grond. | If the temperature at the circumference of the outer sheath of a continuously fully loaded cable at a depth of 0.7 m and with a ground temperature of 20 °C is approximately 35 °C, the evaporation process of the moisture in the sand directly around the cable begins (VDE 0298 Part 2). When only paper insulation was used, drying out problems were not an issue because the conductor temperature for paper cables was limited to 50 °C and the sheath temperature was lower than 35 °C. As a result, sand and clay could hardly dry out. With the advent of XLPE insulated cables, the sheath temperature can rise to approximately 75 °C at a maximum conductor temperature of 90 °C, which means careful attention must be paid to the risk of soil drying out. | the risk of drying out the original soil material and because the new environmental conditions are thus known. More specific information can be found in the literature (Heinhold, 1999). Uitdroging
Het risico van uitdroging bestaat als het aan de omtrek van de kabelmantel verdampte vocht niet ‘vervangen’ wordt door ander vocht. Deze situatie kan optreden als: | The risk of drying out exists if the moisture evaporated around the cable sheath is not 'replaced' by other moisture. This situation can occur if: | sheath temperature can rise to approximately 75 °C at a maximum conductor temperature of 90 °C, which means careful attention must be paid to the risk of soil drying out.
het binnendringen van neerslag in de kabelsleuf en in directe omgeving bemoeilijkt of onmogelijk is (door bestrating, vloeistofdichte toplaag en zijwanden) of | the infiltration of precipitation into the cable trench and its immediate surroundings is hindered or impossible (due to paving, liquid-tight top layer, and side walls) or | risk of soil drying out. The risk of drying out exists if the moisture evaporated around the cable sheath is not 'replaced' by other moisture. This situation can occur if:
doordat er (veel) minder neerslag is dan oorspronkelijk verwacht was of | because there is (much) less precipitation than originally expected or | situation can occur if: the infiltration of precipitation into the cable trench and its immediate surroundings is hindered or impossible (due to paving, liquid-tight top layer, and side walls) or
doordat het grondwaterpeil is gezakt. | because the groundwater level has dropped. | cable trench and its immediate surroundings is hindered or impossible (due to paving, liquid-tight top layer, and side walls) or because there is (much) less precipitation than originally expected or
Onder bestrating | Under paving | is hindered or impossible (due to paving, liquid-tight top layer, and side walls) or because there is (much) less precipitation than originally expected or because the groundwater level has dropped.
Een kruising van een kabelsleuf met een weg, kan onder de weg uitdroging van het zand om de kabels tot gevolg hebben. Onder elke (gedeeltelijke) waterdichte afdekking van de sleuf met meer dan één meter lengte bestaat dit gevaar. Ook doet zich de situatie voor dat vóór installatie van de kabels onder een toplaag van asfalt of beton de bodem­tempera­tuur in de zomer 5 °C of meer hoger kan zijn dan de temperatuur van de grond in het open veld (op de zelfde diepte gemeten). Dit komt door de opwarming van het asfalt of het beton door de zonnewarmte. | A crossing of a cable trench with a road can result in the drying out of the sand around the cables under the road. This danger exists under any (partially) watertight covering of the trench longer than one meter. Additionally, the situation can occur where, before the installation of the cables under a layer of asphalt or concrete, the soil temperature in the summer can be 5°C or more higher than the temperature of the ground in an open field (measured at the same depth). This is due to the heating of the asphalt or concrete by solar heat. | or impossible (due to paving, liquid-tight top layer, and side walls) or because there is (much) less precipitation than originally expected or because the groundwater level has dropped. Under paving
Onder een vloeistofdichte toplaag | Under a liquid-tight top layer | higher than the temperature of the ground in an open field (measured at the same depth). This is due to the heating of the asphalt or concrete by solar heat.
In industriële installaties liggen de met zand en back-fill gevulde kabelsleuven vaak tussen de beton­fundaties voor de apparaten of tussen (dure) zijdelingse betonnen wanden. Over de kabelsleuf moet dan meestal een vloeistofdichte en of een berijdbare toplaag worden aangebracht. Deze toplaag moet, indien het zand en de back-fill na enige tijd, ondanks het compacteren, toch nog iets inklinken, mee kunnen zakken om te voorkomen dat er een warmte isolerend luchtlaag(je) ρ | In industrial installations, the cable trenches filled with sand and back-fill are often located between the concrete foundations for the equipment or between (expensive) lateral concrete walls. Over the cable trench, a liquid-tight and/or drivable top layer usually needs to be applied. This top layer must be able to sink along with the sand and back-fill if they settle slightly over time, despite compaction, to prevent the formation of a heat-insulating air layer. | the ground in an open field (measured at the same depth). This is due to the heating of the asphalt or concrete by solar heat. Under a liquid-tight top layer
T | T | top layer must be able to sink along with the sand and back-fill if they settle slightly over time, despite compaction, to prevent the formation of a heat-insulating air layer.
≈ 40 K·m/W, ontstaat tussen de back-fill en de aangebrachte toplaag. | ≈ 40 K·m/W, forms between the back-fill and the applied top layer. | layer must be able to sink along with the sand and back-fill if they settle slightly over time, despite compaction, to prevent the formation of a heat-insulating air layer. T
Met het risico van bodemuitdroging rekening kan rekening worden gehouden door bij het ontwerp met een voldoend hoog gekozen waarde voor de specifieke thermische grondweerstand te rekenen of te rekenen met een maximum buitenmanteltemperatuur van de kabel. Het compleet uitdrogen van een operationele kabelsleuf kan enige tijd duren en kondigt zich pas aan als het te laat is. Een juiste inschatting van de waarde van ρ | The risk of soil drying can be taken into account by using a sufficiently high value for the specific thermal soil resistance in the design or by calculating with a maximum outer sheath temperature of the cable. The complete drying out of an operational cable trench can take some time and only becomes apparent when it is too late. An accurate estimation of the value of ρ | if they settle slightly over time, despite compaction, to prevent the formation of a heat-insulating air layer. T ≈ 40 K·m/W, forms between the back-fill and the applied top layer.
T | T | The complete drying out of an operational cable trench can take some time and only becomes apparent when it is too late. An accurate estimation of the value of ρ
met de minimum hoeveelheid vocht na een langdurig operationeel bedrijf is dus essentieel. Omdat ook hier geldt dat een keten is zo sterk is als de zwakste schakel, is de slechtste waarde van ρ | with the minimum amount of moisture after prolonged operational use is therefore essential. Because, as the saying goes, a chain is only as strong as its weakest link, the worst value of ρ | complete drying out of an operational cable trench can take some time and only becomes apparent when it is too late. An accurate estimation of the value of ρ T
T | T | amount of moisture after prolonged operational use is therefore essential. Because, as the saying goes, a chain is only as strong as its weakest link, the worst value of ρ
in het tracé doorslaggevend voor het hele kabel circuit. | in the route is decisive for the entire cable circuit. | of moisture after prolonged operational use is therefore essential. Because, as the saying goes, a chain is only as strong as its weakest link, the worst value of ρ T
Bodemtemperatuur | Bodemtemperatuur | as the saying goes, a chain is only as strong as its weakest link, the worst value of ρ T in the route is decisive for the entire cable circuit.
De bodemtemperatuur heeft grote invloed op de kabelbelastbaarheid. De temperatuur wordt beïnvloed door allerlei in de grond aanwezige warmteproducerende bronnen, zoals parallelle circuits en warmteleidingen. Ook seizoensinvloeden zoals zomer- en wintercondities mogen niet verwaarloosd worden. De seizoensinvloed kan tot 10 graden verschil in bodemtemperatuur veroorzaken. | The soil temperature has a significant impact on cable load capacity. The temperature is influenced by various heat-producing sources present in the ground, such as parallel circuits and heating pipes. Seasonal influences, such as summer and winter conditions, should also not be neglected. Seasonal influence can cause up to a 10-degree difference in soil temperature. | the saying goes, a chain is only as strong as its weakest link, the worst value of ρ T in the route is decisive for the entire cable circuit. Bodemtemperatuur
Berekening van de stroombelastbaarheid | Calculation of current-carrying capacity | parallel circuits and heating pipes. Seasonal influences, such as summer and winter conditions, should also not be neglected. Seasonal influence can cause up to a 10-degree difference in soil temperature.
De maximale belasting van de kabels wordt enerzijds begrensd door de maximale temperatuur die de isolatie toestaat en anderzijds door het uitdrogen van de grond rond de kabel. In Nederland kan de grond uitdrogen bij een geleidertemperatuur van 50 °C en hoger. Voor GPLK kabels beperkt het isolatiemateriaal de geleidertemperatuur tot 50 °C. De buitenmantel heeft dan een lagere temperatuur, waardoor bij deze kabels het risico op gronduitdroging niet groot is. Deze kabels kunnen zodoende nominaal worden belast. Vanwege de negatieve invloed op de levensduur wordt een tijdelijke overbelasting van deze kabels vermeden. XLPE-kabels staan hogere temperaturen van de isolatie toe dan GPLK-kabels. De maximaal toelaatbare geleidertemperatuur van deze kabel is 90 °C. Deze hoge temperatuur brengt een groot risico op uitdroging van de grond met zich mee. Uitdroging van de grond is een niet-omkeerbaar proces, waarbij de thermische eigenschap van de wijzigt. De thermische grondweerstand neemt toe met als gevolg dat de kabel blijvend zijn warmte minder goed afstaat. De geleidertemperatuur wordt dus beperkt door eisen te stellen aan de maximale buitenmanteltemperatuur, zodat de grond niet uitdroogt. De XLPE-kabels hebben zodoende een marge in de belastbaarheid. Door de traagheid van het opwarmingsproces is in specifieke omstandigheden een tijdelijke overbelasting toegestaan. Als voorbeeld wordt de belastbaarheid van een drie-aderige XLPE-kabel met 95 mm | The maximum load of the cables is limited on one hand by the maximum temperature that the insulation allows and on the other hand by the drying out of the soil around the cable. In the Netherlands, the soil can dry out at a conductor temperature of 50 °C and higher. For GPLK cables, the insulation material limits the conductor temperature to 50 °C. The outer sheath then has a lower temperature, so the risk of soil drying out with these cables is not significant. These cables can therefore be loaded nominally. Due to the negative impact on lifespan, temporary overloading of these cables is avoided. XLPE cables allow higher insulation temperatures than GPLK cables. The maximum allowable conductor temperature for these cables is 90 °C. This high temperature poses a significant risk of soil drying out. Soil drying is an irreversible process, which changes the thermal properties of the soil. The thermal soil resistance increases, resulting in the cable permanently dissipating its heat less effectively. Therefore, the conductor temperature is limited by setting requirements for the maximum outer sheath temperature to prevent soil drying. XLPE cables thus have a margin in load capacity. Due to the slow heating process, temporary overloading is allowed in specific circumstances. For example, the load capacity of a three-core XLPE cable with 95 mm | pipes. Seasonal influences, such as summer and winter conditions, should also not be neglected. Seasonal influence can cause up to a 10-degree difference in soil temperature. Calculation of current-carrying capacity
2 | 2 | margin in load capacity. Due to the slow heating process, temporary overloading is allowed in specific circumstances. For example, the load capacity of a three-core XLPE cable with 95 mm
koperen geleiders gegeven. De kabel is begraven op 1 m diepte in grond met een thermische weerstand van 1 Km/W en een omgevingstemperatuur van 15 °C. Bij deze omstandigheden kan deze kabel, uitgaande van een geleidertemperatuur van 90 °C maximaal een continue stroom voeren van 305 A. De temperatuur van de buitenmantel wordt dan 61 °C. Bij deze temperatuur zal de grond rondom de kabel uitdrogen. Om dit te voorkomen kan ervoor gekozen worden de temperatuur van de buitenmantel te begrenzen op 45 °C. In dat geval is de maximaal toegestane continue stroom 255 A. Uitgaande van deze stroomwaarde heeft de kabel een marge voor tijdelijke belastingen van 50 A. Indien een tijdelijke overbelasting wordt toegestaan, mag de belasting van deze kabel volgens de norm IEC 60853 in deze omstandigheden zelfs gedurende twee uren van 255 A naar 348 A worden verhoogd of gedurende vijf uren van 255 A naar 339 A. | copper conductors given. The cable is buried at a depth of 1 meter in soil with a thermal resistance of 1 Km/W and an ambient temperature of 15 °C. Under these conditions, this cable, assuming a conductor temperature of 90 °C, can carry a continuous current of up to 305 A. The temperature of the outer sheath will then be 61 °C. At this temperature, the soil around the cable will dry out. To prevent this, the temperature of the outer sheath can be limited to 45 °C. In that case, the maximum allowable continuous current is 255 A. Based on this current value, the cable has a margin for temporary loads of 50 A. If a temporary overload is allowed, the load on this cable, according to the IEC 60853 standard, can even be increased from 255 A to 348 A for two hours or from 255 A to 339 A for five hours under these conditions. | in load capacity. Due to the slow heating process, temporary overloading is allowed in specific circumstances. For example, the load capacity of a three-core XLPE cable with 95 mm 2
Met de in deze paragraaf beschreven omgevingsfactoren kan de belastbaarheid van een kabel met behulp van de internationaal erkende norm IEC 60287 exact uitgerekend worden (Phase, 2006). Het is echter niet altijd eenvoudig om aan de benodigde parameters te komen. Kabelfabrikanten specificeren de belastbaarheid van kabels voor nominale omstandigheden en zij geven correctiefactoren voor afwijkingen van temperaturen en liggingomstandigheden van de nominale waarden. Ook de norm NEN 1010 maakt gebruik van correctiefactoren. | With the environmental factors described in this paragraph, the load capacity of a cable can be precisely calculated using the internationally recognized standard IEC 60287 (Phase, 2006). However, it is not always easy to obtain the necessary parameters. Cable manufacturers specify the load capacity of cables for nominal conditions and provide correction factors for deviations in temperatures and installation conditions from the nominal values. The NEN 1010 standard also uses correction factors. | the IEC 60853 standard, can even be increased from 255 A to 348 A for two hours or from 255 A to 339 A for five hours under these conditions.
Netontwerpers hanteren vaak bedrijfseigen richtlijnen die veelal afgeleid zijn van methodes die werken met correctiefactoren om de nominale stroom voor iedere gewenste situatie te berekenen. Daarboven wordt in verband met de levensduur van de kabels een ‘optimale’ stroom vastgesteld. De bedrijfsstroom mag hier niet boven uitkomen. De optimale stroom is afgeleid uit de statistieken met betrekking tot de levensduur van de kabel en de te verwachten kosten. De optimale stroom bedraagt voor GPLK kabels 70% en voor XLPE kabels 90% van de nominale stroom. | Network designers often use company-specific guidelines that are largely derived from methods that work with correction factors to calculate the nominal current for any desired situation. Additionally, an 'optimal' current is established in relation to the lifespan of the cables. The operating current must not exceed this value. The optimal current is derived from statistics regarding the cable's lifespan and the expected costs. The optimal current amounts to 70% of the nominal current for GPLK cables and 90% for XLPE cables. | load capacity of cables for nominal conditions and provide correction factors for deviations in temperatures and installation conditions from the nominal values. The NEN 1010 standard also uses correction factors.
Wisselende belasting | Variable load | is derived from statistics regarding the cable's lifespan and the expected costs. The optimal current amounts to 70% of the nominal current for GPLK cables and 90% for XLPE cables.
De berekeningen en richtlijnen gaan er normaal gesproken van uit dat er een stationaire stroom door de kabel vloeit. In werkelijkheid verandert de belasting over de dag. In het geval van een dagelijks wisselende belasting zal de maximale temperatuur van de kabel meestal lager zijn dan de temperatuur die hoort bij een stationair vloeiende stroom ter grootte van het maximum van de dagcyclus. Met die wetenschap is het mogelijk om de kabel tijdelijk meer dan nominaal te belasten. De berekeningsmethode hiervoor is te vinden in de norm IEC 60853. Het betreft hier de berekening van de dynamische kabelbelastbaarheid van de kabel. | The calculations and guidelines normally assume that a steady current flows through the cable. In reality, the load changes throughout the day. In the case of a daily fluctuating load, the maximum temperature of the cable will usually be lower than the temperature associated with a steady current equal to the maximum of the daily cycle. With that knowledge, it is possible to temporarily load the cable more than nominally. The calculation method for this can be found in the IEC 60853 standard. This concerns the calculation of the dynamic cable load capacity. | from statistics regarding the cable's lifespan and the expected costs. The optimal current amounts to 70% of the nominal current for GPLK cables and 90% for XLPE cables. Variable load
Een sterk wisselende belasting is slecht voor de levensduur van GPLK-kabels. De aders van GPLK-kabels zijn omsloten door een loodmantel. Door sterke verwarming van de kabel zal de het impregneermiddel (de massa) vloeibaar worden en uitzetten waardoor de druk binnen de kabel toeneemt en alle holtes gevuld worden. Hierbij zal de loodmantel zich zetten in het pantser. Ook kan het impregneermiddel zich verplaatsen (migreren) door de kabel en eventueel zelfs door de moffen. Bij het afkoelen van de kabel zal de druk afnemen maar de eenmaal uitgezette loodmantel zal niet elastisch krimpen. Hierdoor zal het impregneermiddel terug migreren maar kunnen ook nieuwe holtes ontstaan. Dit effect in sterk wisselend belaste GPLK-kabels wordt het pomp- en zuigeffect genoemd. Dit effect vergroot de kans op storingen in moffen en eindsluitingen en veroorzaakt veroudering van de kabel zelf. In lokale holtes ontstaan hierdoor deelontladingen, die het impregneermiddel ontleden en verkoling van de papierisolatie veroorzaken. Uiteindelijk zal er een kortsluiting optreden. Vanwege dit effect en om reden van milieuaspecten worden bij vervanging en nieuwbouw alleen kunststof kabels toegepast. | A highly fluctuating load is detrimental to the lifespan of GPLK cables. The conductors of GPLK cables are enclosed by a lead sheath. Due to significant heating of the cable, the impregnating compound (the mass) will become liquid and expand, increasing the pressure within the cable and filling all voids. In this process, the lead sheath will settle into the armor. The impregnating compound can also migrate through the cable and potentially even through the joints. When the cable cools down, the pressure will decrease, but the expanded lead sheath will not elastically contract. As a result, the impregnating compound will migrate back, but new voids can also form. This effect in highly fluctuating loaded GPLK cables is known as the pumping and suction effect. This effect increases the likelihood of failures in joints and terminations and causes aging of the cable itself. In local voids, partial discharges occur, which decompose the impregnating compound and cause charring of the paper insulation. Ultimately, a short circuit will occur. Due to this effect and for environmental reasons, only plastic cables are used in replacements and new constructions. | temporarily load the cable more than nominally. The calculation method for this can be found in the IEC 60853 standard. This concerns the calculation of the dynamic cable load capacity.
Samenvattend zijn de voordelen van XLPE-kabel ten opzichte van de GPLK-kabel: | In summary, the advantages of XLPE cable compared to GPLK cable are: | cause charring of the paper insulation. Ultimately, a short circuit will occur. Due to this effect and for environmental reasons, only plastic cables are used in replacements and new constructions.
hogere belastbaarheid, zowel continue als tijdelijk toegenomen belasting (kortstondige overbelasting is toegestaan) | higher load capacity, both continuous and temporarily increased load (short-term overload is allowed) | Due to this effect and for environmental reasons, only plastic cables are used in replacements and new constructions. In summary, the advantages of XLPE cable compared to GPLK cable are:
beter bestand tegen sterk wisselende belasting (dit maakt de kabel bij uitstek geschikt voor het aansluiten van fluctuerende bronnen zoals decentrale opwekking) | better resistant to highly variable loads (this makes the cable particularly suitable for connecting fluctuating sources such as decentralized generation) | in replacements and new constructions. In summary, the advantages of XLPE cable compared to GPLK cable are: higher load capacity, both continuous and temporarily increased load (short-term overload is allowed)
doordat de kunststof kabels geen pomp- en zuigeffect vertonen zijn zij betrouwbaarder. | Because the plastic cables do not exhibit a pumping and suction effect, they are more reliable. | both continuous and temporarily increased load (short-term overload is allowed) better resistant to highly variable loads (this makes the cable particularly suitable for connecting fluctuating sources such as decentralized generation)
Tabel 4.6 geeft een overzicht van de maximale stroombelastbaarheid van enkele veelgebruikte kunststof MS-kabels. De waarden zijn berekend aan de hand van IEC 60287, waarbij de liggingsomstandigheid is gespecificeerd in NPR 3626: | Table 4.6 provides an overview of the maximum current-carrying capacity of some commonly used plastic medium-voltage cables. The values are calculated based on IEC 60287, with the installation conditions specified in NPR 3626: | (this makes the cable particularly suitable for connecting fluctuating sources such as decentralized generation) Because the plastic cables do not exhibit a pumping and suction effect, they are more reliable.
Bodemtemperatuur: θ | Soil temperature: θ | an overview of the maximum current-carrying capacity of some commonly used plastic medium-voltage cables. The values are calculated based on IEC 60287, with the installation conditions specified in NPR 3626:
omg | omg | the maximum current-carrying capacity of some commonly used plastic medium-voltage cables. The values are calculated based on IEC 60287, with the installation conditions specified in NPR 3626: Soil temperature: θ
maximum current-carrying capacity of some commonly used plastic medium-voltage cables. The values are calculated based on IEC 60287, with the installation conditions specified in NPR 3626: Soil temperature: θ omg
Geleidertempetratuur: θ | Conductor temperature: θ | capacity of some commonly used plastic medium-voltage cables. The values are calculated based on IEC 60287, with the installation conditions specified in NPR 3626: Soil temperature: θ omg = 15°C
geleider | geleider | commonly used plastic medium-voltage cables. The values are calculated based on IEC 60287, with the installation conditions specified in NPR 3626: Soil temperature: θ omg = 15°C Conductor temperature: θ
used plastic medium-voltage cables. The values are calculated based on IEC 60287, with the installation conditions specified in NPR 3626: Soil temperature: θ omg = 15°C Conductor temperature: θ geleider
Liggingsdiepte: L = 1 m | Laying depth: L = 1 m | medium-voltage cables. The values are calculated based on IEC 60287, with the installation conditions specified in NPR 3626: Soil temperature: θ omg = 15°C Conductor temperature: θ geleider = 90°C
Thermische weerstand van de grond: ρ | Thermal resistivity of the soil: ρ | based on IEC 60287, with the installation conditions specified in NPR 3626: Soil temperature: θ omg = 15°C Conductor temperature: θ geleider = 90°C Laying depth: L = 1 m
T | T | installation conditions specified in NPR 3626: Soil temperature: θ omg = 15°C Conductor temperature: θ geleider = 90°C Laying depth: L = 1 m Thermal resistivity of the soil: ρ
conditions specified in NPR 3626: Soil temperature: θ omg = 15°C Conductor temperature: θ geleider = 90°C Laying depth: L = 1 m Thermal resistivity of the soil: ρ T
Geen beïnvloeding door andere warmtebronnen; 1 circuit | No influence from other heat sources; 1 circuit | NPR 3626: Soil temperature: θ omg = 15°C Conductor temperature: θ geleider = 90°C Laying depth: L = 1 m Thermal resistivity of the soil: ρ T = 0.75 Km/W
Gedeeltelijke uitdroging van de grond: kritische isotherm 30°C; thermische weerstand van de uitgedroogde grond: ρ | Partial drying of the soil: critical isotherm 30°C; thermal resistivity of the dried soil: ρ | Conductor temperature: θ geleider = 90°C Laying depth: L = 1 m Thermal resistivity of the soil: ρ T = 0.75 Km/W No influence from other heat sources; 1 circuit
T | T | the soil: ρ T = 0.75 Km/W No influence from other heat sources; 1 circuit Partial drying of the soil: critical isotherm 30°C; thermal resistivity of the dried soil: ρ
soil: ρ T = 0.75 Km/W No influence from other heat sources; 1 circuit Partial drying of the soil: critical isotherm 30°C; thermal resistivity of the dried soil: ρ T
Tabel 4.6 Stroombelastbaarheid van enkele veelgebruikte drieaderige kabels | Table 4.6 Current-carrying capacity of some commonly used three-core cables
Geleiderdoorsnede (mm | Conductor cross-section (mm) | circuit Partial drying of the soil: critical isotherm 30°C; thermal resistivity of the dried soil: ρ T = 2.5 Km/W Table 4.6 Current-carrying capacity of some commonly used three-core cables
2 | 2 | of the soil: critical isotherm 30°C; thermal resistivity of the dried soil: ρ T = 2.5 Km/W Table 4.6 Current-carrying capacity of some commonly used three-core cables Conductor cross-section (mm)
) | ) | the soil: critical isotherm 30°C; thermal resistivity of the dried soil: ρ T = 2.5 Km/W Table 4.6 Current-carrying capacity of some commonly used three-core cables Conductor cross-section (mm) 2
Aluminium geleider | Aluminum conductor | soil: critical isotherm 30°C; thermal resistivity of the dried soil: ρ T = 2.5 Km/W Table 4.6 Current-carrying capacity of some commonly used three-core cables Conductor cross-section (mm) 2 )
Koperen geleider | Copper conductor | isotherm 30°C; thermal resistivity of the dried soil: ρ T = 2.5 Km/W Table 4.6 Current-carrying capacity of some commonly used three-core cables Conductor cross-section (mm) 2 ) Aluminum conductor
3 x 50 | 3 x 50 | thermal resistivity of the dried soil: ρ T = 2.5 Km/W Table 4.6 Current-carrying capacity of some commonly used three-core cables Conductor cross-section (mm) 2 ) Aluminum conductor Copper conductor
– | – | the dried soil: ρ T = 2.5 Km/W Table 4.6 Current-carrying capacity of some commonly used three-core cables Conductor cross-section (mm) 2 ) Aluminum conductor Copper conductor 3 x 50
185 A | 185 A | dried soil: ρ T = 2.5 Km/W Table 4.6 Current-carrying capacity of some commonly used three-core cables Conductor cross-section (mm) 2 ) Aluminum conductor Copper conductor 3 x 50 –
3 x 95 | 3 x 95 | ρ T = 2.5 Km/W Table 4.6 Current-carrying capacity of some commonly used three-core cables Conductor cross-section (mm) 2 ) Aluminum conductor Copper conductor 3 x 50 – 185 A
210 A | 210 A | 2.5 Km/W Table 4.6 Current-carrying capacity of some commonly used three-core cables Conductor cross-section (mm) 2 ) Aluminum conductor Copper conductor 3 x 50 – 185 A 3 x 95
265 A | 265 A | Table 4.6 Current-carrying capacity of some commonly used three-core cables Conductor cross-section (mm) 2 ) Aluminum conductor Copper conductor 3 x 50 – 185 A 3 x 95 210 A
3 x 150 | 3 x 150 | Current-carrying capacity of some commonly used three-core cables Conductor cross-section (mm) 2 ) Aluminum conductor Copper conductor 3 x 50 – 185 A 3 x 95 210 A 265 A
265 A | 265 A | some commonly used three-core cables Conductor cross-section (mm) 2 ) Aluminum conductor Copper conductor 3 x 50 – 185 A 3 x 95 210 A 265 A 3 x 150
335 A | 335 A | used three-core cables Conductor cross-section (mm) 2 ) Aluminum conductor Copper conductor 3 x 50 – 185 A 3 x 95 210 A 265 A 3 x 150 265 A
3 x 240 | 3 x 240 | cables Conductor cross-section (mm) 2 ) Aluminum conductor Copper conductor 3 x 50 – 185 A 3 x 95 210 A 265 A 3 x 150 265 A 335 A
345 A | 345 A | (mm) 2 ) Aluminum conductor Copper conductor 3 x 50 – 185 A 3 x 95 210 A 265 A 3 x 150 265 A 335 A 3 x 240
430 A | 430 A | ) Aluminum conductor Copper conductor 3 x 50 – 185 A 3 x 95 210 A 265 A 3 x 150 265 A 335 A 3 x 240 345 A
4.1.6 Belastbaarheid bij kortsluitstromen | 4.1.6 Current-carrying capacity during short-circuit currents | conductor Copper conductor 3 x 50 – 185 A 3 x 95 210 A 265 A 3 x 150 265 A 335 A 3 x 240 345 A 430 A
Alle kabels moeten een kortsluitstroom kunnen voeren totdat deze door de beveiliging wordt afgeschakeld. De tijdsduur dat een kortsluitstroom mag vloeien wordt bepaald door de kabeleigenschappen en is gespecificeerd door de fabrikant. Indien dit gegeven niet bekend is, geeft de norm NEN 1010 een methode om de kortsluitbelastbaarheid te berekenen. Hierbij wordt ervan uitgegaan dat de kortsluitstroom in ieder geval binnen 5 s wordt afgeschakeld. Binnen deze tijd is het opwarmen van de kabel een adiabatisch proces. Dit betekent dat de opwarming van de kabel gedurende een zo korte tijd plaatsvindt, dat geen warmteuitwisseling plaatsvindt met de omgeving. | All cables must be able to carry a short-circuit current until it is interrupted by the protection system. The duration that a short-circuit current is allowed to flow is determined by the cable properties and is specified by the manufacturer. If this information is not known, the NEN 1010 standard provides a method to calculate the short-circuit load capacity. It is assumed that the short-circuit current will be interrupted within 5 seconds. During this time, the heating of the cable is an adiabatic process. This means that the heating of the cable occurs over such a short period that no heat exchange takes place with the surroundings. | – 185 A 3 x 95 210 A 265 A 3 x 150 265 A 335 A 3 x 240 345 A 430 A 4.1.6 Current-carrying capacity during short-circuit currents
Voor kortsluitingen gedurende een kortere tijd dan 5 s kan de maximale tijdsduur | For short circuits lasting less than 5 seconds, the maximum duration | of the cable is an adiabatic process. This means that the heating of the cable occurs over such a short period that no heat exchange takes place with the surroundings.
t | t | heating of the cable occurs over such a short period that no heat exchange takes place with the surroundings. For short circuits lasting less than 5 seconds, the maximum duration
, waarin bij een gegeven kortsluitstroom de temperatuur van de geleiders zal stijgen van de hoogst toelaatbare bedrijfstemperatuur tot de hoogst toelaatbare temperatuur bij kortsluiting, bij benadering met de volgende formule worden berekend: | , in which, for a given short-circuit current, the temperature of the conductors will rise from the maximum allowable operating temperature to the maximum allowable temperature during a short circuit, can be approximately calculated using the following formula: | of the cable occurs over such a short period that no heat exchange takes place with the surroundings. For short circuits lasting less than 5 seconds, the maximum duration t
[ | [ | the temperature of the conductors will rise from the maximum allowable operating temperature to the maximum allowable temperature during a short circuit, can be approximately calculated using the following formula:
4.1 | 4.1 | temperature of the conductors will rise from the maximum allowable operating temperature to the maximum allowable temperature during a short circuit, can be approximately calculated using the following formula: [
] | ] | of the conductors will rise from the maximum allowable operating temperature to the maximum allowable temperature during a short circuit, can be approximately calculated using the following formula: [ 4.1
waarin: | in which: | the conductors will rise from the maximum allowable operating temperature to the maximum allowable temperature during a short circuit, can be approximately calculated using the following formula: [ 4.1 ]
t | t | will rise from the maximum allowable operating temperature to the maximum allowable temperature during a short circuit, can be approximately calculated using the following formula: [ 4.1 ] in which:
tijdsduur van de kortsluitstroom (s) | duration of the short-circuit current (s) | rise from the maximum allowable operating temperature to the maximum allowable temperature during a short circuit, can be approximately calculated using the following formula: [ 4.1 ] in which: t
S | S | temperature to the maximum allowable temperature during a short circuit, can be approximately calculated using the following formula: [ 4.1 ] in which: t duration of the short-circuit current (s)
nominale kerndoorsnede (mm | nominal core cross-section (mm) | to the maximum allowable temperature during a short circuit, can be approximately calculated using the following formula: [ 4.1 ] in which: t duration of the short-circuit current (s) S
2 | 2 | temperature during a short circuit, can be approximately calculated using the following formula: [ 4.1 ] in which: t duration of the short-circuit current (s) S nominal core cross-section (mm)
) | ) | during a short circuit, can be approximately calculated using the following formula: [ 4.1 ] in which: t duration of the short-circuit current (s) S nominal core cross-section (mm) 2
I | I | a short circuit, can be approximately calculated using the following formula: [ 4.1 ] in which: t duration of the short-circuit current (s) S nominal core cross-section (mm) 2 )
k | k | short circuit, can be approximately calculated using the following formula: [ 4.1 ] in which: t duration of the short-circuit current (s) S nominal core cross-section (mm) 2 ) I
effectieve kortsluitstroom (A) | effective short-circuit current (A) | circuit, can be approximately calculated using the following formula: [ 4.1 ] in which: t duration of the short-circuit current (s) S nominal core cross-section (mm) 2 ) I k
k | k | calculated using the following formula: [ 4.1 ] in which: t duration of the short-circuit current (s) S nominal core cross-section (mm) 2 ) I k effective short-circuit current (A)
een factor waarbij rekening is gehouden met de kabeleigenschappen | a factor that takes into account the cable properties | using the following formula: [ 4.1 ] in which: t duration of the short-circuit current (s) S nominal core cross-section (mm) 2 ) I k effective short-circuit current (A) k
De factor | The factor | t duration of the short-circuit current (s) S nominal core cross-section (mm) 2 ) I k effective short-circuit current (A) k a factor that takes into account the cable properties
k | k | of the short-circuit current (s) S nominal core cross-section (mm) 2 ) I k effective short-circuit current (A) k a factor that takes into account the cable properties The factor
houdt rekening met de soortelijke weerstand, de temperatuurcoëfficiënt, de soortelijke warmte van het geleidermateriaal, de hoogst toelaatbare bedrijfstemperatuur (de begintemperatuur, | takes into account the specific resistance, the temperature coefficient, the specific heat of the conductor material, the maximum allowable operating temperature (the initial temperature, | the short-circuit current (s) S nominal core cross-section (mm) 2 ) I k effective short-circuit current (A) k a factor that takes into account the cable properties The factor k
θ | θ | the cable properties The factor k takes into account the specific resistance, the temperature coefficient, the specific heat of the conductor material, the maximum allowable operating temperature (the initial temperature,
i | i | cable properties The factor k takes into account the specific resistance, the temperature coefficient, the specific heat of the conductor material, the maximum allowable operating temperature (the initial temperature, θ
) | ) | properties The factor k takes into account the specific resistance, the temperature coefficient, the specific heat of the conductor material, the maximum allowable operating temperature (the initial temperature, θ i
en de hoogst toelaatbare temperatuur bij kortsluiting (de eindtemperatuur, | and the maximum allowable temperature during a short circuit (the final temperature, | The factor k takes into account the specific resistance, the temperature coefficient, the specific heat of the conductor material, the maximum allowable operating temperature (the initial temperature, θ i )
θ | θ | the specific heat of the conductor material, the maximum allowable operating temperature (the initial temperature, θ i ) and the maximum allowable temperature during a short circuit (the final temperature,
f | f | specific heat of the conductor material, the maximum allowable operating temperature (the initial temperature, θ i ) and the maximum allowable temperature during a short circuit (the final temperature, θ
) | ) | heat of the conductor material, the maximum allowable operating temperature (the initial temperature, θ i ) and the maximum allowable temperature during a short circuit (the final temperature, θ f
. Voor de gangbare isolatiematerialen en geleidermaterialen wordt de waarde van | . For common insulation materials and conductor materials, the value of | of the conductor material, the maximum allowable operating temperature (the initial temperature, θ i ) and the maximum allowable temperature during a short circuit (the final temperature, θ f )
k | k | temperature, θ i ) and the maximum allowable temperature during a short circuit (the final temperature, θ f ) . For common insulation materials and conductor materials, the value of
gegeven in tabel 4.7. De berekeningsmethode wordt nader toegelicht in hoofdstuk 10, bij de berekening van de kortsluitvastheid. | given in Table 4.7. The calculation method is further explained in Chapter 10, in the section on short-circuit strength calculation. | θ i ) and the maximum allowable temperature during a short circuit (the final temperature, θ f ) . For common insulation materials and conductor materials, the value of k
Tabel 4.7 Waarden voor k voor diverse geleiders en isolatie | Table 4.7 Values for k for various conductors and insulation | common insulation materials and conductor materials, the value of k given in Table 4.7. The calculation method is further explained in Chapter 10, in the section on short-circuit strength calculation.
Geleiderisolatie | Geleiderisolatie | given in Table 4.7. The calculation method is further explained in Chapter 10, in the section on short-circuit strength calculation. Table 4.7 Values for k for various conductors and insulation
PVC 70°C | PVC 70°C | in Table 4.7. The calculation method is further explained in Chapter 10, in the section on short-circuit strength calculation. Table 4.7 Values for k for various conductors and insulation Geleiderisolatie
PVC 90°C | PVC 90°C | 4.7. The calculation method is further explained in Chapter 10, in the section on short-circuit strength calculation. Table 4.7 Values for k for various conductors and insulation Geleiderisolatie PVC 70°C
EPR/XLPE | EPR/XLPE | calculation method is further explained in Chapter 10, in the section on short-circuit strength calculation. Table 4.7 Values for k for various conductors and insulation Geleiderisolatie PVC 70°C PVC 90°C
≤ 300 mm | ≤ 300 mm | method is further explained in Chapter 10, in the section on short-circuit strength calculation. Table 4.7 Values for k for various conductors and insulation Geleiderisolatie PVC 70°C PVC 90°C EPR/XLPE
2 | 2 | explained in Chapter 10, in the section on short-circuit strength calculation. Table 4.7 Values for k for various conductors and insulation Geleiderisolatie PVC 70°C PVC 90°C EPR/XLPE ≤ 300 mm
> 300 mm | > 300 mm | in Chapter 10, in the section on short-circuit strength calculation. Table 4.7 Values for k for various conductors and insulation Geleiderisolatie PVC 70°C PVC 90°C EPR/XLPE ≤ 300 mm 2
2 | 2 | in the section on short-circuit strength calculation. Table 4.7 Values for k for various conductors and insulation Geleiderisolatie PVC 70°C PVC 90°C EPR/XLPE ≤ 300 mm 2 > 300 mm
≤ 300 mm | ≤ 300 mm | the section on short-circuit strength calculation. Table 4.7 Values for k for various conductors and insulation Geleiderisolatie PVC 70°C PVC 90°C EPR/XLPE ≤ 300 mm 2 > 300 mm 2
2 | 2 | short-circuit strength calculation. Table 4.7 Values for k for various conductors and insulation Geleiderisolatie PVC 70°C PVC 90°C EPR/XLPE ≤ 300 mm 2 > 300 mm 2 ≤ 300 mm
> 300 mm | > 300 mm² | strength calculation. Table 4.7 Values for k for various conductors and insulation Geleiderisolatie PVC 70°C PVC 90°C EPR/XLPE ≤ 300 mm 2 > 300 mm 2 ≤ 300 mm 2
2 | 2 | 4.7 Values for k for various conductors and insulation Geleiderisolatie PVC 70°C PVC 90°C EPR/XLPE ≤ 300 mm 2 > 300 mm 2 ≤ 300 mm 2 > 300 mm²
q | q | Values for k for various conductors and insulation Geleiderisolatie PVC 70°C PVC 90°C EPR/XLPE ≤ 300 mm 2 > 300 mm 2 ≤ 300 mm 2 > 300 mm² 2
i | i | for k for various conductors and insulation Geleiderisolatie PVC 70°C PVC 90°C EPR/XLPE ≤ 300 mm 2 > 300 mm 2 ≤ 300 mm 2 > 300 mm² 2 q
70 | 70 | k for various conductors and insulation Geleiderisolatie PVC 70°C PVC 90°C EPR/XLPE ≤ 300 mm 2 > 300 mm 2 ≤ 300 mm 2 > 300 mm² 2 q i
70 | 70 | for various conductors and insulation Geleiderisolatie PVC 70°C PVC 90°C EPR/XLPE ≤ 300 mm 2 > 300 mm 2 ≤ 300 mm 2 > 300 mm² 2 q i 70
90 | 90 | various conductors and insulation Geleiderisolatie PVC 70°C PVC 90°C EPR/XLPE ≤ 300 mm 2 > 300 mm 2 ≤ 300 mm 2 > 300 mm² 2 q i 70 70
90 | 90 | conductors and insulation Geleiderisolatie PVC 70°C PVC 90°C EPR/XLPE ≤ 300 mm 2 > 300 mm 2 ≤ 300 mm 2 > 300 mm² 2 q i 70 70 90
90 | 90 | and insulation Geleiderisolatie PVC 70°C PVC 90°C EPR/XLPE ≤ 300 mm 2 > 300 mm 2 ≤ 300 mm 2 > 300 mm² 2 q i 70 70 90 90
q | q | insulation Geleiderisolatie PVC 70°C PVC 90°C EPR/XLPE ≤ 300 mm 2 > 300 mm 2 ≤ 300 mm 2 > 300 mm² 2 q i 70 70 90 90 90
f | f | Geleiderisolatie PVC 70°C PVC 90°C EPR/XLPE ≤ 300 mm 2 > 300 mm 2 ≤ 300 mm 2 > 300 mm² 2 q i 70 70 90 90 90 q
160 | 160 | PVC 70°C PVC 90°C EPR/XLPE ≤ 300 mm 2 > 300 mm 2 ≤ 300 mm 2 > 300 mm² 2 q i 70 70 90 90 90 q f
140 | 140 | 70°C PVC 90°C EPR/XLPE ≤ 300 mm 2 > 300 mm 2 ≤ 300 mm 2 > 300 mm² 2 q i 70 70 90 90 90 q f 160
160 | 160 | PVC 90°C EPR/XLPE ≤ 300 mm 2 > 300 mm 2 ≤ 300 mm 2 > 300 mm² 2 q i 70 70 90 90 90 q f 160 140
140 | 140 | 90°C EPR/XLPE ≤ 300 mm 2 > 300 mm 2 ≤ 300 mm 2 > 300 mm² 2 q i 70 70 90 90 90 q f 160 140 160
250 | 250 | EPR/XLPE ≤ 300 mm 2 > 300 mm 2 ≤ 300 mm 2 > 300 mm² 2 q i 70 70 90 90 90 q f 160 140 160 140
Geleidermateriaal | Geleidermateriaal | ≤ 300 mm 2 > 300 mm 2 ≤ 300 mm 2 > 300 mm² 2 q i 70 70 90 90 90 q f 160 140 160 140 250
waarden van | values of | 300 mm 2 > 300 mm 2 ≤ 300 mm 2 > 300 mm² 2 q i 70 70 90 90 90 q f 160 140 160 140 250 Geleidermateriaal
k | k | 2 > 300 mm 2 ≤ 300 mm 2 > 300 mm² 2 q i 70 70 90 90 90 q f 160 140 160 140 250 Geleidermateriaal values of
Koper | Koper | > 300 mm 2 ≤ 300 mm 2 > 300 mm² 2 q i 70 70 90 90 90 q f 160 140 160 140 250 Geleidermateriaal values of k
115 | 115 | 300 mm 2 ≤ 300 mm 2 > 300 mm² 2 q i 70 70 90 90 90 q f 160 140 160 140 250 Geleidermateriaal values of k Koper
103 | 103 | mm 2 ≤ 300 mm 2 > 300 mm² 2 q i 70 70 90 90 90 q f 160 140 160 140 250 Geleidermateriaal values of k Koper 115
100 | 100 | 2 ≤ 300 mm 2 > 300 mm² 2 q i 70 70 90 90 90 q f 160 140 160 140 250 Geleidermateriaal values of k Koper 115 103
86 | 86 | ≤ 300 mm 2 > 300 mm² 2 q i 70 70 90 90 90 q f 160 140 160 140 250 Geleidermateriaal values of k Koper 115 103 100
143 | 143 | 300 mm 2 > 300 mm² 2 q i 70 70 90 90 90 q f 160 140 160 140 250 Geleidermateriaal values of k Koper 115 103 100 86
Aluminium | Aluminium | mm 2 > 300 mm² 2 q i 70 70 90 90 90 q f 160 140 160 140 250 Geleidermateriaal values of k Koper 115 103 100 86 143
76 | 76 | 2 > 300 mm² 2 q i 70 70 90 90 90 q f 160 140 160 140 250 Geleidermateriaal values of k Koper 115 103 100 86 143 Aluminium
68 | 68 | > 300 mm² 2 q i 70 70 90 90 90 q f 160 140 160 140 250 Geleidermateriaal values of k Koper 115 103 100 86 143 Aluminium 76
66 | 66 | 300 mm² 2 q i 70 70 90 90 90 q f 160 140 160 140 250 Geleidermateriaal values of k Koper 115 103 100 86 143 Aluminium 76 68
57 | 57 | mm² 2 q i 70 70 90 90 90 q f 160 140 160 140 250 Geleidermateriaal values of k Koper 115 103 100 86 143 Aluminium 76 68 66
93 | 93 | 2 q i 70 70 90 90 90 q f 160 140 160 140 250 Geleidermateriaal values of k Koper 115 103 100 86 143 Aluminium 76 68 66 57
Hieruit wordt de waarde van | From this, the value of | q i 70 70 90 90 90 q f 160 140 160 140 250 Geleidermateriaal values of k Koper 115 103 100 86 143 Aluminium 76 68 66 57 93
I | I | 90 90 q f 160 140 160 140 250 Geleidermateriaal values of k Koper 115 103 100 86 143 Aluminium 76 68 66 57 93 From this, the value of
k,1s | k,1s | 90 q f 160 140 160 140 250 Geleidermateriaal values of k Koper 115 103 100 86 143 Aluminium 76 68 66 57 93 From this, the value of I
berekend: de maximale waarde van de kortsluitstroom, die gedurende 1 seconde door de kabel mag vloeien zonder dat deze beschadigt. | calculated: the maximum value of the short-circuit current that may flow through the cable for 1 second without causing damage. | q f 160 140 160 140 250 Geleidermateriaal values of k Koper 115 103 100 86 143 Aluminium 76 68 66 57 93 From this, the value of I k,1s
[ | [ | 66 57 93 From this, the value of I k,1s calculated: the maximum value of the short-circuit current that may flow through the cable for 1 second without causing damage.
4.2 | 4.2 | 57 93 From this, the value of I k,1s calculated: the maximum value of the short-circuit current that may flow through the cable for 1 second without causing damage. [
] | ] | 93 From this, the value of I k,1s calculated: the maximum value of the short-circuit current that may flow through the cable for 1 second without causing damage. [ 4.2
De kortsluitstroom, die gedurende een willekeurige tijd | The short-circuit current, which flows for any given period | From this, the value of I k,1s calculated: the maximum value of the short-circuit current that may flow through the cable for 1 second without causing damage. [ 4.2 ]
t | t | maximum value of the short-circuit current that may flow through the cable for 1 second without causing damage. [ 4.2 ] The short-circuit current, which flows for any given period
door de kabel mag vloeien wordt dan als volgt uit | through the cable may flow is then determined as follows | value of the short-circuit current that may flow through the cable for 1 second without causing damage. [ 4.2 ] The short-circuit current, which flows for any given period t
I | I | cable for 1 second without causing damage. [ 4.2 ] The short-circuit current, which flows for any given period t through the cable may flow is then determined as follows
k,1s | k,1s | for 1 second without causing damage. [ 4.2 ] The short-circuit current, which flows for any given period t through the cable may flow is then determined as follows I
berekend: | calculated: | 1 second without causing damage. [ 4.2 ] The short-circuit current, which flows for any given period t through the cable may flow is then determined as follows I k,1s
[ | [ | second without causing damage. [ 4.2 ] The short-circuit current, which flows for any given period t through the cable may flow is then determined as follows I k,1s calculated:
4.3 | 4.3 | without causing damage. [ 4.2 ] The short-circuit current, which flows for any given period t through the cable may flow is then determined as follows I k,1s calculated: [
] | ] | causing damage. [ 4.2 ] The short-circuit current, which flows for any given period t through the cable may flow is then determined as follows I k,1s calculated: [ 4.3
4.2 Moffen | 4.2 Joints | damage. [ 4.2 ] The short-circuit current, which flows for any given period t through the cable may flow is then determined as follows I k,1s calculated: [ 4.3 ]
Kabels worden geproduceerd in beperkte lengtes. Bij toepassing in een circuit worden meerdere lengten door middel van moffen aan elkaar gelast. Ook bij een reparatie worden de kabels met moffen weer met elkaar verbonden. Aan het begin en aan het einde van het circuit worden de kabels met behulp van eindsluitingen op de andere componenten aangesloten. In het verleden zijn in MS-netten voor GPLK-kabels massamoffen en oliemoffen toegepast. Tegenwoordig worden moffen (en eindsluitingen) voornamelijk in kunststofuitvoeringen toegepast. | Cables are produced in limited lengths. When used in a circuit, multiple lengths are welded together using joints. During a repair, the cables are also reconnected with joints. At the beginning and end of the circuit, the cables are connected to other components using terminations. In the past, mass joints and oil joints were used for GPLK cables in medium voltage networks. Nowadays, joints (and terminations) are primarily used in plastic versions. | 4.2 ] The short-circuit current, which flows for any given period t through the cable may flow is then determined as follows I k,1s calculated: [ 4.3 ] 4.2 Joints
Moffen hebben grote invloed op de betrouwbaarheid. In de praktijk is gebleken dat kabelstoringen meestal in de moffen optreden. De moffen blijven zwakke schakels in de elektriciteitsnetten, hoe goed zij ook gemaakt zijn. Figuur 4.8 toont een MS-verbindingsmof voor XLPE-kabels. In het algemeen is een mof opgebouwd uit een verbinding voor de geleider (1). Voorheen werden persverbinders gebruikt, maar tegenwoordig worden schroefverbinders gebruikt. Om de geleider wordt een isolatielichaam van siliconenrubber aangebracht (2). Op het contactvlak met de geleider is een halfgeleidende laag aangebracht (3) voor de veldsturing. Ook op het contactvlak met het isolatiescherm van de kabel is een halfgeleidende laag aangebracht (4) voor de veldsturing. De afscherming van de kabel wordt aan beide uiteinden met de afscherming van de mof verbonden (5), zodat de afscherming doorloopt. Het geheel wordt omgeven door een beschermende laag (6) die verhindert dat vuil en vocht binnendringen. | Joints have a significant impact on reliability. In practice, it has been shown that cable faults usually occur in the joints. The joints remain weak links in the electrical networks, no matter how well they are made. Figure 4.8 shows a medium voltage joint for XLPE cables. In general, a joint consists of a connection for the conductor (1). Previously, crimp connectors were used, but nowadays screw connectors are used. Around the conductor, a silicone rubber insulating body is applied (2). On the contact surface with the conductor, a semiconductive layer is applied (3) for field control. A semiconductive layer is also applied on the contact surface with the cable's insulation screen (4) for field control. The cable shielding is connected to the joint shielding at both ends (5), so the shielding continues. The entire assembly is surrounded by a protective layer (6) that prevents dirt and moisture from entering. | components using terminations. In the past, mass joints and oil joints were used for GPLK cables in medium voltage networks. Nowadays, joints (and terminations) are primarily used in plastic versions.
Figuur 4.8 Middenspanningsmof voor enkeladerige kabel | Figure 4.8 Medium Voltage Joint for Single-Core Cable | connected to the joint shielding at both ends (5), so the shielding continues. The entire assembly is surrounded by a protective layer (6) that prevents dirt and moisture from entering.
Figuur 4.9 Middenspanningsmof voor drieaderige kabel | Figure 4.9 Medium Voltage Joint for Three-Core Cable | (5), so the shielding continues. The entire assembly is surrounded by a protective layer (6) that prevents dirt and moisture from entering. Figure 4.8 Medium Voltage Joint for Single-Core Cable
Figuur 4.9 toont een vergelijkbare constructie voor een drieaderige kabel. Hierin wordt elke ader individueel afgeschermd, waarna de drie aders gezamenlijk worden omsloten door een beschermende laag. | Figure 4.9 shows a similar construction for a three-core cable. In this, each core is individually shielded, after which the three cores are collectively enclosed by a protective layer. | is surrounded by a protective layer (6) that prevents dirt and moisture from entering. Figure 4.8 Medium Voltage Joint for Single-Core Cable Figure 4.9 Medium Voltage Joint for Three-Core Cable
Figuur 4.10 toont een veelgebruikte mof om papiergeïsoleerde (GPLK) en kunststofgeïsoleerde (XLPE) kabels te verbinden. De aders bevinden zich in een kunststof omhulsel, dat gevuld wordt met een isolatiemedium van vloeibare siliconen. De mof wordt omsloten door een buitenmof, die voor vochtafscherming gevuld wordt met een harsverbinding. | Figure 4.10 shows a commonly used joint to connect paper-insulated (PILC) and plastic-insulated (XLPE) cables. The conductors are housed in a plastic casing, which is filled with a liquid silicone insulating medium. The joint is enclosed by an outer sleeve, which is filled with a resin compound for moisture protection. | Cable Figure 4.9 shows a similar construction for a three-core cable. In this, each core is individually shielded, after which the three cores are collectively enclosed by a protective layer.
Figuur 4.10 Overgangsmof voor drieaderige GPLK- naar XLPE-kabel | Figure 4.10 Transition joint for three-core GPLK to XLPE cable | a plastic casing, which is filled with a liquid silicone insulating medium. The joint is enclosed by an outer sleeve, which is filled with a resin compound for moisture protection.
Voor het herstellen van een defect worden speciale herstelmoffen gebruikt, die een extra lange geleiderverbinding hebben. Normaal gesproken zal een defect stuk van de kabel worden uitgenomen, waarna dit vervangen wordt door een nieuw kabelstuk dat met twee moffen aan de bestaande kabel wordt gemonteerd. Van de herstelmof is de totale lengte groter dan die van een gewone verbindingsmof, waardoor deze in de meeste gevallen het defecte kabelstuk in één keer kan vervangen. | For repairing a defect, special repair sleeves are used, which have an extra-long conductor connection. Normally, a defective section of the cable will be removed and replaced with a new cable section that is mounted to the existing cable with two sleeves. The total length of the repair sleeve is greater than that of a regular joint sleeve, allowing it to replace the defective cable section in one go in most cases. | insulating medium. The joint is enclosed by an outer sleeve, which is filled with a resin compound for moisture protection. Figure 4.10 Transition joint for three-core GPLK to XLPE cable
Figuur 4.11 LS-aftakmof | Figure 4.11 Low-Voltage Branch Sleeve | The total length of the repair sleeve is greater than that of a regular joint sleeve, allowing it to replace the defective cable section in one go in most cases.
In het LS-net wordt elke aansluiting op de hoofdkabel met behulp van aftakmoffen gerealiseerd. Moderne LS-aftakmoffen kunnen onder spanning worden aangebracht zonder de aders te onderbreken. Figuur 4.11 toont de verbindingen binnen een aftakmof. Een klem wordt om de vier geleiders aangebracht. Door het aandraaien van de bouten komt de knelverbinding met de geleider tot stand. De mof wordt omgeven door een omhulling. Deze wordt gevuld met een stabiliserende en isolerende substantie. | In the low-voltage network, every connection to the main cable is made using branch sleeves. Modern low-voltage branch sleeves can be installed under voltage without interrupting the conductors. Figure 4.11 shows the connections within a branch sleeve. A clamp is placed around the four conductors. By tightening the bolts, the compression connection with the conductor is established. The sleeve is surrounded by a casing. This is filled with a stabilizing and insulating substance. | repair sleeve is greater than that of a regular joint sleeve, allowing it to replace the defective cable section in one go in most cases. Figure 4.11 Low-Voltage Branch Sleeve
4.3 Transformatoren | 4.3 Transformers | four conductors. By tightening the bolts, the compression connection with the conductor is established. The sleeve is surrounded by a casing. This is filled with a stabilizing and insulating substance.
Transformatoren verbinden de netten van verschillende spanningsniveaus met elkaar. In sommige gevallen verbinden transformatoren netten van gelijk spanningsniveau, bijvoorbeeld in uitgestrekte netten, waar zogenaamde boostertransformatoren het optredende spanningsverlies in het circuit compenseren. In distributienetten zijn de belangrijkste transformatoren: | Transformers connect networks of different voltage levels with each other. In some cases, transformers connect networks of the same voltage level, for example in extensive networks, where so-called booster transformers compensate for the occurring voltage loss in the circuit. In distribution networks, the main transformers are: | By tightening the bolts, the compression connection with the conductor is established. The sleeve is surrounded by a casing. This is filled with a stabilizing and insulating substance. 4.3 Transformers
voedingstransformatoren, meestal tussen HS- en MS-niveau | power transformers, usually between HV and MV levels | of the same voltage level, for example in extensive networks, where so-called booster transformers compensate for the occurring voltage loss in the circuit. In distribution networks, the main transformers are:
distributietransformatoren tussen MS- en LS-niveau | distribution transformers between MV and LV levels | extensive networks, where so-called booster transformers compensate for the occurring voltage loss in the circuit. In distribution networks, the main transformers are: power transformers, usually between HV and MV levels
Voedingstransformatoren bestaan in zeer veel uitvoeringsvormen. De belangrijkste kenmerken van een transformator zijn: | Power transformers come in a wide variety of designs. The main characteristics of a transformer are: | for the occurring voltage loss in the circuit. In distribution networks, the main transformers are: power transformers, usually between HV and MV levels distribution transformers between MV and LV levels
nominale spanning: elke transformator heeft een primaire en een secundaire wikkeling en soms ook een tertiaire wikkeling; voor elke wikkeling is de nominale spanning gegeven in V | nominal voltage: each transformer has a primary and a secondary winding and sometimes also a tertiary winding; for each winding, the nominal voltage is given in V | transformers, usually between HV and MV levels distribution transformers between MV and LV levels Power transformers come in a wide variety of designs. The main characteristics of a transformer are:
nominaal vermogen: het schijnbare vermogen dat de transformator kan transporteren, gegeven in VA | nominal power: the apparent power that the transformer can transfer, given in VA | a transformer are: nominal voltage: each transformer has a primary and a secondary winding and sometimes also a tertiary winding; for each winding, the nominal voltage is given in V
relatieve kortsluitspanning: de spanning die over de primaire wikkeling staat indien de secundaire wikkeling is kortgesloten, gegeven in procenten van de nominale spanning | relative short-circuit voltage: the voltage across the primary winding when the secondary winding is short-circuited, given as a percentage of the nominal voltage | winding and sometimes also a tertiary winding; for each winding, the nominal voltage is given in V nominal power: the apparent power that the transformer can transfer, given in VA
schakeling: de drie fasewikkelingen kunnen op diverse manieren met elkaar worden geschakeld; gebruikelijk is een driehoekschakeling of een sterschakeling, al dan niet met uitgevoerd sterpunt. | circuit: the three-phase windings can be connected in various ways; commonly, a delta connection or a star connection, with or without a neutral point, is used. | the transformer can transfer, given in VA relative short-circuit voltage: the voltage across the primary winding when the secondary winding is short-circuited, given as a percentage of the nominal voltage
De schakeling van de transformatorwikkelingen wordt bepaald door het aangesloten net. Dit kan een zwevend of een impedantie-geaard net zijn. Bij een HS/MS-voedingstransformator is de primaire wikkeling meestal in ster geschakeld en is de secundaire wikkeling in driehoek geschakeld. Deze schakeling wordt aangeduid met de lettercombinatie Yd. Voor de driehoekschakeling wordt gekozen omdat het MS-net meestal een zwevend net is. Hier is geen nulgeleider aanwezig. | The configuration of the transformer windings is determined by the connected network. This can be a floating or impedance-grounded network. In a high-voltage/medium-voltage (HV/MV) power transformer, the primary winding is usually connected in a star configuration, and the secondary winding is connected in a delta configuration. This configuration is indicated by the letter combination Yd. The delta configuration is chosen because the MV network is usually a floating network. There is no neutral conductor present here. | of the nominal voltage circuit: the three-phase windings can be connected in various ways; commonly, a delta connection or a star connection, with or without a neutral point, is used.
Voor de omzetting van middenspanning naar laagspanning worden distributietransformatoren gebruikt. Dit zijn meestal normtransformatoren, zo genoemd omdat de typen in genormeerde reeksen geproduceerd worden. Normtransformatoren hebben een primaire wikkeling met aftakkingen op 11250, 11000, 10750, 10500 en 10250 Volt (NEN 2761 tot en met 2765, zie ook NEN-EN 50464 en NEN-EN 50541). De laagspanningswikkeling van de normtransformator heeft een nominale spanning van 420 Volt. | For the conversion of medium voltage to low voltage, distribution transformers are used. These are usually standard transformers, so called because the types are produced in standardized series. Standard transformers have a primary winding with taps at 11250, 11000, 10750, 10500, and 10250 Volts (NEN 2761 through 2765, see also NEN-EN 50464 and NEN-EN 50541). The low voltage winding of the standard transformer has a nominal voltage of 420 Volts. | This configuration is indicated by the letter combination Yd. The delta configuration is chosen because the MV network is usually a floating network. There is no neutral conductor present here.
Bij een MS/LS-distributietransformator is de primaire wikkeling in driehoek geschakeld en is de laagspanningswikkeling in ster geschakeld. Aan laagspanningszijde is het sterpunt uitgevoerd (zie figuur 4.13). Deze schakeling wordt aangeduid met de lettercombinatie Dyn. Het sterpunt wordt aangesloten op de nulgeleider van het laagspanningssysteem, het kabelscherm of de loodmantel en is in het netstation geaard. De belangrijkste technische gegevens van de normtransformatoren zijn in tabel 4.8 vermeld (EnergieNed, 1996). Het kortsluitverlies is gelijk aan het I | In an MV/LV distribution transformer, the primary winding is connected in a delta configuration, and the low voltage winding is connected in a star configuration. On the low voltage side, the star point is implemented (see figure 4.13). This configuration is indicated by the letter combination Dyn. The star point is connected to the neutral conductor of the low voltage system, the cable screen, or the lead sheath and is grounded in the substation. The main technical data of the standard transformers are listed in table 4.8 (EnergieNed, 1996). The short-circuit loss is equal to the I | 10500, and 10250 Volts (NEN 2761 through 2765, see also NEN-EN 50464 and NEN-EN 50541). The low voltage winding of the standard transformer has a nominal voltage of 420 Volts.
2 | 2 | sheath and is grounded in the substation. The main technical data of the standard transformers are listed in table 4.8 (EnergieNed, 1996). The short-circuit loss is equal to the I
R-verlies als gevolg van de stroom door de transformator. Het kortsluitverlies is gegeven bij het nominale getransporteerde vermogen. Het nullastverlies ontstaat door het magnetiseren van de transformator. Het nullastverlies is onafhankelijk van het getransporteerde vermogen. | I²R loss as a result of the current through the transformer. The short-circuit loss is given at the nominal transmitted power. The no-load loss occurs due to the magnetization of the transformer. The no-load loss is independent of the transmitted power. | and is grounded in the substation. The main technical data of the standard transformers are listed in table 4.8 (EnergieNed, 1996). The short-circuit loss is equal to the I 2
Tabel 4.8 Technische gegevens van normtransformatoren | Table 4.8 Technical Data of Standard Transformers | The short-circuit loss is given at the nominal transmitted power. The no-load loss occurs due to the magnetization of the transformer. The no-load loss is independent of the transmitted power.
Nominaal vermogen (kVA) | Nominal power (kVA) | nominal transmitted power. The no-load loss occurs due to the magnetization of the transformer. The no-load loss is independent of the transmitted power. Table 4.8 Technical Data of Standard Transformers
Relatieve kortsluit- | Relative short-circuit | The no-load loss occurs due to the magnetization of the transformer. The no-load loss is independent of the transmitted power. Table 4.8 Technical Data of Standard Transformers Nominal power (kVA)
spanning (%) | voltage (%) | loss occurs due to the magnetization of the transformer. The no-load loss is independent of the transmitted power. Table 4.8 Technical Data of Standard Transformers Nominal power (kVA) Relative short-circuit
Kortsluitverlies (kW) | Short-circuit loss (kW) | due to the magnetization of the transformer. The no-load loss is independent of the transmitted power. Table 4.8 Technical Data of Standard Transformers Nominal power (kVA) Relative short-circuit voltage (%)
Nullastverlies (kW) | No-load loss (kW) | magnetization of the transformer. The no-load loss is independent of the transmitted power. Table 4.8 Technical Data of Standard Transformers Nominal power (kVA) Relative short-circuit voltage (%) Short-circuit loss (kW)
50 | 50 | transformer. The no-load loss is independent of the transmitted power. Table 4.8 Technical Data of Standard Transformers Nominal power (kVA) Relative short-circuit voltage (%) Short-circuit loss (kW) No-load loss (kW)
4 | 4 | The no-load loss is independent of the transmitted power. Table 4.8 Technical Data of Standard Transformers Nominal power (kVA) Relative short-circuit voltage (%) Short-circuit loss (kW) No-load loss (kW) 50
0,8 | 0.8 | no-load loss is independent of the transmitted power. Table 4.8 Technical Data of Standard Transformers Nominal power (kVA) Relative short-circuit voltage (%) Short-circuit loss (kW) No-load loss (kW) 50 4
0,1 | 0.1 | loss is independent of the transmitted power. Table 4.8 Technical Data of Standard Transformers Nominal power (kVA) Relative short-circuit voltage (%) Short-circuit loss (kW) No-load loss (kW) 50 4 0.8
100 | 100 | is independent of the transmitted power. Table 4.8 Technical Data of Standard Transformers Nominal power (kVA) Relative short-circuit voltage (%) Short-circuit loss (kW) No-load loss (kW) 50 4 0.8 0.1
4 | 4 | independent of the transmitted power. Table 4.8 Technical Data of Standard Transformers Nominal power (kVA) Relative short-circuit voltage (%) Short-circuit loss (kW) No-load loss (kW) 50 4 0.8 0.1 100
1,4 | 1.4 | of the transmitted power. Table 4.8 Technical Data of Standard Transformers Nominal power (kVA) Relative short-circuit voltage (%) Short-circuit loss (kW) No-load loss (kW) 50 4 0.8 0.1 100 4
0,2 | 0.2 | the transmitted power. Table 4.8 Technical Data of Standard Transformers Nominal power (kVA) Relative short-circuit voltage (%) Short-circuit loss (kW) No-load loss (kW) 50 4 0.8 0.1 100 4 1.4
160 | 160 | transmitted power. Table 4.8 Technical Data of Standard Transformers Nominal power (kVA) Relative short-circuit voltage (%) Short-circuit loss (kW) No-load loss (kW) 50 4 0.8 0.1 100 4 1.4 0.2
4 | 4 | power. Table 4.8 Technical Data of Standard Transformers Nominal power (kVA) Relative short-circuit voltage (%) Short-circuit loss (kW) No-load loss (kW) 50 4 0.8 0.1 100 4 1.4 0.2 160
1,9 | 1.9 | Table 4.8 Technical Data of Standard Transformers Nominal power (kVA) Relative short-circuit voltage (%) Short-circuit loss (kW) No-load loss (kW) 50 4 0.8 0.1 100 4 1.4 0.2 160 4
0,3 | 0.3 | 4.8 Technical Data of Standard Transformers Nominal power (kVA) Relative short-circuit voltage (%) Short-circuit loss (kW) No-load loss (kW) 50 4 0.8 0.1 100 4 1.4 0.2 160 4 1.9
250 | 250 | Technical Data of Standard Transformers Nominal power (kVA) Relative short-circuit voltage (%) Short-circuit loss (kW) No-load loss (kW) 50 4 0.8 0.1 100 4 1.4 0.2 160 4 1.9 0.3
4 | 4 | Data of Standard Transformers Nominal power (kVA) Relative short-circuit voltage (%) Short-circuit loss (kW) No-load loss (kW) 50 4 0.8 0.1 100 4 1.4 0.2 160 4 1.9 0.3 250
2,6 | 2.6 | of Standard Transformers Nominal power (kVA) Relative short-circuit voltage (%) Short-circuit loss (kW) No-load loss (kW) 50 4 0.8 0.1 100 4 1.4 0.2 160 4 1.9 0.3 250 4
0,4 | 0.4 | Standard Transformers Nominal power (kVA) Relative short-circuit voltage (%) Short-circuit loss (kW) No-load loss (kW) 50 4 0.8 0.1 100 4 1.4 0.2 160 4 1.9 0.3 250 4 2.6
400 | 400 | Transformers Nominal power (kVA) Relative short-circuit voltage (%) Short-circuit loss (kW) No-load loss (kW) 50 4 0.8 0.1 100 4 1.4 0.2 160 4 1.9 0.3 250 4 2.6 0.4
4 | 4 | Nominal power (kVA) Relative short-circuit voltage (%) Short-circuit loss (kW) No-load loss (kW) 50 4 0.8 0.1 100 4 1.4 0.2 160 4 1.9 0.3 250 4 2.6 0.4 400
3,8 | 3.8 | power (kVA) Relative short-circuit voltage (%) Short-circuit loss (kW) No-load loss (kW) 50 4 0.8 0.1 100 4 1.4 0.2 160 4 1.9 0.3 250 4 2.6 0.4 400 4
0,5 | 0.5 | (kVA) Relative short-circuit voltage (%) Short-circuit loss (kW) No-load loss (kW) 50 4 0.8 0.1 100 4 1.4 0.2 160 4 1.9 0.3 250 4 2.6 0.4 400 4 3.8
630 | 630 | Relative short-circuit voltage (%) Short-circuit loss (kW) No-load loss (kW) 50 4 0.8 0.1 100 4 1.4 0.2 160 4 1.9 0.3 250 4 2.6 0.4 400 4 3.8 0.5
4 | 4 | short-circuit voltage (%) Short-circuit loss (kW) No-load loss (kW) 50 4 0.8 0.1 100 4 1.4 0.2 160 4 1.9 0.3 250 4 2.6 0.4 400 4 3.8 0.5 630
5,2 | 5.2 | voltage (%) Short-circuit loss (kW) No-load loss (kW) 50 4 0.8 0.1 100 4 1.4 0.2 160 4 1.9 0.3 250 4 2.6 0.4 400 4 3.8 0.5 630 4
0,8 | 0.8 | (%) Short-circuit loss (kW) No-load loss (kW) 50 4 0.8 0.1 100 4 1.4 0.2 160 4 1.9 0.3 250 4 2.6 0.4 400 4 3.8 0.5 630 4 5.2
1000 | 1000 | Short-circuit loss (kW) No-load loss (kW) 50 4 0.8 0.1 100 4 1.4 0.2 160 4 1.9 0.3 250 4 2.6 0.4 400 4 3.8 0.5 630 4 5.2 0.8
6 | 6 | loss (kW) No-load loss (kW) 50 4 0.8 0.1 100 4 1.4 0.2 160 4 1.9 0.3 250 4 2.6 0.4 400 4 3.8 0.5 630 4 5.2 0.8 1000
8,8 | 8.8 | (kW) No-load loss (kW) 50 4 0.8 0.1 100 4 1.4 0.2 160 4 1.9 0.3 250 4 2.6 0.4 400 4 3.8 0.5 630 4 5.2 0.8 1000 6
1,0 | 1.0 | No-load loss (kW) 50 4 0.8 0.1 100 4 1.4 0.2 160 4 1.9 0.3 250 4 2.6 0.4 400 4 3.8 0.5 630 4 5.2 0.8 1000 6 8.8
1600 | 1600 | loss (kW) 50 4 0.8 0.1 100 4 1.4 0.2 160 4 1.9 0.3 250 4 2.6 0.4 400 4 3.8 0.5 630 4 5.2 0.8 1000 6 8.8 1.0
6 | 6 | (kW) 50 4 0.8 0.1 100 4 1.4 0.2 160 4 1.9 0.3 250 4 2.6 0.4 400 4 3.8 0.5 630 4 5.2 0.8 1000 6 8.8 1.0 1600
12,9 | 12.9 | 50 4 0.8 0.1 100 4 1.4 0.2 160 4 1.9 0.3 250 4 2.6 0.4 400 4 3.8 0.5 630 4 5.2 0.8 1000 6 8.8 1.0 1600 6
1,4 | 1.4 | 4 0.8 0.1 100 4 1.4 0.2 160 4 1.9 0.3 250 4 2.6 0.4 400 4 3.8 0.5 630 4 5.2 0.8 1000 6 8.8 1.0 1600 6 12.9
2000 | 2000 | 0.8 0.1 100 4 1.4 0.2 160 4 1.9 0.3 250 4 2.6 0.4 400 4 3.8 0.5 630 4 5.2 0.8 1000 6 8.8 1.0 1600 6 12.9 1.4
6 | 6 | 0.1 100 4 1.4 0.2 160 4 1.9 0.3 250 4 2.6 0.4 400 4 3.8 0.5 630 4 5.2 0.8 1000 6 8.8 1.0 1600 6 12.9 1.4 2000
16,1 | 16.1 | 100 4 1.4 0.2 160 4 1.9 0.3 250 4 2.6 0.4 400 4 3.8 0.5 630 4 5.2 0.8 1000 6 8.8 1.0 1600 6 12.9 1.4 2000 6
1,8 | 1.8 | 4 1.4 0.2 160 4 1.9 0.3 250 4 2.6 0.4 400 4 3.8 0.5 630 4 5.2 0.8 1000 6 8.8 1.0 1600 6 12.9 1.4 2000 6 16.1
2500 | 2500 | 1.4 0.2 160 4 1.9 0.3 250 4 2.6 0.4 400 4 3.8 0.5 630 4 5.2 0.8 1000 6 8.8 1.0 1600 6 12.9 1.4 2000 6 16.1 1.8
6 | 6 | 0.2 160 4 1.9 0.3 250 4 2.6 0.4 400 4 3.8 0.5 630 4 5.2 0.8 1000 6 8.8 1.0 1600 6 12.9 1.4 2000 6 16.1 1.8 2500
20,2 | 20.2 | 160 4 1.9 0.3 250 4 2.6 0.4 400 4 3.8 0.5 630 4 5.2 0.8 1000 6 8.8 1.0 1600 6 12.9 1.4 2000 6 16.1 1.8 2500 6
2,1 | 2.1 | 4 1.9 0.3 250 4 2.6 0.4 400 4 3.8 0.5 630 4 5.2 0.8 1000 6 8.8 1.0 1600 6 12.9 1.4 2000 6 16.1 1.8 2500 6 20.2
Oliegevulde transformatoren | Oil-filled transformers | 1.9 0.3 250 4 2.6 0.4 400 4 3.8 0.5 630 4 5.2 0.8 1000 6 8.8 1.0 1600 6 12.9 1.4 2000 6 16.1 1.8 2500 6 20.2 2.1
De meeste transformatoren zijn uitgevoerd als oliegevulde transformatoren. Het isolatiemedium van oliegevulde transformatoren bestaat uit papierisolatie die is gewikkeld om de geleiders van de wikkelingen en de olie, waarin de kern en de wikkelingen gedompeld zijn. De koeling wordt verkregen doordat de olie op natuurlijke wijze in de transformator circuleert tussen de wikkelingen en de transformatorbak. Figuur 4.13 geeft een mooi beeld van een opengewerkte oliegevulde distributietransformator. In het binnenste is het juk met de drie MS-wikkelingen zichtbaar. De LS-wikkelingen bevinden zich daaronder. De drie MS-aansluitklemmen zijn goed zichtbaar aan de bovenzijde. De vier LS-aansluitklemmen (drie fasen en sterpunt) bevinden zich erachter. | Most transformers are designed as oil-filled transformers. The insulation medium of oil-filled transformers consists of paper insulation wrapped around the conductors of the windings and the oil in which the core and windings are immersed. Cooling is achieved by the natural circulation of oil within the transformer between the windings and the transformer tank. Figure 4.13 provides a clear view of a cutaway oil-filled distribution transformer. Inside, the yoke with the three medium voltage (MV) windings is visible. The low voltage (LV) windings are located below them. The three MV terminal connections are clearly visible at the top. The four LV terminal connections (three phases and neutral) are located behind them. | 250 4 2.6 0.4 400 4 3.8 0.5 630 4 5.2 0.8 1000 6 8.8 1.0 1600 6 12.9 1.4 2000 6 16.1 1.8 2500 6 20.2 2.1 Oil-filled transformers
Figuur 4.12 Oliegevulde distributietransformatoren | Figure 4.12 Oil-filled distribution transformers | (LV) windings are located below them. The three MV terminal connections are clearly visible at the top. The four LV terminal connections (three phases and neutral) are located behind them.
De maximaal toelaatbare temperatuur van de papierisolatie is gesteld op 140 °C. Voor de belastbaarheid van de transformator is dit een beperkende factor. Het bereiken van de maximale temperatuur wordt evenals bij kabels beïnvloed door de omgevingstemperatuur en door de temperatuurstijging van de geleiders. | The maximum allowable temperature of the paper insulation is set at 140 °C. This is a limiting factor for the load capacity of the transformer. Reaching the maximum temperature, as with cables, is influenced by the ambient temperature and the temperature rise of the conductors. | them. The three MV terminal connections are clearly visible at the top. The four LV terminal connections (three phases and neutral) are located behind them. Figure 4.12 Oil-filled distribution transformers
Figuur 4.13 Opengewerkte distributietransformator en zijn schakelschema | Figure 4.13 Cutaway view of distribution transformer and its circuit diagram | a limiting factor for the load capacity of the transformer. Reaching the maximum temperature, as with cables, is influenced by the ambient temperature and the temperature rise of the conductors.
Op specifieke plaatsen tussen de windingen in de transformator kunnen hot spots optreden. Dit zijn plekken die warmer zijn dan gemiddeld. Een hot spot temperatuur boven 98 °C heeft een grote nadelige invloed op de levensduur van het isolatiemedium van de transformator en daarmee op zijn levensduur. Boven de 140 °C wordt de papierisolatie onherstelbaar aangetast. In de winter is door de lage omgevingstemperatuur de transformator iets hoger belastbaar dan in de zomer. | At specific locations between the windings in the transformer, hot spots can occur. These are areas that are warmer than average. A hot spot temperature above 98°C has a significant adverse effect on the lifespan of the transformer's insulation medium and, consequently, on its overall lifespan. Above 140°C, the paper insulation becomes irreparably damaged. In winter, due to the lower ambient temperature, the transformer can handle a slightly higher load than in summer. | the maximum temperature, as with cables, is influenced by the ambient temperature and the temperature rise of the conductors. Figure 4.13 Cutaway view of distribution transformer and its circuit diagram
Oliegevulde transformatoren worden als voedingstransformatoren en als distributietransformatoren toegepast. Distributietransformatoren worden in het algemeen minder zwaar belast dan voedingstransformatoren omdat bij het plaatsen rekening wordt gehouden met een groei van de belasting gedurende hun verwachte plaatsingsduur. Het blijkt niet voldoende om alleen de gemiddelde temperatuur van de olie te monitoren. Werkelijk optredende hot spot temperaturen zijn van vele omstandigheden afhankelijk, zoals constructie, buitentemperatuur en bedrijfsvoering. De toelaatbare belasting van de oliegevulde transformator wordt met name bepaald door: | Oil-filled transformers are used as power transformers and as distribution transformers. Distribution transformers are generally less heavily loaded than power transformers because their placement takes into account the expected growth in load over their anticipated service life. It is not sufficient to monitor only the average temperature of the oil. Actual occurring hot spot temperatures depend on many factors, such as construction, ambient temperature, and operation. The permissible load of the oil-filled transformer is primarily determined by: | its overall lifespan. Above 140°C, the paper insulation becomes irreparably damaged. In winter, due to the lower ambient temperature, the transformer can handle a slightly higher load than in summer.
periodieke overbelasting als gevolg van het dagelijks variërende belastingspatroon of | periodic overloading as a result of the daily varying load pattern or | of the oil. Actual occurring hot spot temperatures depend on many factors, such as construction, ambient temperature, and operation. The permissible load of the oil-filled transformer is primarily determined by:
tijdelijke overbelasting in geval van storingssituaties. | temporary overloading in case of fault situations. | such as construction, ambient temperature, and operation. The permissible load of the oil-filled transformer is primarily determined by: periodic overloading as a result of the daily varying load pattern or
Er is gepubliceerd over methodes om in praktijk met deze materie om te gaan (Nuon, 2005) en IEC heeft normen gepubliceerd voor de berekening van de maximaal toegestane overbelasting (IEC 60076-2 en IEC 60076-7). | Methods for dealing with this matter in practice have been published (Nuon, 2005), and IEC has published standards for calculating the maximum permissible overload (IEC 60076-2 and IEC 60076-7). | The permissible load of the oil-filled transformer is primarily determined by: periodic overloading as a result of the daily varying load pattern or temporary overloading in case of fault situations.
Droge transformatoren | Dry transformers | situations. Methods for dealing with this matter in practice have been published (Nuon, 2005), and IEC has published standards for calculating the maximum permissible overload (IEC 60076-2 and IEC 60076-7).
In verband met milieueisen of veiligheid mogen soms geen oliegevulde transformatoren worden toegepast. In die gevallen worden gietharstransformatoren gebruikt. | Due to environmental or safety requirements, oil-filled transformers are sometimes not allowed. In those cases, cast resin transformers are used. | for dealing with this matter in practice have been published (Nuon, 2005), and IEC has published standards for calculating the maximum permissible overload (IEC 60076-2 and IEC 60076-7). Dry transformers
Deze transformatoren zijn duurder en moeten in geconditioneerde ruimtes (met betrekking tot vocht en stof) staan. Droge transformatoren warmen sneller op dan oliegevulde transformatoren en kunnen zodoende minder lang overbelast worden. | These transformers are more expensive and must be placed in conditioned environments (with respect to moisture and dust). Dry transformers heat up faster than oil-filled transformers and therefore can be overloaded for a shorter duration. | maximum permissible overload (IEC 60076-2 and IEC 60076-7). Dry transformers Due to environmental or safety requirements, oil-filled transformers are sometimes not allowed. In those cases, cast resin transformers are used.
De maximaal toegestane temperatuur van droge transformatoren wordt bepaald door de isolatie. De transformatoren zijn ingedeeld in isolatieklassen, die elk een specifieke maximale hot spot temperatuur voorschrijven. Voor deze transformatoren bestaan normen die voorschrijven hoe met overbelasting moet worden omgegaan (IEC 60076-12). | The maximum allowable temperature of dry transformers is determined by the insulation. The transformers are classified into insulation classes, each prescribing a specific maximum hot spot temperature. There are standards for these transformers that dictate how to handle overloading (IEC 60076-12). | and must be placed in conditioned environments (with respect to moisture and dust). Dry transformers heat up faster than oil-filled transformers and therefore can be overloaded for a shorter duration.
Figuur 4.14 Inwendige van een gietharstransformator van 1000 kVA en 12 kV | Figure 4.14 Interior of a cast resin transformer of 1000 kVA and 12 kV | insulation. The transformers are classified into insulation classes, each prescribing a specific maximum hot spot temperature. There are standards for these transformers that dictate how to handle overloading (IEC 60076-12).
Transformatorregeling | Transformatorregeling | spot temperature. There are standards for these transformers that dictate how to handle overloading (IEC 60076-12). Figure 4.14 Interior of a cast resin transformer of 1000 kVA and 12 kV
De wikkelingen van transformatoren kunnen worden uitgevoerd met aftakkingen waardoor andere overzetverhoudingen kunnen worden gekozen. Bij de meeste MS/LS distributietransformatoren zijn deze aftakkingen aan de primaire zijde aangesloten. Op deze aftakkingen zijn de contacten van een instelbare trappenschakelaar aangesloten. Deze schakelaar kan veelal alleen geschakeld worden als de transformator buiten bedrijf is. Deze transformatoren zijn uitgevoerd met vijf instelbare trappen. De keuze voor de juiste trapstand hangt af van de gemiddelde spanning aan MS-zijde en de gewenste spanning in het LS-net. | The windings of transformers can be equipped with taps that allow for different voltage ratios to be selected. In most medium voltage/low voltage (MV/LV) distribution transformers, these taps are connected on the primary side. The contacts of an adjustable tap changer are connected to these taps. This switch can usually only be operated when the transformer is out of service. These transformers are equipped with five adjustable steps. The choice of the correct tap position depends on the average voltage on the MV side and the desired voltage in the LV network. | temperature. There are standards for these transformers that dictate how to handle overloading (IEC 60076-12). Figure 4.14 Interior of a cast resin transformer of 1000 kVA and 12 kV Transformatorregeling
Daarnaast bestaan er regelbare transformatoren waarbij de trappenschakelaar tijdens bedrijf kan worden versteld. De trappenschakelaar zal zich hierbij veelal aan de primaire zijde van de transformator bevinden. Dit omdat aan de primaire zijde de stroomwaarden kleiner zijn dan aan de secundaire zijde en daardoor de schakelaar minder robuust hoeft te worden uitgevoerd. De volgende uitvoeringsvormen bestaan: | Additionally, there are adjustable transformers where the tap changer can be adjusted during operation. The tap changer is usually located on the primary side of the transformer. This is because the current values on the primary side are smaller than on the secondary side, and therefore the switch does not need to be as robust. The following configurations exist: | are equipped with five adjustable steps. The choice of the correct tap position depends on the average voltage on the MV side and the desired voltage in the LV network.
HS/MS transformatoren | HV/MV transformers | because the current values on the primary side are smaller than on the secondary side, and therefore the switch does not need to be as robust. The following configurations exist:
regelingen zonder stroomcompensatie | systems without current compensation | current values on the primary side are smaller than on the secondary side, and therefore the switch does not need to be as robust. The following configurations exist: HV/MV transformers
regelingen met stroomcompensatie | systems with current compensation | primary side are smaller than on the secondary side, and therefore the switch does not need to be as robust. The following configurations exist: HV/MV transformers systems without current compensation
MS-regeltransformatoren (booster) | MV control transformers (booster) | than on the secondary side, and therefore the switch does not need to be as robust. The following configurations exist: HV/MV transformers systems without current compensation systems with current compensation
MS/LS geregelde transformatoren | MV/LV regulated transformers | side, and therefore the switch does not need to be as robust. The following configurations exist: HV/MV transformers systems without current compensation systems with current compensation MV control transformers (booster)
LS-regeltransformatoren | LV regulated transformers | the switch does not need to be as robust. The following configurations exist: HV/MV transformers systems without current compensation systems with current compensation MV control transformers (booster) MV/LV regulated transformers
Figuur 4.15 Principe van een trappenschakelaar | Figure 4.15 Principle of a step switch | not need to be as robust. The following configurations exist: HV/MV transformers systems without current compensation systems with current compensation MV control transformers (booster) MV/LV regulated transformers LV regulated transformers
Figuur 4.16 Trappenschakelaar van een oliegevulde transformator | Figure 4.16 Step switch of an oil-filled transformer | following configurations exist: HV/MV transformers systems without current compensation systems with current compensation MV control transformers (booster) MV/LV regulated transformers LV regulated transformers Figure 4.15 Principle of a step switch
HS/MS transformatoren | HV/MV transformers | compensation systems with current compensation MV control transformers (booster) MV/LV regulated transformers LV regulated transformers Figure 4.15 Principle of a step switch Figure 4.16 Step switch of an oil-filled transformer
In de HS/MS onderstations staan regelbare transformatoren opgesteld. Deze voedingstransformatoren hebben een trappenschakelaar die in bedrijf geschakeld wordt met behulp van een OLTC (On Load Tap Changer). Een keuzeschakelaar stelt de overzetverhouding voor twee naast elkaar gelegen aftakkingen in, waarna een twee standenschakelaar de overgang naar de volgende aftakking realiseert. De twee standenschakelaar realiseert de omschakeling via twee weerstanden voor de demping. In figuur 4.15 is de trappenschakelaar in stand 3. Door schakelaar 2 of 4 te sluiten wordt een hogere dan wel lagere overzetverhouding gekozen. De omschakeling wordt pas een feit door de twee standenschakelaar van stand B naar stand A te verplaatsen. De trappenschakelaar bevindt zich meestal aan de primaire zijde omdat daar de stromen kleiner zijn en een lichtere schakelaarconstructie gekozen kan worden. | In the HV/MV substations, adjustable transformers are installed. These supply transformers have a tap changer that is operated using an OLTC (On Load Tap Changer). A selector switch sets the transformation ratio for two adjacent taps, after which a two-position switch realizes the transition to the next tap. The two-position switch achieves the transition via two resistors for damping. In figure 4.15, the tap changer is in position 3. By closing switch 2 or 4, a higher or lower transformation ratio is selected. The transition is only completed by moving the two-position switch from position B to position A. The tap changer is usually located on the primary side because the currents are smaller there, allowing for a lighter switch construction. | with current compensation MV control transformers (booster) MV/LV regulated transformers LV regulated transformers Figure 4.15 Principle of a step switch Figure 4.16 Step switch of an oil-filled transformer HV/MV transformers
De besturing van deze trappenschakelaar gebeurt automatisch op basis van de aan secundaire zijde gemeten spanning. Op deze wijze blijft de spanning op de MS-rail binnen een marge redelijk constant. Figuur 4.16 illustreert de uitvoering van een trappenschakelaar. Duidelijk zichtbaar is dat de contacten van de trappenschakelaar zich naast de wikkelingen in dezelfde oliegevulde transformatorbak bevinden. | The control of this tap changer is done automatically based on the voltage measured on the secondary side. In this way, the voltage on the medium-voltage busbar remains reasonably constant within a margin. Figure 4.16 illustrates the design of a tap changer. It is clearly visible that the contacts of the tap changer are located next to the windings in the same oil-filled transformer tank. | two-position switch from position B to position A. The tap changer is usually located on the primary side because the currents are smaller there, allowing for a lighter switch construction.
MS-regeltransformatoren | Medium-voltage regulating transformers | illustrates the design of a tap changer. It is clearly visible that the contacts of the tap changer are located next to the windings in the same oil-filled transformer tank.
In uitgestrekte MS-netten kunnen regeltransformatoren worden toegepast. Deze staan opgesteld in de regelstations. Met behulp van deze transformator kan, onafhankelijk van de regeling in het onderstation, de waarde van de spanning in het achterliggende MS-net worden verbeterd. Deze regeltransformatoren zijn vaak autotransformatoren of boostertransformatoren. | In extensive medium-voltage networks, regulating transformers can be used. These are installed in the regulating stations. With the help of these transformers, the voltage value in the downstream medium-voltage network can be improved, independent of the regulation in the substation. These regulating transformers are often autotransformers or booster transformers. | of a tap changer. It is clearly visible that the contacts of the tap changer are located next to the windings in the same oil-filled transformer tank. Medium-voltage regulating transformers
MS/LS geregelde transformatoren | MV/LV regulated transformers | of these transformers, the voltage value in the downstream medium-voltage network can be improved, independent of the regulation in the substation. These regulating transformers are often autotransformers or booster transformers.
Indien bijzondere eisen worden gesteld aan de kwaliteit van de spanning bij aan-geslotenen in een LS-net, dan kan het wenselijk zijn een geregelde MS/LS distributietransformator toe te passen. Grote spanningsafwijkingen kunnen veroorzaakt worden door een sterk wisselende MS-voedingsspanning en door sterke belastingsveranderingen in het LS-net. Een duidelijk praktijkprobleem treedt op bij decentrale opwekkers in de glastuinbouw (zie figuren 3.6 en 3.7). In deze gevallen kan een geregelde MS/LS distributietransformator worden ingezet om de spanning aan laagspanningszijde te regelen. Dit is een relatief nieuw ontwerp, waarbij niet met behulp van een trappenschakelaar maar met behulp van vermogenselektronica (IGBT’s) geschakeld wordt tussen de aftakkingen van de primaire wikkeling. Hiermee is het mogelijk om ook tussen twee trapstanden een variabele spanning te kiezen, waarmee over het gehele bereik een traploze regeling is gerealiseerd. Hiermee kan een stabiele secundaire spanning worden gerealiseerd (Imtech Vonk, 2010). | If special requirements are imposed on the quality of the voltage for consumers in an LV network, it may be desirable to use a regulated MV/LV distribution transformer. Large voltage deviations can be caused by a highly variable MV supply voltage and significant load changes in the LV network. A clear practical problem occurs with decentralized generators in greenhouse horticulture (see figures 3.6 and 3.7). In these cases, a regulated MV/LV distribution transformer can be used to regulate the voltage on the low-voltage side. This is a relatively new design, where switching between the taps of the primary winding is done not with a tap changer but with power electronics (IGBTs). This makes it possible to choose a variable voltage between two tap positions, achieving a stepless regulation over the entire range. This allows for a stable secondary voltage to be realized (Imtech Vonk, 2010). | the voltage value in the downstream medium-voltage network can be improved, independent of the regulation in the substation. These regulating transformers are often autotransformers or booster transformers. MV/LV regulated transformers
Figuur 4.17 Schakelschema van een elektronisch geregelde MS/LS transformator | Figure 4.17 Circuit diagram of an electronically controlled MV/LV transformer | to choose a variable voltage between two tap positions, achieving a stepless regulation over the entire range. This allows for a stable secondary voltage to be realized (Imtech Vonk, 2010).
Figuur 4.17 illustreert de werking met behulp van de elektronische schakelaars. Indien alleen schakelaar 1 gesloten is, staat de primaire spanning over de volledige primaire wikkeling. Indien schakelaar 1 geopend wordt en schakelaar 2 gesloten, wordt één deel van de primaire wikkeling stroomloos. Als gevolg stijgt de secundaire spanning. De secundaire spanning kan verder worden opgeregeld door te schakelen met schakelaars 2 en 3 en met schakelaars 3 en 4. Doordat de elektronische schakelaars zeer snel (ongeveer 10 kHz) schakelen, regelt de transformator de schakeling van de primaire wikkelingen bij benadering traploos. | Figure 4.17 illustrates the operation using electronic switches. If only switch 1 is closed, the primary voltage is applied across the entire primary winding. If switch 1 is opened and switch 2 is closed, one part of the primary winding is de-energized. As a result, the secondary voltage increases. The secondary voltage can be further adjusted by switching with switches 2 and 3 and with switches 3 and 4. Because the electronic switches operate very quickly (approximately 10 kHz), the transformer regulates the switching of the primary windings almost steplessly. | a stepless regulation over the entire range. This allows for a stable secondary voltage to be realized (Imtech Vonk, 2010). Figure 4.17 Circuit diagram of an electronically controlled MV/LV transformer
LS-regeltransformatoren | LS control transformers | 2 and 3 and with switches 3 and 4. Because the electronic switches operate very quickly (approximately 10 kHz), the transformer regulates the switching of the primary windings almost steplessly.
In uitgestrekte LS-netten is soms behoefte aan het verbeteren van de kwaliteit van de spanning. Hierbij worden, vergelijkbaar met de regeltransformatoren op MS-niveau, autotransformatoren ingezet met een redelijk fijne spanningsregeling. Meestal zijn deze transformatoren gecombineerd met een nulpunttransformator waarmee de asymmetrie, door ongelijk verdeelde belasting over de fasen, wordt verbeterd. De nulpunttransformator wordt nader toegelicht in paragraaf 8.4. | In extensive low-voltage networks, there is sometimes a need to improve the quality of the voltage. For this purpose, similar to the regulating transformers at the medium-voltage level, autotransformers with a reasonably fine voltage regulation are used. These transformers are usually combined with a neutral point transformer, which improves asymmetry caused by unevenly distributed loads across the phases. The neutral point transformer is further explained in paragraph 8.4. | and with switches 3 and 4. Because the electronic switches operate very quickly (approximately 10 kHz), the transformer regulates the switching of the primary windings almost steplessly. LS control transformers
4.4 Smoorspoelen | 4.4 Choke Coils | transformers are usually combined with a neutral point transformer, which improves asymmetry caused by unevenly distributed loads across the phases. The neutral point transformer is further explained in paragraph 8.4.
Smoorspoelen worden met name toegepast om de kortsluitstromen te beperken. In sommige gevallen is het kortsluitvermogen te groot voor de standaard installaties in het MS-net. Dit is met name het geval bij onderstations die direct vanuit het hoogspanningsnet gevoed worden. Kortsluitingen dicht bij het onderstation worden via de HS/MS-transformator gevoed vanuit het hoogspanningsnet en kunnen te grote stromen veroorzaken. In die gevallen wordt de kortsluitstroom beperkt door het plaatsen van smoorspoelen in de MS-streng. Vaak worden deze smoorspoelen in het onderstation aan het begin de streng geplaatst. Door tussenschakeling van de smoorspoel neemt de totale impedantie toe, waardoor de kortsluitstroom afneemt. | Choke coils are primarily used to limit short-circuit currents. In some cases, the short-circuit capacity is too large for the standard installations in the medium voltage (MV) network. This is particularly the case for substations that are fed directly from the high voltage (HV) network. Short circuits close to the substation are fed through the HV/MV transformer from the high voltage network and can cause excessively large currents. In such cases, the short-circuit current is limited by placing choke coils in the MV line. These choke coils are often placed at the beginning of the line in the substation. By interposing the choke coil, the total impedance increases, thereby reducing the short-circuit current. | combined with a neutral point transformer, which improves asymmetry caused by unevenly distributed loads across the phases. The neutral point transformer is further explained in paragraph 8.4. 4.4 Choke Coils
Smoorspoelen worden niet toegepast bij TS/MS-onderstations. De reden is dat de TS/MS-transformator gevoed wordt door een HS/TS-transformator, hogerop in het net. De serieschakeling van deze twee transformatoren maakt dat de maximale waarde van de kortsluitstroom, in vergelijking met de waarden die bij HS/MS-onderstations bereikt kunnen worden, de grenswaarde van de installatie niet overschrijdt. | Choke coils are not used in TS/MS substations. The reason is that the TS/MS transformer is fed by an HS/TS transformer higher up in the network. The series connection of these two transformers ensures that the maximum value of the short-circuit current, compared to the values that can be reached in HS/MS substations, does not exceed the installation's limit value. | line. These choke coils are often placed at the beginning of the line in the substation. By interposing the choke coil, the total impedance increases, thereby reducing the short-circuit current.
Een driefasensmoorspoel bestaat uit drie luchtspoelen, voor elke fase een, die boven elkaar gestapeld worden, zoals afgebeeld in figuur 4.18. De individuele spoelen zijn op zodanige afstand van elkaar gemonteerd, dat de onderlinge inductieve koppeling verwaarloosbaar klein is. | A three-phase reactor consists of three air-core coils, one for each phase, stacked on top of each other as shown in figure 4.18. The individual coils are mounted at such a distance from each other that the mutual inductive coupling is negligibly small. | these two transformers ensures that the maximum value of the short-circuit current, compared to the values that can be reached in HS/MS substations, does not exceed the installation's limit value.
Figuur 4.18 Kortsluitstroom beperkende smoorspoelen, drie fasen gestapeld | Figure 4.18 Short-circuit current limiting reactors, three phases stacked | on top of each other as shown in figure 4.18. The individual coils are mounted at such a distance from each other that the mutual inductive coupling is negligibly small.
Luchtspoelen hebben het voordeel dat zij niet in verzadiging geraken bij het voeren van een kortsluitstroom. Bovendien hebben zij lage weerstandverliezen, die vaak verwaarloosd worden. De impedantie, waardoor de kortsluitstroom wordt beperkt, is bijna uitsluitend reactief. Het berekenen van de kortsluitstroom is beschreven in hoofdstuk 10. Een voorbeeld van de specificaties van een smoorspoel is: | Air-core reactors have the advantage that they do not become saturated when carrying a short-circuit current. Additionally, they have low resistance losses, which are often negligible. The impedance that limits the short-circuit current is almost exclusively reactive. The calculation of the short-circuit current is described in Chapter 10. An example of the specifications of a reactor is: | 4.18. The individual coils are mounted at such a distance from each other that the mutual inductive coupling is negligibly small. Figure 4.18 Short-circuit current limiting reactors, three phases stacked
U | U | impedance that limits the short-circuit current is almost exclusively reactive. The calculation of the short-circuit current is described in Chapter 10. An example of the specifications of a reactor is:
nom | nom | that limits the short-circuit current is almost exclusively reactive. The calculation of the short-circuit current is described in Chapter 10. An example of the specifications of a reactor is: U
: 10 kV | : 10 kV | limits the short-circuit current is almost exclusively reactive. The calculation of the short-circuit current is described in Chapter 10. An example of the specifications of a reactor is: U nom
S | S | current is almost exclusively reactive. The calculation of the short-circuit current is described in Chapter 10. An example of the specifications of a reactor is: U nom : 10 kV
nom | nom | is almost exclusively reactive. The calculation of the short-circuit current is described in Chapter 10. An example of the specifications of a reactor is: U nom : 10 kV S
: 5,8 MVA (I | : 5.8 MVA (I | almost exclusively reactive. The calculation of the short-circuit current is described in Chapter 10. An example of the specifications of a reactor is: U nom : 10 kV S nom
nom | nom | calculation of the short-circuit current is described in Chapter 10. An example of the specifications of a reactor is: U nom : 10 kV S nom : 5.8 MVA (I
of the short-circuit current is described in Chapter 10. An example of the specifications of a reactor is: U nom : 10 kV S nom : 5.8 MVA (I nom
u | u | current is described in Chapter 10. An example of the specifications of a reactor is: U nom : 10 kV S nom : 5.8 MVA (I nom = 335 A)
k | k | is described in Chapter 10. An example of the specifications of a reactor is: U nom : 10 kV S nom : 5.8 MVA (I nom = 335 A) u
: 1,74 % | : 1.74% | described in Chapter 10. An example of the specifications of a reactor is: U nom : 10 kV S nom : 5.8 MVA (I nom = 335 A) u k
P | P | Chapter 10. An example of the specifications of a reactor is: U nom : 10 kV S nom : 5.8 MVA (I nom = 335 A) u k : 1.74%
k | k | 10. An example of the specifications of a reactor is: U nom : 10 kV S nom : 5.8 MVA (I nom = 335 A) u k : 1.74% P
: 2,69 kW | : 2.69 kW | An example of the specifications of a reactor is: U nom : 10 kV S nom : 5.8 MVA (I nom = 335 A) u k : 1.74% P k
R : 0,008 | R: 0.008 | the specifications of a reactor is: U nom : 10 kV S nom : 5.8 MVA (I nom = 335 A) u k : 1.74% P k : 2.69 kW
Ω | Ohms | of a reactor is: U nom : 10 kV S nom : 5.8 MVA (I nom = 335 A) u k : 1.74% P k : 2.69 kW R: 0.008
X : 0,3 | X: 0.3 | a reactor is: U nom : 10 kV S nom : 5.8 MVA (I nom = 335 A) u k : 1.74% P k : 2.69 kW R: 0.008 Ohms
Ω | Ohms | is: U nom : 10 kV S nom : 5.8 MVA (I nom = 335 A) u k : 1.74% P k : 2.69 kW R: 0.008 Ohms X: 0.3
I | I | U nom : 10 kV S nom : 5.8 MVA (I nom = 335 A) u k : 1.74% P k : 2.69 kW R: 0.008 Ohms X: 0.3 Ohms
k,2sec | k,2sec | nom : 10 kV S nom : 5.8 MVA (I nom = 335 A) u k : 1.74% P k : 2.69 kW R: 0.008 Ohms X: 0.3 Ohms I
: 14 kA | : 14 kA | : 10 kV S nom : 5.8 MVA (I nom = 335 A) u k : 1.74% P k : 2.69 kW R: 0.008 Ohms X: 0.3 Ohms I k,2sec
4.5 Vermogenschakelaars | 4.5 Circuit Breakers | S nom : 5.8 MVA (I nom = 335 A) u k : 1.74% P k : 2.69 kW R: 0.008 Ohms X: 0.3 Ohms I k,2sec : 14 kA
Een vermogenschakelaar heeft als taak het inschakelen, voeren en uitschakelen van een normale bedrijfstroom en het afschakelen van overbelastingen en kortsluitstromen. Een vermogenschakelaar moet zodanig gekozen worden dat hij in staat is de grootst mogelijke kortsluitstroom af te schakelen. De kortsluitstroom moet dan ook worden berekend voor elke locatie waar een vermogenschakelaar wordt opgesteld. De wijze waarop deze berekend wordt, is beschreven in hoofdstuk 10. De vermogenschakelaar is een van de belangrijkste beveiligende componenten in het elektriciteitsnet. De belangrijkste gespecificeerde kenmerken zijn de nominale spanning en de uitschakelstroom (de grootte van de maximaal af te schakelen stroom), in kA, of het schakelvermogen (het maximaal af te schakelen vermogen), in MVA. | A circuit breaker is responsible for switching on, carrying, and switching off a normal operating current, as well as disconnecting overloads and short-circuit currents. A circuit breaker must be selected in such a way that it is capable of disconnecting the maximum possible short-circuit current. Therefore, the short-circuit current must be calculated for each location where a circuit breaker is installed. The method for this calculation is described in chapter 10. The circuit breaker is one of the most important protective components in the electrical network. The main specified characteristics are the nominal voltage and the breaking current (the magnitude of the maximum current to be disconnected), in kA, or the breaking capacity (the maximum power to be disconnected), in MVA. | 5.8 MVA (I nom = 335 A) u k : 1.74% P k : 2.69 kW R: 0.008 Ohms X: 0.3 Ohms I k,2sec : 14 kA 4.5 Circuit Breakers
Alle vermogenschakelaars hebben dezelfde basiskenmerken maar verschillen onderling sterk voor de diverse spanningsniveaus, maximale afschakelstroom en type. De vermogenschakelaar wordt aangestuurd door de beveiliging (beschreven in hoofdstuk 6). De beveiliging geeft bij het overschrijden van de ingestelde stroom, spanning of een combinatie daarvan, een afschakelcommando (trip) naar de vermogenschakelaar. Hierop opent de vermogenschakelaar, aangedreven door een mechanisme, zijn contacten. | All circuit breakers have the same basic features but differ significantly for various voltage levels, maximum breaking current, and type. The circuit breaker is controlled by the protection system (described in chapter 6). When the set current, voltage, or a combination thereof is exceeded, the protection system sends a trip command to the circuit breaker. In response, the circuit breaker, driven by a mechanism, opens its contacts. | the nominal voltage and the breaking current (the magnitude of the maximum current to be disconnected), in kA, or the breaking capacity (the maximum power to be disconnected), in MVA.
Figuur 4.19 Vacuüm MS vermogenschakelaar | Figure 4.19 Vacuum MV circuit breaker | voltage, or a combination thereof is exceeded, the protection system sends a trip command to the circuit breaker. In response, the circuit breaker, driven by a mechanism, opens its contacts.
Figuur 4.20 Vacuüm MS vermogenschakelaar | Figure 4.20 Vacuum MV circuit breaker | exceeded, the protection system sends a trip command to the circuit breaker. In response, the circuit breaker, driven by a mechanism, opens its contacts. Figure 4.19 Vacuum MV circuit breaker
Dit mechanisme kan een veermechanisme zijn, een mechanisme dat wordt aangedreven door gecomprimeerde lucht of een mechanisme dat is gebaseerd op elektromagnetische krachten (EM-aandrijving). Bij het openen van de contacten ontstaat een lichtboog, die zo snel mogelijk gedoofd moet worden. De lichtboog wordt onderbroken in een bluskamer. De bluskamer kan gevuld zijn met olie, SF | This mechanism can be a spring mechanism, a mechanism driven by compressed air, or a mechanism based on electromagnetic forces (EM drive). When the contacts open, an arc is created, which must be extinguished as quickly as possible. The arc is interrupted in an arc chamber. The arc chamber can be filled with oil, SF | trip command to the circuit breaker. In response, the circuit breaker, driven by a mechanism, opens its contacts. Figure 4.19 Vacuum MV circuit breaker Figure 4.20 Vacuum MV circuit breaker
6 | 6 | open, an arc is created, which must be extinguished as quickly as possible. The arc is interrupted in an arc chamber. The arc chamber can be filled with oil, SF
of vacuüm. In oliearme schakelaars wordt de lichtboog gedoofd door er een straal ongeïoniseerde verse olie langs te blazen. In SF | or vacuum. In oil-minimal switches, the arc is extinguished by blowing a jet of non-ionized fresh oil along it. In SF | an arc is created, which must be extinguished as quickly as possible. The arc is interrupted in an arc chamber. The arc chamber can be filled with oil, SF 6
6 | 6 | arc chamber can be filled with oil, SF 6 or vacuum. In oil-minimal switches, the arc is extinguished by blowing a jet of non-ionized fresh oil along it. In SF
schakelaars wordt de lichtboog gedoofd door de diëlektrische eigenschappen van het gas. In vacuümschakelaars is weinig tot geen medium aanwezig dat kan ioniseren, zodat er een minimale lichtboog ontstaat. Het isolatiemedium of het vacuüm in de bluskamer dienen ervoor te zorgen dat de lichtboog dooft als de stroom de eerstvolgende nuldoorgang bereikt. Vacuümschakelaars worden veelvuldig gebruikt in modern MS-schakelmaterieel tot 36 kV. Dit schakelmaterieel is geschikt voor uitschakelstromen tot 50 kA. | switches, the arc is extinguished by the dielectric properties of the gas. In vacuum switches, there is little to no medium present that can ionize, resulting in a minimal arc. The insulating medium or the vacuum in the arc chamber ensures that the arc is extinguished when the current reaches the next zero crossing. Vacuum switches are widely used in modern medium-voltage switchgear up to 36 kV. This switchgear is suitable for breaking currents up to 50 kA. | chamber can be filled with oil, SF 6 or vacuum. In oil-minimal switches, the arc is extinguished by blowing a jet of non-ionized fresh oil along it. In SF 6
De oliearme vermogenschakelaar is zodanig ontworpen dat hij de hitte van de lichtboog tijdens het onderbreken van de kortsluitstroom kan weerstaan. Tijdens het afschakelen ontstaan inbrandplekken op de contacten, zodat de vermogenschakelaar na een gespecificeerd aantal schakelhandelingen moet worden gereviseerd. Bij vacuüm vermogenschakelaars wordt inbranden van de contacten voorkomen door de kortsluitstroom door middel van een magneetveld over het gehele oppervlak van de contacten te verdelen (het principe van ‘diffuse ontlading’) of door een snelle rotatie over het oppervlak. Hiermee wordt bereikt dat de contacten in een vacuüm vermogenschakelaar geen enkel onderhoud behoeven. Figuur 4.19 geeft een voorbeeld van een vacuüm vermogenschakelaar en figuur 4.20 toont de uitvoeringsvorm van een uitrijdbare vacuüm vermogenschakelaar. | The low-oil circuit breaker is designed to withstand the heat of the arc during the interruption of the short-circuit current. During disconnection, burn marks appear on the contacts, so the circuit breaker must be overhauled after a specified number of switching operations. In vacuum circuit breakers, burning of the contacts is prevented by distributing the short-circuit current over the entire surface of the contacts using a magnetic field (the principle of 'diffuse discharge') or by rapid rotation over the surface. This ensures that the contacts in a vacuum circuit breaker require no maintenance. Figure 4.19 provides an example of a vacuum circuit breaker, and Figure 4.20 shows the design of a withdrawable vacuum circuit breaker. | current reaches the next zero crossing. Vacuum switches are widely used in modern medium-voltage switchgear up to 36 kV. This switchgear is suitable for breaking currents up to 50 kA.
4.6 Schakelinstallaties | 4.6 Switchgear Installations | in a vacuum circuit breaker require no maintenance. Figure 4.19 provides an example of a vacuum circuit breaker, and Figure 4.20 shows the design of a withdrawable vacuum circuit breaker.
Schakelinstallaties worden in onder-, regel-, schakel- en netstations gebruikt voor het veranderen van de netwerkconfiguratie en voor het afschakelen van kortsluitingen. In onderstations en schakelstations verdeelt de schakelinstallatie de voeding van de MS-strengen. In geval van een storing kunnen eventueel aanwezige reservecomponenten ingeschakeld worden. Ook worden op strategische stations in het netwerk vermogenschakelaars met beveiligingen ingezet om eventueel optredende kortsluitstromen selectief af te schakelen. Van alle netstations in een MS-ring wordt er één gekozen waarvan een schakelaar of lastscheider normaal geopend is, waarmee een gewenste netopening wordt gecreëerd. De meeste netstations zijn uitgerust met handmatig te bedienen lastscheiders in de kabelaansluitingen. Met een lastscheider kan alleen de nominale belastingstroom worden afgeschakeld. Voor het afschakelen van een kortsluitstroom of het inschakelen van een belastingstroom is een vermogenschakelaar vereist. De MS/LS transformator in de netstations is aan de MS-zijde beschermd door een vermogenschakelaar of door zekeringen. Aan de LS-zijde worden meestal zekeringen gebruikt om de installatie te beschermen tegen kortsluitstromen. | Switchgear installations are used in substations, control stations, switching stations, and network stations for changing the network configuration and for disconnecting short circuits. In substations and switching stations, the switchgear installation distributes the power of the medium voltage (MV) lines. In case of a fault, any available spare components can be activated. Circuit breakers with protection are also used at strategic stations in the network to selectively disconnect any occurring short-circuit currents. Of all the network stations in an MV ring, one is chosen where a switch or load disconnect switch is normally open, creating a desired network opening. Most network stations are equipped with manually operated load disconnect switches in the cable connections. A load disconnect switch can only disconnect the nominal load current. For disconnecting a short-circuit current or switching on a load current, a circuit breaker is required. The MV/low voltage (LV) transformer in the network stations is protected on the MV side by a circuit breaker or fuses. On the LV side, fuses are usually used to protect the installation against short-circuit currents. | circuit breaker require no maintenance. Figure 4.19 provides an example of a vacuum circuit breaker, and Figure 4.20 shows the design of a withdrawable vacuum circuit breaker. 4.6 Switchgear Installations
Schakelinstallaties kunnen uitgevoerd zijn als: | Switchgear installations can be configured as: | the network stations is protected on the MV side by a circuit breaker or fuses. On the LV side, fuses are usually used to protect the installation against short-circuit currents.
open installaties: afzonderlijke componenten in de openlucht, onderling verbonden met niet geïsoleerde geleiders | open installations: separate components in the open air, interconnected with non-insulated conductors | the MV side by a circuit breaker or fuses. On the LV side, fuses are usually used to protect the installation against short-circuit currents. Switchgear installations can be configured as:
gesloten installaties: componenten samengeschakeld in metalen omhulling, gevuld met een gasvormig, vloeibaar of vaste stof isolerend medium | closed installations: components interconnected in a metal enclosure, filled with a gaseous, liquid, or solid insulating medium | side, fuses are usually used to protect the installation against short-circuit currents. Switchgear installations can be configured as: open installations: separate components in the open air, interconnected with non-insulated conductors
semi-open installaties: afzonderlijke omsloten componenten, onderling verbonden in een open installatie | semi-open installations: separate enclosed components, interconnected in an open installation | as: open installations: separate components in the open air, interconnected with non-insulated conductors closed installations: components interconnected in a metal enclosure, filled with a gaseous, liquid, or solid insulating medium
omsloten installaties: componenten in een volledig gesloten kunststoffen of metalen omhulsel, door de fabriek als een geheel geleverd. | enclosed installations: components in a completely sealed plastic or metal enclosure, delivered as a whole by the factory. | with non-insulated conductors closed installations: components interconnected in a metal enclosure, filled with a gaseous, liquid, or solid insulating medium semi-open installations: separate enclosed components, interconnected in an open installation
In de MS-schakelsystemen wordt gebruik gemaakt van gesloten en omsloten installaties. In de huidig verkrijgbare MS-schakelinstallaties wordt vacuüm- of SF | In the medium voltage switchgear systems, closed and enclosed installations are used. In the currently available medium voltage switchgear installations, vacuum or SF | insulating medium semi-open installations: separate enclosed components, interconnected in an open installation enclosed installations: components in a completely sealed plastic or metal enclosure, delivered as a whole by the factory.
6 | 6 | delivered as a whole by the factory. In the medium voltage switchgear systems, closed and enclosed installations are used. In the currently available medium voltage switchgear installations, vacuum or SF
-technologie toegepast. De schakelinstallaties worden geleverd als kant-en-klare installaties, afgestemd op hun functie: | -technology is applied. The switchgear systems are delivered as turnkey installations, tailored to their function: | as a whole by the factory. In the medium voltage switchgear systems, closed and enclosed installations are used. In the currently available medium voltage switchgear installations, vacuum or SF 6
hoofdverdeelinstallatie, | main distribution installation, | installations are used. In the currently available medium voltage switchgear installations, vacuum or SF 6 -technology is applied. The switchgear systems are delivered as turnkey installations, tailored to their function:
onderverdeelinstallatie en | sub-distribution installation and | In the currently available medium voltage switchgear installations, vacuum or SF 6 -technology is applied. The switchgear systems are delivered as turnkey installations, tailored to their function: main distribution installation,
ringkabelinstallatie. | ring main unit. | available medium voltage switchgear installations, vacuum or SF 6 -technology is applied. The switchgear systems are delivered as turnkey installations, tailored to their function: main distribution installation, sub-distribution installation and
Deze installaties worden op de volgende pagina’s kort beschreven. Daarbij is gebruik gemaakt van informatie van Eaton Holec. | These installations are briefly described on the following pages. Information from Eaton Holec has been used for this purpose. | switchgear installations, vacuum or SF 6 -technology is applied. The switchgear systems are delivered as turnkey installations, tailored to their function: main distribution installation, sub-distribution installation and ring main unit.
Figuur 4.21 Toepassing van typen schakelinstallaties | Figure 4.21 Application of types of switchgear installations | their function: main distribution installation, sub-distribution installation and ring main unit. These installations are briefly described on the following pages. Information from Eaton Holec has been used for this purpose.
Tabel 4.9 Overzicht van de componenten in de schakelinstallaties en hun toepassingen | Table 4.9 Overview of the components in the switchgear installations and their applications | ring main unit. These installations are briefly described on the following pages. Information from Eaton Holec has been used for this purpose. Figure 4.21 Application of types of switchgear installations
Component | Component | from Eaton Holec has been used for this purpose. Figure 4.21 Application of types of switchgear installations Table 4.9 Overview of the components in the switchgear installations and their applications
Functie | Functie | Eaton Holec has been used for this purpose. Figure 4.21 Application of types of switchgear installations Table 4.9 Overview of the components in the switchgear installations and their applications Component
Toepassing | Toepassing | Holec has been used for this purpose. Figure 4.21 Application of types of switchgear installations Table 4.9 Overview of the components in the switchgear installations and their applications Component Functie
vermogenschakelaars | vermogenschakelaars | has been used for this purpose. Figure 4.21 Application of types of switchgear installations Table 4.9 Overview of the components in the switchgear installations and their applications Component Functie Toepassing
afschakelen van kortsluitstromen | disconnecting short-circuit currents | been used for this purpose. Figure 4.21 Application of types of switchgear installations Table 4.9 Overview of the components in the switchgear installations and their applications Component Functie Toepassing vermogenschakelaars
in onder-, regel- en schakelstations en in beveiligde velden van netstations (>35A) | in substations, control stations, and switchgear stations, and in protected fields of network stations (>35A) | this purpose. Figure 4.21 Application of types of switchgear installations Table 4.9 Overview of the components in the switchgear installations and their applications Component Functie Toepassing vermogenschakelaars disconnecting short-circuit currents
lastscheiders | lastscheiders | components in the switchgear installations and their applications Component Functie Toepassing vermogenschakelaars disconnecting short-circuit currents in substations, control stations, and switchgear stations, and in protected fields of network stations (>35A)
tot stand brengen van een zichtbare onderbreking | creating a visible disconnection | in the switchgear installations and their applications Component Functie Toepassing vermogenschakelaars disconnecting short-circuit currents in substations, control stations, and switchgear stations, and in protected fields of network stations (>35A) lastscheiders
afschakelen van nominale stromen | disconnecting nominal currents | and their applications Component Functie Toepassing vermogenschakelaars disconnecting short-circuit currents in substations, control stations, and switchgear stations, and in protected fields of network stations (>35A) lastscheiders creating a visible disconnection
bestand tegen doorgaande kortsluitstromen | resistant to continuous short-circuit currents | Component Functie Toepassing vermogenschakelaars disconnecting short-circuit currents in substations, control stations, and switchgear stations, and in protected fields of network stations (>35A) lastscheiders creating a visible disconnection disconnecting nominal currents
bestand tegen het inschakelen van een kortsluitstroom | resistant to the switching on of a short-circuit current | short-circuit currents in substations, control stations, and switchgear stations, and in protected fields of network stations (>35A) lastscheiders creating a visible disconnection disconnecting nominal currents resistant to continuous short-circuit currents
in netstations | in network stations | and in protected fields of network stations (>35A) lastscheiders creating a visible disconnection disconnecting nominal currents resistant to continuous short-circuit currents resistant to the switching on of a short-circuit current
scheiders | scheiders | fields of network stations (>35A) lastscheiders creating a visible disconnection disconnecting nominal currents resistant to continuous short-circuit currents resistant to the switching on of a short-circuit current in network stations
tot stand brengen van een zichtbare onderbreking | creating a visible disconnection | of network stations (>35A) lastscheiders creating a visible disconnection disconnecting nominal currents resistant to continuous short-circuit currents resistant to the switching on of a short-circuit current in network stations scheiders
afschakelen van onbelaste circuits | disconnecting unloaded circuits | lastscheiders creating a visible disconnection disconnecting nominal currents resistant to continuous short-circuit currents resistant to the switching on of a short-circuit current in network stations scheiders creating a visible disconnection
bestand tegen doorgaande kortsluitstromen | resistant to continuous short-circuit currents | visible disconnection disconnecting nominal currents resistant to continuous short-circuit currents resistant to the switching on of a short-circuit current in network stations scheiders creating a visible disconnection disconnecting unloaded circuits
in onder-, regel-, schakel- en netstations | in substations, control stations, switching stations, and network stations | resistant to continuous short-circuit currents resistant to the switching on of a short-circuit current in network stations scheiders creating a visible disconnection disconnecting unloaded circuits resistant to continuous short-circuit currents
aarders | aarders | on of a short-circuit current in network stations scheiders creating a visible disconnection disconnecting unloaded circuits resistant to continuous short-circuit currents in substations, control stations, switching stations, and network stations
aarden van systeemonderdelen zodat veilig gewerkt kan worden | grounding of system components to ensure safe operation | of a short-circuit current in network stations scheiders creating a visible disconnection disconnecting unloaded circuits resistant to continuous short-circuit currents in substations, control stations, switching stations, and network stations aarders
in onder-, regel-, schakel- en netstations | in substations, control stations, switching stations, and network stations | creating a visible disconnection disconnecting unloaded circuits resistant to continuous short-circuit currents in substations, control stations, switching stations, and network stations aarders grounding of system components to ensure safe operation
smeltveiligheden | smeltveiligheden | continuous short-circuit currents in substations, control stations, switching stations, and network stations aarders grounding of system components to ensure safe operation in substations, control stations, switching stations, and network stations
onderbreken van kortsluitstromen | interrupting short-circuit currents | short-circuit currents in substations, control stations, switching stations, and network stations aarders grounding of system components to ensure safe operation in substations, control stations, switching stations, and network stations smeltveiligheden
in transformator- en kabelvelden van netstations | in transformer and cable fields of network stations | substations, control stations, switching stations, and network stations aarders grounding of system components to ensure safe operation in substations, control stations, switching stations, and network stations smeltveiligheden interrupting short-circuit currents
Figuur 4.22 MMS en Unitole | Figure 4.22 MMS and Unitole | aarders grounding of system components to ensure safe operation in substations, control stations, switching stations, and network stations smeltveiligheden interrupting short-circuit currents in transformer and cable fields of network stations
Hoofdverdeelinstallatie | Hoofdverdeelinstallatie | to ensure safe operation in substations, control stations, switching stations, and network stations smeltveiligheden interrupting short-circuit currents in transformer and cable fields of network stations Figure 4.22 MMS and Unitole
De hoofdverdeelinstallaties worden in de onder-, regel- en schakelstations toegepast. Het dubbelrailsysteem wordt gevoed door een of meer HS/MS-voedings-transformatoren. Alle velden voor de afgaande richtingen van het MS-transportnet of het MS-distributienet worden hierop aangesloten. Een voorbeeld is MMS, een metaalomsloten, luchtgeïsoleerd schakelsysteem met geïntegreerde vacuümonderbrekers. Dit is gebouwd rond een dubbelrailsysteem en is geschikt voor spanningen tot 24 kV. De installatie is modulair opgebouwd voor vermogenschakelaarvelden en raildwarskoppelvelden. De installatie kan voorzien worden van stationsautomatisering. Een ander voorbeeld is Unitole voor enkelrailtoepassingen. Dit systeem is voorzien van uitrijdbare vacuümvermogenschakelaars en/of contactors. | The main distribution installations are used in substations, control stations, and switching stations. The double busbar system is powered by one or more HV/MV supply transformers. All fields for the outgoing directions of the MV transmission network or the MV distribution network are connected to this. An example is MMS, a metal-enclosed, air-insulated switchgear system with integrated vacuum circuit breakers. This is built around a double busbar system and is suitable for voltages up to 24 kV. The installation is modularly constructed for circuit breaker fields and bus coupler fields. The installation can be equipped with station automation. Another example is Unitole for single busbar applications. This system is equipped with withdrawable vacuum circuit breakers and/or contactors. | ensure safe operation in substations, control stations, switching stations, and network stations smeltveiligheden interrupting short-circuit currents in transformer and cable fields of network stations Figure 4.22 MMS and Unitole Hoofdverdeelinstallatie
Onderverdeelinstallatie | Onderverdeelinstallatie | bus coupler fields. The installation can be equipped with station automation. Another example is Unitole for single busbar applications. This system is equipped with withdrawable vacuum circuit breakers and/or contactors.
De onderverdeelinstallaties worden gebruikt in regel- en schakelstations. Deze installaties worden ook buiten de distributienetten toegepast bij infrastructuurprojecten, bij de industrie en in bedrijfsgebouwen. Ook bij de decentrale opwekking, zoals windparken en grote WKK-installaties worden deze schakelinstallaties gebruikt. Het systeem is meestal voorzien van een langssectioneerbaar enkelrailsysteem. Een voorbeeld is SVS, een metaalomsloten, epoxyharsgeïsoleerd schakelsysteem met vast ingebouwde vacuümvermogenschakelaars. Het systeem is geschikt voor spanningen tot 24 kV. | The distribution installations are used in control and switching stations. These installations are also applied outside the distribution networks in infrastructure projects, in industry, and in commercial buildings. These switching installations are also used in decentralized generation, such as wind farms and large CHP installations. The system is usually equipped with a longitudinally sectionalizable single busbar system. An example is SVS, a metal-enclosed, epoxy resin-insulated switching system with fixed built-in vacuum circuit breakers. The system is suitable for voltages up to 24 kV. | coupler fields. The installation can be equipped with station automation. Another example is Unitole for single busbar applications. This system is equipped with withdrawable vacuum circuit breakers and/or contactors. Onderverdeelinstallatie
Ringkabelinstallaties | Ringkabelinstallaties | sectionalizable single busbar system. An example is SVS, a metal-enclosed, epoxy resin-insulated switching system with fixed built-in vacuum circuit breakers. The system is suitable for voltages up to 24 kV.
De ringkabelinstallaties worden ook wel RMU (Ring Main Unit) genoemd. De meest voorkomende uitvoering bestaat uit twee of meer kabelvelden met lastscheiders en een met smeltveiligheid of vermogenschakelaar beveiligde aftakking. Deze uitvoering wordt het meest toegepast in compacte transformatorstations en schakelbare knooppunten in MS-distributienetten. In geval van twee kabelvelden en een beveiligd transformatorveld spreekt men van een KKT-installatie (Kabel-Kabel-Transformator). | The ring cable installations are also known as RMU (Ring Main Unit). The most common configuration consists of two or more cable sections with load break switches and a branch protected by a fuse or circuit breaker. This configuration is most commonly used in compact transformer stations and switchable nodes in medium voltage distribution networks. In the case of two cable sections and a protected transformer section, it is referred to as a KKT installation (Cable-Cable-Transformer). | single busbar system. An example is SVS, a metal-enclosed, epoxy resin-insulated switching system with fixed built-in vacuum circuit breakers. The system is suitable for voltages up to 24 kV. Ringkabelinstallaties
Figuur 4.23 SVS | Figure 4.23 SVS | stations and switchable nodes in medium voltage distribution networks. In the case of two cable sections and a protected transformer section, it is referred to as a KKT installation (Cable-Cable-Transformer).
Deze installaties zijn altijd enkelvoudig opgebouwd zonder reserve componenten en worden voornamelijk toegepast in netstations. Een voorbeeld is Xiria, geschikt voor spanningen tot 24 kV. De vacuümvermogenschakelaars, hoofdrails en lastscheiders zijn ondergebracht in een geheel gesloten metalen omhulling. Het systeem is geschikt voor stationsautomatisering (afstandbediening en stroom- en spanningsmeetfuncties). Het systeem is uitgerust met lastscheiders en vermogenschakelaars voor 12kV/20kA en 24kV/16kA. De nominale stroom van de lastscheider bedraagt 630 A. De nominale stroom van de vermogenschakelaar bedraagt 200 of 500 A. | These installations are always built as single units without spare components and are mainly used in substations. An example is Xiria, suitable for voltages up to 24 kV. The vacuum circuit breakers, main busbars, and load break switches are housed in a completely enclosed metal casing. The system is suitable for station automation (remote control and current and voltage measurement functions). The system is equipped with load break switches and circuit breakers for 12kV/20kA and 24kV/16kA. The nominal current of the load break switch is 630 A. The nominal current of the circuit breaker is 200 or 500 A. | nodes in medium voltage distribution networks. In the case of two cable sections and a protected transformer section, it is referred to as a KKT installation (Cable-Cable-Transformer). Figure 4.23 SVS
Een ander voorbeeld is de zeer veel gebruikte Magnefix. Dit zijn ringkabelinstallaties voor toepassing in 10 kV tot 15 kV distributienetten. Door de compacte constructie kan het systeem in zeer kleine ruimtes in netstations, (hoge) gebouwen en voor het aansluiten van windturbines worden toegepast. Het systeem is volledig epoxyharsgeïsoleerd, uitgerust met lastscheiders en smeltveiligheden of vermogenschakelaars voor 12kV/14,4 kA-netten en voor 15kV/20kA-netten. De nominale belastingstroom van de lastscheiders bedraagt 400 of 450 A en van de vermogenschakelaars bedraagt deze 400 A. Standaard worden de lastscheiders handmatig bediend met behulp van éénfasige schakelkappen. | Another example is the widely used Magnefix. These are ring main units for use in 10 kV to 15 kV distribution networks. Due to the compact design, the system can be used in very small spaces in substations, (tall) buildings, and for connecting wind turbines. The system is fully epoxy resin insulated, equipped with load break switches and fuses or circuit breakers for 12kV/14.4 kA networks and for 15kV/20kA networks. The nominal load current of the load break switches is 400 or 450 A, and for the circuit breakers, it is 400 A. Standard load break switches are manually operated using single-phase switch caps. | and circuit breakers for 12kV/20kA and 24kV/16kA. The nominal current of the load break switch is 630 A. The nominal current of the circuit breaker is 200 or 500 A.
Figuur 4.24 Magnefix en Xiria | Figure 4.24 Magnefix and Xiria | of the load break switches is 400 or 450 A, and for the circuit breakers, it is 400 A. Standard load break switches are manually operated using single-phase switch caps.
Het personeel kan deze schakelkappen met een bedieningshandel verwijderen en terugplaatsen. De distributietransformator wordt beveiligd met smeltveiligheden. Het is ook mogelijk deze te beveiligen met een vermogenschakelaar en een elektronisch beveiligingsrelais. Voor de detectie van kortsluitstromen kan het Magnefix-systeem worden uitgerust met magnetische indicators met handmatige reset of met elektronische indicators met automatische reset. Ook kunnen sensoren met indicatie op afstand via GSM-communicatie worden gebruikt. | The staff can remove and replace these switch caps using an operating handle. The distribution transformer is protected with fuses. It is also possible to protect it with a circuit breaker and an electronic protection relay. For the detection of short-circuit currents, the Magnefix system can be equipped with magnetic indicators with manual reset or electronic indicators with automatic reset. Sensors with remote indication via GSM communication can also be used. | is 400 or 450 A, and for the circuit breakers, it is 400 A. Standard load break switches are manually operated using single-phase switch caps. Figure 4.24 Magnefix and Xiria
Vanaf de transformator wordt een LS-verdeelinrichting gevoed, waarop de LS-strengen zijn aangesloten. Figuur 4.26 toont 5 gemonteerde velden in een Alfen compactstation, waarvan op de linker drie velden een kabel is aangesloten. De voeding vanaf de trafo komt binnen op het rek links. Geheel rechts, achter de grijze afdekplaat, kan een zesde worden gemonteerd. Elke kabel en de voeding vanuit de transformator is op de LS-verdeelinrichting beveiligd met smeltveiligheden, die eenvoudig uitgewisseld kunnen worden en tevens als schakelelement fungeren. | From the transformer, a low-voltage distribution unit is powered, to which the low-voltage strings are connected. Figure 4.26 shows 5 mounted fields in an Alfen compact station, with cables connected to the left three fields. The power from the transformer enters on the left rack. On the far right, behind the gray cover plate, a sixth field can be mounted. Each cable and the power supply from the transformer is protected on the low-voltage distribution unit with fuses, which can be easily replaced and also function as switching elements. | currents, the Magnefix system can be equipped with magnetic indicators with manual reset or electronic indicators with automatic reset. Sensors with remote indication via GSM communication can also be used.
4.7 Smeltveiligheden | 4.7 Fuses | mounted. Each cable and the power supply from the transformer is protected on the low-voltage distribution unit with fuses, which can be easily replaced and also function as switching elements.
Zowel in de middenspanning als in de laagspanning worden smeltveiligheden toegepast. Een smeltveiligheid is in feite een bewust aangebrachte zwakke schakel in het netwerk, die bij een overbelasting of bij een kortsluiting als eerste kapot gaat en daarmee de stroom onderbreekt. Het werkingsprincipe berust op het smelten van een dunne smeltgeleider bij een stroom die groter is dan de nominale stroomwaarde. | Both in medium voltage and low voltage, fuses are used. A fuse is essentially a deliberately installed weak link in the network that breaks first in the event of an overload or short circuit, thereby interrupting the current. The operating principle is based on the melting of a thin fuse element when the current exceeds the nominal current value. | cable and the power supply from the transformer is protected on the low-voltage distribution unit with fuses, which can be easily replaced and also function as switching elements. 4.7 Fuses
Figuur 4.25 Netstation met Magnefix | Figure 4.25 Substation with Magnefix | an overload or short circuit, thereby interrupting the current. The operating principle is based on the melting of a thin fuse element when the current exceeds the nominal current value.
Figuur 4.26 LS-verdeelinrichting | Figure 4.26 Low-voltage distribution panel | thereby interrupting the current. The operating principle is based on the melting of a thin fuse element when the current exceeds the nominal current value. Figure 4.25 Substation with Magnefix
De constructie van de smeltgeleider bepaalt of er een trage of snelle onderbreking plaatsvindt. De smelttijd is afhankelijk van de dikte van de draad en van de ontwikkelde warmte in de draad. De smelttijd is evenredig met het kwadraat van de stroomsterkte. Door de grootte van de kortsluitstroom kan het voorkomen dat de smeltveiligheid de kortsluitstroom onderbreekt nog voordat deze zijn maximale waarde bereikt. De grootte van deze stroom wordt aangeduid als de kapstroom. De smelttijden van een smeltpatroon als functie van de stroomsterkte worden door de fabrikant weergegeven in de kenmerkende stroom/tijdkarakteristiek. De werking van de smeltveiligheid wordt nader toegelicht in hoofdstuk 6. | The construction of the fuse element determines whether a slow or fast interruption occurs. The melting time depends on the thickness of the wire and the heat developed in the wire. The melting time is proportional to the square of the current strength. Due to the magnitude of the short-circuit current, it may happen that the fuse interrupts the short-circuit current before it reaches its maximum value. The magnitude of this current is referred to as the cut-off current. The melting times of a fuse element as a function of the current strength are provided by the manufacturer in the characteristic current/time curve. The operation of the fuse is further explained in chapter 6. | operating principle is based on the melting of a thin fuse element when the current exceeds the nominal current value. Figure 4.25 Substation with Magnefix Figure 4.26 Low-voltage distribution panel
Er zijn diverse typen smeltpatronen, afhankelijk van hun toepassing. De type-aanduiding bestaat uit een lettercodering. De eerste letter staat voor het onderbrekingsgebied van de smeltpatronen: | There are various types of fuse elements, depending on their application. The type designation consists of a letter code. The first letter represents the interruption range of the fuse elements: | fuse element as a function of the current strength are provided by the manufacturer in the characteristic current/time curve. The operation of the fuse is further explained in chapter 6.
g: onderbreken in het gehele bereik | g: interrupt in the entire range | There are various types of fuse elements, depending on their application. The type designation consists of a letter code. The first letter represents the interruption range of the fuse elements:
a: onderbreken in een gedeelte van het bereik | a: interrupt in a portion of the range | elements, depending on their application. The type designation consists of a letter code. The first letter represents the interruption range of the fuse elements: g: interrupt in the entire range
De tweede letter staat voor de gebruikscategorie: | The second letter stands for the usage category: | consists of a letter code. The first letter represents the interruption range of the fuse elements: g: interrupt in the entire range a: interrupt in a portion of the range
G: algemene toepassing | G: general application | represents the interruption range of the fuse elements: g: interrupt in the entire range a: interrupt in a portion of the range The second letter stands for the usage category:
M: motorbeveiliging (vroeger back-up beveiliging) | M: motor protection (formerly backup protection) | range of the fuse elements: g: interrupt in the entire range a: interrupt in a portion of the range The second letter stands for the usage category: G: general application
R: halfgeleiderbeveiliging | R: semiconductor protection | interrupt in the entire range a: interrupt in a portion of the range The second letter stands for the usage category: G: general application M: motor protection (formerly backup protection)
Tr: transformatorbeveiliging | Tr: transformer protection | entire range a: interrupt in a portion of the range The second letter stands for the usage category: G: general application M: motor protection (formerly backup protection) R: semiconductor protection
F: snel onderbreken, algemene toepassing | F: fast interrupt, general application | interrupt in a portion of the range The second letter stands for the usage category: G: general application M: motor protection (formerly backup protection) R: semiconductor protection Tr: transformer protection
FF: supersnel onderbreken, algemene toepassing | FF: ultra-fast interrupt, general application | the range The second letter stands for the usage category: G: general application M: motor protection (formerly backup protection) R: semiconductor protection Tr: transformer protection F: fast interrupt, general application
Enkele voorbeelden van bekende toepassingen zijn: | Some examples of well-known applications are: | stands for the usage category: G: general application M: motor protection (formerly backup protection) R: semiconductor protection Tr: transformer protection F: fast interrupt, general application FF: ultra-fast interrupt, general application
gG: onderbreken in het gehele bereik, algemene toepassing: leidingbeveiliging | gG: interrupt across the entire range, general application: line protection | general application M: motor protection (formerly backup protection) R: semiconductor protection Tr: transformer protection F: fast interrupt, general application FF: ultra-fast interrupt, general application Some examples of well-known applications are:
aM: onderbreken in een gedeelte van het bereik: motorbeveiliging | aM: interrupt in a portion of the range: motor protection | protection Tr: transformer protection F: fast interrupt, general application FF: ultra-fast interrupt, general application Some examples of well-known applications are: gG: interrupt across the entire range, general application: line protection
gTr: onderbreken in het gehele bereik: transformatorbeveiliging | gTr: interrupt across the entire range: transformer protection | ultra-fast interrupt, general application Some examples of well-known applications are: gG: interrupt across the entire range, general application: line protection aM: interrupt in a portion of the range: motor protection
gF: onderbreken in het gehele bereik, snel onderbreken: beveiliging van lange leidingen | gF: interrupt across the entire range, fast interrupt: long line protection | applications are: gG: interrupt across the entire range, general application: line protection aM: interrupt in a portion of the range: motor protection gTr: interrupt across the entire range: transformer protection
De smeltgeleider heeft een bepaalde weerstand, waardoor de smeltveiligheid warmte produceert. De geproduceerde warmte van alle smeltveiligheden gezamenlijk kan leiden tot een aanzienlijke temperatuurstijging in een netstation. Om die reden zijn verliesarme typen ontwikkeld. | The fuse element has a certain resistance, which causes the fuse to produce heat. The heat generated by all the fuses together can lead to a significant temperature increase in a substation. For this reason, low-loss types have been developed. | protection aM: interrupt in a portion of the range: motor protection gTr: interrupt across the entire range: transformer protection gF: interrupt across the entire range, fast interrupt: long line protection
De smeltveiligheid omvat alle onderdelen die samen de gehele beveiliging vormen en één van de onderdelen is de smeltpatroon. Een smeltpatroon is in diverse uitvoeringsvormen verkrijgbaar. Een veel toegepast type is de mespatroon, die bestaat uit een keramisch lichaam, metalen sluitplaten, contactmessen en een melder. | The fuse safety encompasses all components that together form the entire protection, and one of the components is the fuse link. A fuse link is available in various designs. A commonly used type is the blade fuse, which consists of a ceramic body, metal end caps, contact blades, and an indicator. | fuse to produce heat. The heat generated by all the fuses together can lead to a significant temperature increase in a substation. For this reason, low-loss types have been developed.
Figuur 4.27 Een serie gG mespatronen voor laagspanning | Figure 4.27 A series of gG blade fuses for low voltage | A fuse link is available in various designs. A commonly used type is the blade fuse, which consists of a ceramic body, metal end caps, contact blades, and an indicator.
4.8 I | 4.8 A | type is the blade fuse, which consists of a ceramic body, metal end caps, contact blades, and an indicator. Figure 4.27 A series of gG blade fuses for low voltage
s | s | the blade fuse, which consists of a ceramic body, metal end caps, contact blades, and an indicator. Figure 4.27 A series of gG blade fuses for low voltage 4.8 A
-begrenzers | -limiters | blade fuse, which consists of a ceramic body, metal end caps, contact blades, and an indicator. Figure 4.27 A series of gG blade fuses for low voltage 4.8 A s
Net als de smeltveiligheid onderbreekt een I | Just like the fuse, a I | fuse, which consists of a ceramic body, metal end caps, contact blades, and an indicator. Figure 4.27 A series of gG blade fuses for low voltage 4.8 A s -limiters
s | s | body, metal end caps, contact blades, and an indicator. Figure 4.27 A series of gG blade fuses for low voltage 4.8 A s -limiters Just like the fuse, a I
-begrenzer de kortsluitstroom voordat deze zijn verwachte maximale waarde bereikt. In dit geval is er dus ook sprake van een kortsluitstroombegrenzing. Een I | -limiter restricts the short-circuit current before it reaches its expected maximum value. In this case, there is also a short-circuit current limitation. An I | metal end caps, contact blades, and an indicator. Figure 4.27 A series of gG blade fuses for low voltage 4.8 A s -limiters Just like the fuse, a I s
s | s | like the fuse, a I s -limiter restricts the short-circuit current before it reaches its expected maximum value. In this case, there is also a short-circuit current limitation. An I
-begrenzer bestaat uit een smeltveiligheid parallel aan een primair circuit. Het primaire circuit heeft een grote nominale stroomsterkte en heeft een klein afschakelvermogen. De smeltveiligheid heeft een groot afschakelvermogen. Een snelle onderbreking wordt gewaarborgd doordat de I | -limiter consists of a fuse in parallel with a primary circuit. The primary circuit has a high nominal current and a low breaking capacity. The fuse has a high breaking capacity. A quick interruption is ensured because the I | the fuse, a I s -limiter restricts the short-circuit current before it reaches its expected maximum value. In this case, there is also a short-circuit current limitation. An I s
s | s | primary circuit. The primary circuit has a high nominal current and a low breaking capacity. The fuse has a high breaking capacity. A quick interruption is ensured because the I
-begrenzer reageert op een sterke stijging van de stroom (grote di/dt). Een ingebouwd meetcircuit bepaalt de stroomwaarde en de di/dt-waarde. Het primaire circuit van de I | -limiter responds to a sharp increase in current (high di/dt). An integrated measuring circuit determines the current value and the di/dt value. The primary circuit of the I | circuit. The primary circuit has a high nominal current and a low breaking capacity. The fuse has a high breaking capacity. A quick interruption is ensured because the I s
s | s | I s -limiter responds to a sharp increase in current (high di/dt). An integrated measuring circuit determines the current value and the di/dt value. The primary circuit of the I
-begrenzer is uitgerust met een springstoflading. Wanneer de vooraf ingestelde grenswaarden van de stroom en de di/dt worden overschreden zal de springstoflading het primaire circuit onderbreken. Daarna zal de smeltveiligheid de kortsluitstroom begrenzen en binnen 0,5 ms onderbreken bij de eerstvolgende nuldoorgang van de spanning. | -limiter is equipped with an explosive charge. When the preset threshold values of the current and the di/dt are exceeded, the explosive charge will interrupt the primary circuit. Subsequently, the fuse will limit the short-circuit current and interrupt it within 0.5 ms at the next zero crossing of the voltage. | s -limiter responds to a sharp increase in current (high di/dt). An integrated measuring circuit determines the current value and the di/dt value. The primary circuit of the I s
Figuur 4.28 I | Figure 4.28 I | the explosive charge will interrupt the primary circuit. Subsequently, the fuse will limit the short-circuit current and interrupt it within 0.5 ms at the next zero crossing of the voltage.
s | s | will interrupt the primary circuit. Subsequently, the fuse will limit the short-circuit current and interrupt it within 0.5 ms at the next zero crossing of the voltage. Figure 4.28 I
-begrenzer met springstoflading | -limiter with explosive charge | interrupt the primary circuit. Subsequently, the fuse will limit the short-circuit current and interrupt it within 0.5 ms at the next zero crossing of the voltage. Figure 4.28 I s
De I | The I | Subsequently, the fuse will limit the short-circuit current and interrupt it within 0.5 ms at the next zero crossing of the voltage. Figure 4.28 I s -limiter with explosive charge
s | s | fuse will limit the short-circuit current and interrupt it within 0.5 ms at the next zero crossing of the voltage. Figure 4.28 I s -limiter with explosive charge The I
-begrenzers worden toegepast in situaties waarin het kortsluitvermogen zodanig hoog is geworden dat de componenten niet meer kortsluitvast zijn. Voorbeelden zijn: | -limiters are used in situations where the short-circuit power has become so high that the components are no longer short-circuit proof. Examples include: | will limit the short-circuit current and interrupt it within 0.5 ms at the next zero crossing of the voltage. Figure 4.28 I s -limiter with explosive charge The I s
parallelschakeling van transformatoren: de rails aan secundaire zijden zijn verbonden met een I | parallel connection of transformers: the busbars on the secondary sides are connected with an I | -limiter with explosive charge The I s -limiters are used in situations where the short-circuit power has become so high that the components are no longer short-circuit proof. Examples include:
s | s | power has become so high that the components are no longer short-circuit proof. Examples include: parallel connection of transformers: the busbars on the secondary sides are connected with an I
-begrenzer; bij een kortsluiting in een streng zal de I | -limiter; in the event of a short circuit in a string the I | has become so high that the components are no longer short-circuit proof. Examples include: parallel connection of transformers: the busbars on the secondary sides are connected with an I s
s | s | include: parallel connection of transformers: the busbars on the secondary sides are connected with an I s -limiter; in the event of a short circuit in a string the I
-begrenzer afschakelen, waardoor de kortsluiting nog maar door één transformator wordt gevoed | -disconnect the I s -limiter, causing the short circuit to be fed by only one transformer | parallel connection of transformers: the busbars on the secondary sides are connected with an I s -limiter; in the event of a short circuit in a string the I s
parallelschakeling van een smoorspoel en een I | parallel connection of a choke coil and an I | -limiter; in the event of a short circuit in a string the I s -disconnect the I s -limiter, causing the short circuit to be fed by only one transformer
s | s | a string the I s -disconnect the I s -limiter, causing the short circuit to be fed by only one transformer parallel connection of a choke coil and an I
-begrenzer: bij normaal bedrijf worden de verliezen en de spanningsval over de smoorspoel voorkomen; nadat de I | -limiter: under normal operation, the losses and the voltage drop across the choke coil are prevented; after the I | string the I s -disconnect the I s -limiter, causing the short circuit to be fed by only one transformer parallel connection of a choke coil and an I s
s | s | transformer parallel connection of a choke coil and an I s -limiter: under normal operation, the losses and the voltage drop across the choke coil are prevented; after the I
-begrenzer heeft afgeschakeld wordt de kortsluitstroom begrensd door de smoorspoel | -limiter has tripped, the short-circuit current is limited by the choke coil | parallel connection of a choke coil and an I s -limiter: under normal operation, the losses and the voltage drop across the choke coil are prevented; after the I s
als beveiliging van zelfopwekkers. | as protection for self-generators. | normal operation, the losses and the voltage drop across the choke coil are prevented; after the I s -limiter has tripped, the short-circuit current is limited by the choke coil
4.9 Toepassing van vermogenselektronica | 4.9 Application of Power Electronics | and the voltage drop across the choke coil are prevented; after the I s -limiter has tripped, the short-circuit current is limited by the choke coil as protection for self-generators.
Vermogenselektronica wordt al veel toegepast in de HS-netten en in regelbare aandrijvingen op LS-niveau. In HS-netten vindt toepassing plaats in de HVDC (High Voltage DC) en in FACTS. Dit laatste is de afkorting voor ‘Flexible AC Transmission System’ en is de verzamelnaam voor vermogenselektronische apparaten die de bestuurbaarheid en de transmissiecapaciteit van elektriciteitsnetwerken vergroten. Voorbeelden van toepassingen in hoogspanningsnetwerken zijn: | Power electronics are already widely used in high-voltage (HV) networks and in adjustable drives at the low-voltage (LV) level. In HV networks, applications are found in HVDC (High Voltage DC) and in FACTS. The latter stands for 'Flexible AC Transmission System' and is the collective term for power electronic devices that enhance the controllability and transmission capacity of electrical networks. Examples of applications in high-voltage networks include: | the choke coil are prevented; after the I s -limiter has tripped, the short-circuit current is limited by the choke coil as protection for self-generators. 4.9 Application of Power Electronics
seriecompensatie: static synchronous series compensator (SSSC) en | series compensation: static synchronous series compensator (SSSC) and | 'Flexible AC Transmission System' and is the collective term for power electronic devices that enhance the controllability and transmission capacity of electrical networks. Examples of applications in high-voltage networks include:
parallelcompensatie: static synchronous compensator (STATCOM) en static var compensator (SVC). | parallel compensation: static synchronous compensator (STATCOM) and static var compensator (SVC). | term for power electronic devices that enhance the controllability and transmission capacity of electrical networks. Examples of applications in high-voltage networks include: series compensation: static synchronous series compensator (SSSC) and
Bij seriecompensatie is het apparaat in serie in een doorgaande verbinding geplaatst. Het apparaat is een variabele spanningsbron. In lange transmissielijnen is de inductie groot. Het apparaat brengt een spanning aan met een zodanige grootte en hoek, dat een compenserende seriecondensator wordt benaderd. Als gevolg vermindert de grootte van de reactantie van de verbinding. | In series compensation, the device is placed in series within a continuous connection. The device is a variable voltage source. In long transmission lines, the inductance is high. The device applies a voltage with such magnitude and angle that it approximates a compensating series capacitor. As a result, the magnitude of the reactance of the connection is reduced. | capacity of electrical networks. Examples of applications in high-voltage networks include: series compensation: static synchronous series compensator (SSSC) and parallel compensation: static synchronous compensator (STATCOM) and static var compensator (SVC).
Bij parallelcompensatie werkt het apparaat als een variabele stroombron. De apparaten kunnen reactief vermogen opnemen (inductief) en afgeven (capacitief). De capacitieve compensator wordt gebruikt om de arbeidsfactor te verbeteren. Door parallel aan een inductieve belasting extra blindvermogen op te wekken, verbetert de cos(φ) van het geheel. Een SVC is een thyristorgeschakelde shuntspoel of shuntcondensator. De regeling van de thyristoren bepaalt de grootte van de reactantie. Standaardsystemen voor SVC’s zijn verkrijgbaar in vermogens van 25, 35 en 50 Mvar bij spanningen tot 36 kV. | In parallel compensation, the device functions as a variable current source. The devices can absorb reactive power (inductive) and supply reactive power (capacitive). The capacitive compensator is used to improve the power factor. By generating additional reactive power in parallel with an inductive load, the overall cos(φ) is improved. An SVC is a thyristor-switched shunt reactor or shunt capacitor. The control of the thyristors determines the magnitude of the reactance. Standard systems for SVCs are available in capacities of 25, 35, and 50 Mvar at voltages up to 36 kV. | The device applies a voltage with such magnitude and angle that it approximates a compensating series capacitor. As a result, the magnitude of the reactance of the connection is reduced.
Een STATCOM is een elektronisch equivalent van een roterende synchrone compensator. De uitwisseling van reactief vermogen tussen het apparaat en het wisselspanningsnet wordt geregeld door de spanning van de STATCOM te variëren. | A STATCOM is an electronic equivalent of a rotating synchronous compensator. The exchange of reactive power between the device and the AC power grid is controlled by varying the voltage of the STATCOM. | control of the thyristors determines the magnitude of the reactance. Standard systems for SVCs are available in capacities of 25, 35, and 50 Mvar at voltages up to 36 kV.
Oorspronkelijk werd deze apparatuur uitsluitend gebruikt in hoogspanningssystemen. Met de introductie van een nieuwe generatie van vermogenselektronische componenten, zoals IGBT’s, GTO’s en IGCT’s, werden onder andere Voltage Source Converters (VSC) geïmplementeerd in de elektrische netwerken. De hierbij gebruikte techniek maakt gebruik van pulsbreedtemodulatie. | Originally, this equipment was exclusively used in high-voltage systems. With the introduction of a new generation of power electronic components, such as IGBTs, GTOs, and IGCTs, Voltage Source Converters (VSC) were implemented in electrical networks. The technique used here employs pulse-width modulation. | an electronic equivalent of a rotating synchronous compensator. The exchange of reactive power between the device and the AC power grid is controlled by varying the voltage of the STATCOM.
Veelgebruikt zijn de converters die ingezet worden als motor drives. Nieuwer is de toepassing van back-to-back converters, die eigenlijk bestaan uit twee STATCOM’s die aan de gelijkspanningszijde met elkaar verbonden zijn. Met deze converter kunnen actief vermogen en blindvermogen afzonderlijk van elkaar geregeld worden. Een voorstel voor toepassing van back-to-back converters in het intelligente knooppunt is in diverse onderzoeken besproken (Provoost, 2009)(De Graaff, 2010). Deze toepassing wordt in het hoofdstuk over Intelligente Netten kort toegelicht. | Converters commonly used as motor drives are widely utilized. Newer is the application of back-to-back converters, which essentially consist of two STATCOMs connected on the DC side. With this converter, active power and reactive power can be controlled independently of each other. A proposal for the application of back-to-back converters in the intelligent node has been discussed in various studies (Provoost, 2009)(De Graaff, 2010). This application is briefly explained in the chapter on Intelligent Grids. | of a new generation of power electronic components, such as IGBTs, GTOs, and IGCTs, Voltage Source Converters (VSC) were implemented in electrical networks. The technique used here employs pulse-width modulation.
Langzamerhand vinden deze technieken hun toepassingen ook in de distributienetwerken, met als doel de kwaliteit van de spanning te verbeteren en koppelingen van netten met gecontroleerde uitwisseling van vermogen mogelijk te maken. Als toepassingen voor distributiesystemen worden concreet genoemd (Cigré, 2005): | Gradually, these techniques are also finding their applications in distribution networks, with the aim of improving voltage quality and enabling network connections with controlled power exchange. Specific applications for distribution systems mentioned include (Cigré, 2005): | the application of back-to-back converters in the intelligent node has been discussed in various studies (Provoost, 2009)(De Graaff, 2010). This application is briefly explained in the chapter on Intelligent Grids.
solid state switchgear equipment: vermogenselektronische schakelaar die kortsluitstromen beperkt en daarmee spanningsdips in ongestoorde netdelen beperkt; kortsluitingen kunnen snel worden afgeschakeld en elektriciteitsvoorziening kan snel worden hersteld; | solid state switchgear equipment: power electronic switch that limits short-circuit currents and thereby reduces voltage dips in undisturbed network sections; short circuits can be quickly disconnected and power supply can be rapidly restored; | finding their applications in distribution networks, with the aim of improving voltage quality and enabling network connections with controlled power exchange. Specific applications for distribution systems mentioned include (Cigré, 2005):
parallelcompensatie met behulp van SVC en STATCOM: met name interessant voor bovengrondse distributienetten; | parallel compensation using SVC and STATCOM: particularly interesting for overhead distribution networks; | equipment: power electronic switch that limits short-circuit currents and thereby reduces voltage dips in undisturbed network sections; short circuits can be quickly disconnected and power supply can be rapidly restored;
dynamic voltage restorer: apparaat om snelle en langzame spanningsveranderingen te compenseren via een in serie met de betreffende verbinding geschakelde transformator; | dynamic voltage restorer: device to compensate for rapid and slow voltage changes via a transformer connected in series with the respective connection; | dips in undisturbed network sections; short circuits can be quickly disconnected and power supply can be rapidly restored; parallel compensation using SVC and STATCOM: particularly interesting for overhead distribution networks;
solid state on-load tap changer: deze techniek is toegepast in regelbare MS/LS transformatoren, waarbij met behulp van thyristoren of IGBT’s de juiste aftakkingen van de primaire wikkeling van een transformator gekozen worden. | solid state on-load tap changer: this technique is applied in adjustable medium voltage/low voltage transformers, where the correct taps of the primary winding of a transformer are selected using thyristors or IGBTs. | and STATCOM: particularly interesting for overhead distribution networks; dynamic voltage restorer: device to compensate for rapid and slow voltage changes via a transformer connected in series with the respective connection;