## Sheet1
Original Text | Translated Text | Previous Context
Netten | Netten
Hoofdstuk 2 behandelt de netten en hun structuren. Eerst komen de verschillen tussen transport en distributie aan de orde. Ook de stations worden in dit hoofdstuk besproken. De structuren van de meeste in Nederland toegepaste midden- en laagspanningsnetten worden toegelicht. Het hoofdstuk besluit met de beschrijving van de aansluitingen voor de diverse aansluitcategorieën. | Chapter 2 covers the networks and their structures. First, the differences between transmission and distribution are addressed. The stations are also discussed in this chapter. The structures of most medium and low voltage networks used in the Netherlands are explained. The chapter concludes with a description of the connections for the various connection categories. | Netten
2 Netten | 2 Networks | chapter. The structures of most medium and low voltage networks used in the Netherlands are explained. The chapter concludes with a description of the connections for the various connection categories.
2.1 Functies van het elektriciteitsnet | 2.1 Functions of the electricity grid | structures of most medium and low voltage networks used in the Netherlands are explained. The chapter concludes with a description of the connections for the various connection categories. 2 Networks
2.2 Spanningsniveaus in het elektriciteitsnet | 2.2 Voltage Levels in the Electricity Grid | voltage networks used in the Netherlands are explained. The chapter concludes with a description of the connections for the various connection categories. 2 Networks 2.1 Functions of the electricity grid
2.3 Kwaliteit en beschikbaarheid | 2.3 Quality and availability | explained. The chapter concludes with a description of the connections for the various connection categories. 2 Networks 2.1 Functions of the electricity grid 2.2 Voltage Levels in the Electricity Grid
2.3.1 Transportnet | 2.3.1 Transmission Network | with a description of the connections for the various connection categories. 2 Networks 2.1 Functions of the electricity grid 2.2 Voltage Levels in the Electricity Grid 2.3 Quality and availability
2.3.2 Distributienet | 2.3.2 Distribution Network | of the connections for the various connection categories. 2 Networks 2.1 Functions of the electricity grid 2.2 Voltage Levels in the Electricity Grid 2.3 Quality and availability 2.3.1 Transmission Network
2.4 Netstructuren | 2.4 Network Structures | for the various connection categories. 2 Networks 2.1 Functions of the electricity grid 2.2 Voltage Levels in the Electricity Grid 2.3 Quality and availability 2.3.1 Transmission Network 2.3.2 Distribution Network
2.4.1 Structuur van transportnetten | 2.4.1 Structure of Transmission Networks | connection categories. 2 Networks 2.1 Functions of the electricity grid 2.2 Voltage Levels in the Electricity Grid 2.3 Quality and availability 2.3.1 Transmission Network 2.3.2 Distribution Network 2.4 Network Structures
2.4.2 Structuur van middenspanningsdistributienetten | 2.4.2 Structure of Medium Voltage Distribution Networks | Functions of the electricity grid 2.2 Voltage Levels in the Electricity Grid 2.3 Quality and availability 2.3.1 Transmission Network 2.3.2 Distribution Network 2.4 Network Structures 2.4.1 Structure of Transmission Networks
2.4.3 Onderzoek naar nieuwe netstructuren | 2.4.3 Research into New Network Structures | Levels in the Electricity Grid 2.3 Quality and availability 2.3.1 Transmission Network 2.3.2 Distribution Network 2.4 Network Structures 2.4.1 Structure of Transmission Networks 2.4.2 Structure of Medium Voltage Distribution Networks
2.4.4 Structuur van laagspanningsdistributienetten | 2.4.4 Structure of Low Voltage Distribution Networks | Quality and availability 2.3.1 Transmission Network 2.3.2 Distribution Network 2.4 Network Structures 2.4.1 Structure of Transmission Networks 2.4.2 Structure of Medium Voltage Distribution Networks 2.4.3 Research into New Network Structures
2.4.5 Stations | 2.4.5 Stations | Distribution Network 2.4 Network Structures 2.4.1 Structure of Transmission Networks 2.4.2 Structure of Medium Voltage Distribution Networks 2.4.3 Research into New Network Structures 2.4.4 Structure of Low Voltage Distribution Networks
2.4.6 Onderstation (OS) | 2.4.6 Substation (SS) | 2.4 Network Structures 2.4.1 Structure of Transmission Networks 2.4.2 Structure of Medium Voltage Distribution Networks 2.4.3 Research into New Network Structures 2.4.4 Structure of Low Voltage Distribution Networks 2.4.5 Stations
2.4.7 Schakelstation (SS) | 2.4.7 Switching Station (SS) | 2.4.1 Structure of Transmission Networks 2.4.2 Structure of Medium Voltage Distribution Networks 2.4.3 Research into New Network Structures 2.4.4 Structure of Low Voltage Distribution Networks 2.4.5 Stations 2.4.6 Substation (SS)
2.4.8 Regelstation (RS) | 2.4.8 Control Station (RS) | Networks 2.4.2 Structure of Medium Voltage Distribution Networks 2.4.3 Research into New Network Structures 2.4.4 Structure of Low Voltage Distribution Networks 2.4.5 Stations 2.4.6 Substation (SS) 2.4.7 Switching Station (SS)
2.4.9 Netstation | 2.4.9 Network Station | Medium Voltage Distribution Networks 2.4.3 Research into New Network Structures 2.4.4 Structure of Low Voltage Distribution Networks 2.4.5 Stations 2.4.6 Substation (SS) 2.4.7 Switching Station (SS) 2.4.8 Control Station (RS)
2.5 Aansluitingen, gebaseerd op aansluitcategorieën | 2.5 Connections, based on connection categories | Networks 2.4.3 Research into New Network Structures 2.4.4 Structure of Low Voltage Distribution Networks 2.4.5 Stations 2.4.6 Substation (SS) 2.4.7 Switching Station (SS) 2.4.8 Control Station (RS) 2.4.9 Network Station
2.5.1 Gewenste aansluitcapaciteit tot en met 1 x 6A op een geschakeld net (A.1) | 2.5.1 Desired connection capacity up to and including 1 x 6A on a switched network (A.1) | Structures 2.4.4 Structure of Low Voltage Distribution Networks 2.4.5 Stations 2.4.6 Substation (SS) 2.4.7 Switching Station (SS) 2.4.8 Control Station (RS) 2.4.9 Network Station 2.5 Connections, based on connection categories
2.5.2 Gewenste aansluitcapaciteit van 3 x 25A tot en met 60 kVA (A.2) | 2.5.2 Desired connection capacity from 3 x 25A up to and including 60 kVA (A.2) | (SS) 2.4.8 Control Station (RS) 2.4.9 Network Station 2.5 Connections, based on connection categories 2.5.1 Desired connection capacity up to and including 1 x 6A on a switched network (A.1)
2.5.3 Gewenste aansluitcapaciteit van 60 kVA tot en met 300 kVA (A.3) | 2.5.3 Desired connection capacity from 60 kVA up to and including 300 kVA (A.3) | Desired connection capacity up to and including 1 x 6A on a switched network (A.1) 2.5.2 Desired connection capacity from 3 x 25A up to and including 60 kVA (A.2)
2.5.4 Gewenste aansluitcapaciteit van 0,3 MVA tot en met 3 MVA met zuivere MS-aansluiting (A.4) | 2.5.4 Desired connection capacity from 0.3 MVA up to and including 3 MVA with pure MV connection (A.4) | (A.1) 2.5.2 Desired connection capacity from 3 x 25A up to and including 60 kVA (A.2) 2.5.3 Desired connection capacity from 60 kVA up to and including 300 kVA (A.3)
2.5.5 Gewenste aansluitcapaciteit van 0,3 MVA tot en met 3 MVA met fysieke levering van LS (A.5) | 2.5.5 Desired connection capacity from 0.3 MVA up to and including 3 MVA with physical delivery of LV (A.5) | connection capacity from 60 kVA up to and including 300 kVA (A.3) 2.5.4 Desired connection capacity from 0.3 MVA up to and including 3 MVA with pure MV connection (A.4)
2.5.6 Gewenste aansluitcapaciteit van 3 MVA tot en met 10 MVA (A.6) | 2.5.6 Desired connection capacity from 3 MVA up to and including 10 MVA (A.6) | up to and including 3 MVA with pure MV connection (A.4) 2.5.5 Desired connection capacity from 0.3 MVA up to and including 3 MVA with physical delivery of LV (A.5)
2.5.7 Gewenste aansluitcapaciteit meer dan 10 MVA (A.7) | 2.5.7 Desired connection capacity more than 10 MVA (A.7) | capacity from 0.3 MVA up to and including 3 MVA with physical delivery of LV (A.5) 2.5.6 Desired connection capacity from 3 MVA up to and including 10 MVA (A.6)
2.6 Keuzes bij het ontwerpen van een net | 2.6 Choices in designing a network | MVA with physical delivery of LV (A.5) 2.5.6 Desired connection capacity from 3 MVA up to and including 10 MVA (A.6) 2.5.7 Desired connection capacity more than 10 MVA (A.7)
2 Netten | 2 Networks | (A.5) 2.5.6 Desired connection capacity from 3 MVA up to and including 10 MVA (A.6) 2.5.7 Desired connection capacity more than 10 MVA (A.7) 2.6 Choices in designing a network
Het doel van een elektriciteitsnet is elektrisch vermogen te transporteren van de locaties waar het wordt opgewekt naar de locaties waar het wordt gebruikt. Dit doel wordt verwezenlijkt op maatschappelijk verantwoorde wijze, met de gewenste kwaliteit en tegen zo laag mogelijke kosten. Naast de kwaliteit wordt de leveringszekerheid als zeer belangrijk ervaren, vanwege het grote maatschappelijke belang van de elektriciteitsvoorziening. Door de goede reputatie van de elektriciteitsbedrijven gaat men ervan uit dat de leveringszekerheid voldoende is. Absolute leveringszekerheid is echter niet mogelijk, want componenten kunnen altijd gestoord raken, hetzij door een eigen defect, hetzij door een externe oorzaak. Een mogelijkheid om storingen te beheersen is het inbouwen van voldoende reserve. Omdat dit gepaard gaat met extra kosten, zal er altijd een afweging gemaakt worden tussen de kosten en de baten van de leveringszekerheid. Bij een optimale leveringszekerheid wordt niet gestreefd naar minimaliseren van risico en gevolgen maar naar het verkrijgen van een aanvaardbaar niveau. Samenvattend zijn de belangrijkste eisen voor elektriciteitsnetten (Kundur, 1994): | The purpose of an electricity grid is to transport electrical power from the locations where it is generated to the locations where it is used. This goal is achieved in a socially responsible manner, with the desired quality and at the lowest possible costs. In addition to quality, supply reliability is considered very important due to the significant societal importance of electricity supply. Due to the good reputation of electricity companies, it is assumed that supply reliability is sufficient. However, absolute supply reliability is not possible, as components can always be disrupted, either by their own defect or by an external cause. One way to manage disruptions is to build in sufficient reserve. Since this involves additional costs, there will always be a trade-off between the costs and benefits of supply reliability. Optimal supply reliability does not aim to minimize risk and consequences but to achieve an acceptable level. In summary, the main requirements for electricity grids are (Kundur, 1994): | Desired connection capacity from 3 MVA up to and including 10 MVA (A.6) 2.5.7 Desired connection capacity more than 10 MVA (A.7) 2.6 Choices in designing a network 2 Networks
het systeem moet de continu veranderende vraag van alle belastingen en het aanbod van alle opwekkers kunnen verwerken, zonder dat apparatuur en verbindingen overbelast raken, | the system must be able to handle the continuously changing demand from all loads and the supply from all generators without overloading equipment and connections, | supply reliability. Optimal supply reliability does not aim to minimize risk and consequences but to achieve an acceptable level. In summary, the main requirements for electricity grids are (Kundur, 1994):
het systeem moet vermogen leveren bij zo laag mogelijke kosten en met minimale milieubelasting, | the system must deliver power at the lowest possible cost and with minimal environmental impact, | electricity grids are (Kundur, 1994): the system must be able to handle the continuously changing demand from all loads and the supply from all generators without overloading equipment and connections,
de kwaliteit van de levering moet voldoen aan minimale systeemeisen betreffende frequentie, spanning en betrouwbaarheid. | the quality of the delivery must meet minimum system requirements regarding frequency, voltage, and reliability. | demand from all loads and the supply from all generators without overloading equipment and connections, the system must deliver power at the lowest possible cost and with minimal environmental impact,
Het begrip ‘net’ is in de Elektriciteitswet 1998 gedefinieerd in artikel 1, sub i. Het komt erop neer dat een elektriciteitsnet het geheel van bedrijfsmiddelen (‘verbindingen en hulpmiddelen’) is, waarmee alle producenten en verbruikers van elektrische energie zijn verbonden en waarmee de elektrische energie wordt getransporteerd. De definitie sluit verbindingen en hulpmiddelen uit die binnen de installatie van een producent of van een afnemer liggen. Om het verschil met particuliere netten aan te duiden, wordt bij het begrip ‘net’ ook wel gesproken over een ‘openbaar net’. | The term 'grid' is defined in the Electricity Act 1998 in Article 1, subsection i. It essentially means that an electricity grid is the entirety of operational resources ('connections and tools') through which all producers and consumers of electrical energy are connected and through which electrical energy is transported. The definition excludes connections and tools that lie within the installation of a producer or a consumer. To distinguish it from private grids, the term 'grid' is also referred to as a 'public grid'. | the system must deliver power at the lowest possible cost and with minimal environmental impact, the quality of the delivery must meet minimum system requirements regarding frequency, voltage, and reliability.
De bedrijfsmiddelen zijn de primaire componenten, die gebruikt worden in het primaire proces van de elektriciteitsvoorziening. Daarnaast bestaan de secundaire systemen en componenten, die het primaire proces ondersteunen. Een voorbeeld van een secundair systeem is het beveiligingssysteem (besproken in hoofdstuk 6). De primaire componenten van de technische infrastructuur hebben een lange levensduur van 20 tot 40 jaar of langer. De investeringen in de infrastructuur zijn hoog, zodat er relatief weinig wijzigingen plaatsvinden. Een nieuw elektriciteitsnet wordt meestal geprojecteerd voor een lange termijn. | The assets are the primary components used in the primary process of electricity supply. Additionally, there are secondary systems and components that support the primary process. An example of a secondary system is the security system (discussed in chapter 6). The primary components of the technical infrastructure have a long lifespan of 20 to 40 years or longer. Investments in the infrastructure are high, so relatively few changes occur. A new electricity grid is usually planned for the long term. | and tools that lie within the installation of a producer or a consumer. To distinguish it from private grids, the term 'grid' is also referred to as a 'public grid'.
2.1 Functies van het elektriciteitsnet | 2.1 Functions of the electricity grid | lifespan of 20 to 40 years or longer. Investments in the infrastructure are high, so relatively few changes occur. A new electricity grid is usually planned for the long term.
Het elektriciteitsnet verzorgt het transport van elektrische energie vanaf internationaal niveau tot aan het lokale niveau bij de individuele aangeslotenen (de zogenaamde kleinverbruikers). Om dit mogelijk te maken zijn alle elektriciteitsnetten op lokaal, regionaal en landelijk niveau met elkaar verbonden tot een gekoppeld elektriciteitsvoorzieningsysteem. In dit systeem wordt onderscheid gemaakt tussen de transportfunctie en de distributiefunctie. Het transportnet verzorgt op landelijk niveau de vermogenstransporten. Ook de verbindingen met de netten van de omringende landen behoren tot het transportnet. De elektriciteitscentrales en de voedingspunten van de distributienetten zijn op het transportnet aangesloten. In de Elektriciteitswet 1998 wordt het transportnet in artikel 10 beschreven als het ‘landelijk hoogspanningsnet’. Een distributienet verdeelt de elektrische energie binnen een regio over alle aangeslotenen. De distributienetten zijn meer vertakt dan de transportnetten en kunnen worden gezien als de ‘haarvaten’ van het elektriciteitsvoorzieningsysteem. In de praktijk worden de transport- en distributiefunctie nader onderverdeeld. Er wordt gesproken over het koppelnet, het transportnet en het distributienet op regionaal en op lokaal niveau. Dit is schematisch weergegeven in figuur 2.1. | The electricity grid facilitates the transport of electrical energy from the international level down to the local level for individual consumers (the so-called small users). To make this possible, all electricity grids at local, regional, and national levels are interconnected into a unified electricity supply system. In this system, a distinction is made between the transport function and the distribution function. The transport grid handles power transmissions at the national level. Connections with the grids of neighboring countries are also part of the transport grid. Power plants and the feed-in points of the distribution networks are connected to the transport grid. In the Electricity Act of 1998, the transport grid is described in Article 10 as the 'national high-voltage grid.' A distribution network distributes electrical energy within a region to all connected users. Distribution networks are more branched than transport grids and can be seen as the 'capillaries' of the electricity supply system. In practice, the transport and distribution functions are further subdivided. There is talk of the coupling grid, the transport grid, and the distribution grid at regional and local levels. This is schematically represented in Figure 2.1. | or longer. Investments in the infrastructure are high, so relatively few changes occur. A new electricity grid is usually planned for the long term. 2.1 Functions of the electricity grid
Het | Het | functions are further subdivided. There is talk of the coupling grid, the transport grid, and the distribution grid at regional and local levels. This is schematically represented in Figure 2.1.
koppelnet | koppelnet | are further subdivided. There is talk of the coupling grid, the transport grid, and the distribution grid at regional and local levels. This is schematically represented in Figure 2.1. Het
(ook wel hoofdtransportnet of transmissienet genoemd) verzorgt op internationaal niveau de koppelingen met het buitenland en verzorgt op nationaal niveau het transport van door grote centrales (vanaf 500 MVA) geproduceerde elektrische energie. Het koppelnet voedt de transportnetten. Het koppelnet is in figuur 2.1 afgebeeld met de binnenste ring. | (also known as the main transmission grid or transmission network) handles international connections with foreign countries and, on a national level, manages the transport of electrical energy produced by large power plants (starting from 500 MVA). The coupling grid feeds the transport grids. The coupling grid is depicted in Figure 2.1 with the inner ring. | further subdivided. There is talk of the coupling grid, the transport grid, and the distribution grid at regional and local levels. This is schematically represented in Figure 2.1. Het koppelnet
Het | Het | electrical energy produced by large power plants (starting from 500 MVA). The coupling grid feeds the transport grids. The coupling grid is depicted in Figure 2.1 with the inner ring.
transportnet | transportnet | energy produced by large power plants (starting from 500 MVA). The coupling grid feeds the transport grids. The coupling grid is depicted in Figure 2.1 with the inner ring. Het
(ook wel sub-transportnet genoemd) is de schakel tussen het koppelnet en de distributienetten. Een transportnet verzorgt de elektriciteitsvoorziening op provinciaal niveau. Elektriciteitscentrales (van 10 tot 500 MVA), windparken en industriële aangeslotenen met vermogens boven ongeveer 10 MVA zijn op de transportnetten aangesloten. De industriële aangeslotenen kunnen ook beschikken over eigen elektriciteitscentrales. De transportnetten zijn in figuur 2.1 afgebeeld met de tweede ring van binnenuit. | (also known as sub-transmission grid) is the link between the coupling grid and the distribution grids. A transmission grid provides electricity supply at the provincial level. Power plants (from 10 to 500 MVA), wind farms, and industrial consumers with capacities above approximately 10 MVA are connected to the transmission grids. The industrial consumers may also have their own power plants. The transmission grids are depicted in Figure 2.1 with the second ring from the inside. | produced by large power plants (starting from 500 MVA). The coupling grid feeds the transport grids. The coupling grid is depicted in Figure 2.1 with the inner ring. Het transportnet
De | De | connected to the transmission grids. The industrial consumers may also have their own power plants. The transmission grids are depicted in Figure 2.1 with the second ring from the inside.
regionale distributienetten | regional distribution networks | to the transmission grids. The industrial consumers may also have their own power plants. The transmission grids are depicted in Figure 2.1 with the second ring from the inside. De
zijn in figuur 2.1 afgebeeld met de derde ring. Deze netten worden gevoed vanuit de transportnetten. Op deze netten zijn ook grote decentrale opwekkers (warmtekrachtcentrales en windturbines) en grote industriële klanten met vermogens van 0,3 tot ongeveer 10 MVA aangesloten. In de regio’s voeden de distributienetten de lokale distributienetten. Het totale vermogen van een regionaal distributienet ligt in de orde van 100 MVA. | are depicted in Figure 2.1 with the third ring. These networks are fed from the transmission grids. In these networks, there are also large decentralized generators (combined heat and power plants and wind turbines) and large industrial customers with capacities ranging from 0.3 to approximately 10 MVA. In the regions, the distribution networks feed the local distribution networks. The total capacity of a regional distribution network is in the order of 100 MVA. | grids. The industrial consumers may also have their own power plants. The transmission grids are depicted in Figure 2.1 with the second ring from the inside. De regional distribution networks
De | De | to approximately 10 MVA. In the regions, the distribution networks feed the local distribution networks. The total capacity of a regional distribution network is in the order of 100 MVA.
lokale distributienetten | local distribution networks | approximately 10 MVA. In the regions, the distribution networks feed the local distribution networks. The total capacity of a regional distribution network is in the order of 100 MVA. De
verdelen de elektrische energie over alle kleine aangeslotenen. De kleine aangeslotenen verbruiken elektrische energie maar kunnen dankzij de opmars van kleinschalige decentrale opwekking (micro-warmtekracht en zonnepanelen) ook produceren. Het totale vermogen van een lokaal distributienet is meestal kleiner dan 1 MVA. De lokale distributienetten zijn in figuur 2.1 afgebeeld met de buitenste drie ringen. | distribute the electrical energy to all small consumers. The small consumers use electrical energy but can also produce it thanks to the rise of small-scale decentralized generation (micro-CHP and solar panels). The total capacity of a local distribution network is usually less than 1 MVA. The local distribution networks are depicted in Figure 2.1 with the outer three rings. | In the regions, the distribution networks feed the local distribution networks. The total capacity of a regional distribution network is in the order of 100 MVA. De local distribution networks
Figuur 2.1 Elektriciteitsnet, ingedeeld naar functies | Figure 2.1 Electricity grid, categorized by functions | solar panels). The total capacity of a local distribution network is usually less than 1 MVA. The local distribution networks are depicted in Figure 2.1 with the outer three rings.
Met het naar buiten toe toenemen van de omvang van de ringen en de hoeveelheid van de aangeslotenen illustreert figuur 2.1 dat de regionale en lokale distributienetten in hun totaliteit (qua omvang) groter zijn dan de transportnetten. | As the size of the rings and the number of connections increase outward, Figure 2.1 illustrates that the regional and local distribution networks, in their entirety (in terms of size), are larger than the transmission networks. | local distribution network is usually less than 1 MVA. The local distribution networks are depicted in Figure 2.1 with the outer three rings. Figure 2.1 Electricity grid, categorized by functions
Tabel 2.1 geeft een overzicht van de soorten productie-eenheden en aangeslotenen die op de hierboven genoemde netten zijn aangesloten. De in de tabel genoemde waarden van vermogens zijn indicatief. De kolom ‘Vermogen per net’ geeft aan welke ordegrootte van vermogenstransporten in de genoemde netten voorkomen. | Table 2.1 provides an overview of the types of production units and connections that are linked to the aforementioned networks. The power values mentioned in the table are indicative. The column 'Power per network' indicates the order of magnitude of power transfers occurring in the specified networks. | and the number of connections increase outward, Figure 2.1 illustrates that the regional and local distribution networks, in their entirety (in terms of size), are larger than the transmission networks.
Tabel 2.1 Overzicht van de netten op diverse niveaus met productie en belastingen | Table 2.1 Overview of the networks at various levels with production and loads | the aforementioned networks. The power values mentioned in the table are indicative. The column 'Power per network' indicates the order of magnitude of power transfers occurring in the specified networks.
Net | Net | column 'Power per network' indicates the order of magnitude of power transfers occurring in the specified networks. Table 2.1 Overview of the networks at various levels with production and loads
Productie-eenheden | Production units | 'Power per network' indicates the order of magnitude of power transfers occurring in the specified networks. Table 2.1 Overview of the networks at various levels with production and loads Net
Aangeslotenen | Aangeslotenen | network' indicates the order of magnitude of power transfers occurring in the specified networks. Table 2.1 Overview of the networks at various levels with production and loads Net Production units
Vermogen per net | Power per network | indicates the order of magnitude of power transfers occurring in the specified networks. Table 2.1 Overview of the networks at various levels with production and loads Net Production units Aangeslotenen
Koppelnet | Koppelnet | of magnitude of power transfers occurring in the specified networks. Table 2.1 Overview of the networks at various levels with production and loads Net Production units Aangeslotenen Power per network
Centrale (>500 MW) | Power plant (>500 MW) | magnitude of power transfers occurring in the specified networks. Table 2.1 Overview of the networks at various levels with production and loads Net Production units Aangeslotenen Power per network Koppelnet
> 1000 MW | > 1000 MW | occurring in the specified networks. Table 2.1 Overview of the networks at various levels with production and loads Net Production units Aangeslotenen Power per network Koppelnet Power plant (>500 MW)
Transportnet | Transportnet | specified networks. Table 2.1 Overview of the networks at various levels with production and loads Net Production units Aangeslotenen Power per network Koppelnet Power plant (>500 MW) > 1000 MW
Centrale (10-500 MW) | Power plant (10-500 MW) | networks. Table 2.1 Overview of the networks at various levels with production and loads Net Production units Aangeslotenen Power per network Koppelnet Power plant (>500 MW) > 1000 MW Transportnet
Grote WKK (>10 MW) | Large CHP (>10 MW) | of the networks at various levels with production and loads Net Production units Aangeslotenen Power per network Koppelnet Power plant (>500 MW) > 1000 MW Transportnet Power plant (10-500 MW)
Windpark (>10 MW) | Wind farm (>10 MW) | various levels with production and loads Net Production units Aangeslotenen Power per network Koppelnet Power plant (>500 MW) > 1000 MW Transportnet Power plant (10-500 MW) Large CHP (>10 MW)
Grote industrie met evt. eigen opwekking (>10 MW) | Large industry with possible own generation (>10 MW) | and loads Net Production units Aangeslotenen Power per network Koppelnet Power plant (>500 MW) > 1000 MW Transportnet Power plant (10-500 MW) Large CHP (>10 MW) Wind farm (>10 MW)
> 100 MW | > 100 MW | network Koppelnet Power plant (>500 MW) > 1000 MW Transportnet Power plant (10-500 MW) Large CHP (>10 MW) Wind farm (>10 MW) Large industry with possible own generation (>10 MW)
Distributienet, regionaal | Distribution network, regional | plant (>500 MW) > 1000 MW Transportnet Power plant (10-500 MW) Large CHP (>10 MW) Wind farm (>10 MW) Large industry with possible own generation (>10 MW) > 100 MW
Middelgrote WKK | Medium-sized CHP | > 1000 MW Transportnet Power plant (10-500 MW) Large CHP (>10 MW) Wind farm (>10 MW) Large industry with possible own generation (>10 MW) > 100 MW Distribution network, regional
(0,3-10 MW) | (0.3-10 MW) | MW Transportnet Power plant (10-500 MW) Large CHP (>10 MW) Wind farm (>10 MW) Large industry with possible own generation (>10 MW) > 100 MW Distribution network, regional Medium-sized CHP
Windturbine (0,3-10 MW) | Wind turbine (0.3-10 MW) | Power plant (10-500 MW) Large CHP (>10 MW) Wind farm (>10 MW) Large industry with possible own generation (>10 MW) > 100 MW Distribution network, regional Medium-sized CHP (0.3-10 MW)
Grootverbruiker | Grootverbruiker | Large CHP (>10 MW) Wind farm (>10 MW) Large industry with possible own generation (>10 MW) > 100 MW Distribution network, regional Medium-sized CHP (0.3-10 MW) Wind turbine (0.3-10 MW)
(0,3-10 MW) | (0.3-10 MW) | CHP (>10 MW) Wind farm (>10 MW) Large industry with possible own generation (>10 MW) > 100 MW Distribution network, regional Medium-sized CHP (0.3-10 MW) Wind turbine (0.3-10 MW) Grootverbruiker
< 100 MW | < 100 MW | MW) Wind farm (>10 MW) Large industry with possible own generation (>10 MW) > 100 MW Distribution network, regional Medium-sized CHP (0.3-10 MW) Wind turbine (0.3-10 MW) Grootverbruiker (0.3-10 MW)
Distributienet, lokaal | Distribution network, local | (>10 MW) Large industry with possible own generation (>10 MW) > 100 MW Distribution network, regional Medium-sized CHP (0.3-10 MW) Wind turbine (0.3-10 MW) Grootverbruiker (0.3-10 MW) < 100 MW
micro-WKK (<0,3 MW) | micro-CHP (<0.3 MW) | industry with possible own generation (>10 MW) > 100 MW Distribution network, regional Medium-sized CHP (0.3-10 MW) Wind turbine (0.3-10 MW) Grootverbruiker (0.3-10 MW) < 100 MW Distribution network, local
PV-systemen (<0,3 MW) | PV systems (<0.3 MW) | own generation (>10 MW) > 100 MW Distribution network, regional Medium-sized CHP (0.3-10 MW) Wind turbine (0.3-10 MW) Grootverbruiker (0.3-10 MW) < 100 MW Distribution network, local micro-CHP (<0.3 MW)
MKB (<0,3 MW) | SME (<0.3 MW) | > 100 MW Distribution network, regional Medium-sized CHP (0.3-10 MW) Wind turbine (0.3-10 MW) Grootverbruiker (0.3-10 MW) < 100 MW Distribution network, local micro-CHP (<0.3 MW) PV systems (<0.3 MW)
Huishoudens | Huishoudens | Distribution network, regional Medium-sized CHP (0.3-10 MW) Wind turbine (0.3-10 MW) Grootverbruiker (0.3-10 MW) < 100 MW Distribution network, local micro-CHP (<0.3 MW) PV systems (<0.3 MW) SME (<0.3 MW)
< 1 MW | < 1 MW | network, regional Medium-sized CHP (0.3-10 MW) Wind turbine (0.3-10 MW) Grootverbruiker (0.3-10 MW) < 100 MW Distribution network, local micro-CHP (<0.3 MW) PV systems (<0.3 MW) SME (<0.3 MW) Huishoudens
2.2 Spanningsniveaus in het elektriciteitsnet | 2.2 Voltage Levels in the Electrical Grid | CHP (0.3-10 MW) Wind turbine (0.3-10 MW) Grootverbruiker (0.3-10 MW) < 100 MW Distribution network, local micro-CHP (<0.3 MW) PV systems (<0.3 MW) SME (<0.3 MW) Huishoudens < 1 MW
De functie heeft een relatie met het spanningsniveau, omdat bij een hoog spanningsniveau een groter vermogen getransporteerd kan worden dan bij een laag spanningsniveau. Als gevolg hebben de hoogspanningsnetten altijd een transportfunctie en de laagspanningsnetten altijd een distributiefunctie. Bovendien is het laagspanningsniveau praktisch en veilig voor het aansluiten van de installaties van de klanten. Tussen de hoog- en laagspanningsniveaus is een overgangsgebied van de transport- naar de distributiefunctie. Het overgangsgebied betreft het middenspanningsniveau. De middenspanningsnetten hebben meestal een distributiefunctie, maar hebben soms ook een transportfunctie. Ondanks deze onduidelijkheid worden de elektriciteitsnetten meestal aangeduid met hun spanningsniveau. Figuur 2.2 geeft een overzicht van de in Nederland toegepaste spanningsniveaus en transformatiestappen. Dit is een overzicht van standaard spanningen. Door innovaties kunnen langzamerhand in de spanningsniveaus en transformatiestappen meerdere varianten ontstaan. Een voorbeeld wordt getoond in figuur 2.10. | The function is related to the voltage level, because at a high voltage level, more power can be transported than at a low voltage level. As a result, high-voltage networks always have a transport function, and low-voltage networks always have a distribution function. Moreover, the low-voltage level is practical and safe for connecting customer installations. Between the high and low voltage levels, there is a transition area from the transport function to the distribution function. This transition area concerns the medium voltage level. Medium voltage networks usually have a distribution function but sometimes also have a transport function. Despite this ambiguity, electrical grids are usually referred to by their voltage level. Figure 2.2 provides an overview of the voltage levels and transformation steps applied in the Netherlands. This is an overview of standard voltages. Due to innovations, multiple variants in voltage levels and transformation steps may gradually emerge. An example is shown in Figure 2.10. | Grootverbruiker (0.3-10 MW) < 100 MW Distribution network, local micro-CHP (<0.3 MW) PV systems (<0.3 MW) SME (<0.3 MW) Huishoudens < 1 MW 2.2 Voltage Levels in the Electrical Grid
Figuur 2.2 Spanningsniveaus | Figure 2.2 Voltage Levels | the Netherlands. This is an overview of standard voltages. Due to innovations, multiple variants in voltage levels and transformation steps may gradually emerge. An example is shown in Figure 2.10.
Het | Het | an overview of standard voltages. Due to innovations, multiple variants in voltage levels and transformation steps may gradually emerge. An example is shown in Figure 2.10. Figure 2.2 Voltage Levels
hoogspanningsniveau | hoogspanningsniveau | overview of standard voltages. Due to innovations, multiple variants in voltage levels and transformation steps may gradually emerge. An example is shown in Figure 2.10. Figure 2.2 Voltage Levels Het
met spanningen van 110 tot en met 380 kV is met een rode kleur aangegeven. Het koppelnet is uitgevoerd voor de spanningsniveaus van 220 en 380 kV en de transportnetten voor de spanningsniveaus van 110 en 150 kV. Het koppelnet en de transportnetten worden beheerd door de landelijk netwerk beheerder (LNB). De netten van lagere spanningsniveaus worden beheerd door de regionale netbeheerders (RNB). De grens tussen het net van de landelijk netwerk beheerder (LNB) en de netten van de regionale netbeheerders (RNB) ligt op de primaire transformatorklemmen. | with voltages ranging from 110 to 380 kV is indicated in red. The coupling network is designed for voltage levels of 220 and 380 kV, and the transmission networks for voltage levels of 110 and 150 kV. The coupling network and the transmission networks are managed by the national network operator (LNB). The networks of lower voltage levels are managed by the regional network operators (RNB). The boundary between the network of the national network operator (LNB) and the networks of the regional network operators (RNB) is at the primary transformer terminals. | of standard voltages. Due to innovations, multiple variants in voltage levels and transformation steps may gradually emerge. An example is shown in Figure 2.10. Figure 2.2 Voltage Levels Het hoogspanningsniveau
Het | Het | regional network operators (RNB). The boundary between the network of the national network operator (LNB) and the networks of the regional network operators (RNB) is at the primary transformer terminals.
tussenspanningsniveau | tussenspanningsniveau | network operators (RNB). The boundary between the network of the national network operator (LNB) and the networks of the regional network operators (RNB) is at the primary transformer terminals. Het
met spanningen van 25 tot en met 50 kV is met een groene kleur aangegeven. De netten op deze spanningsniveaus hebben een transportfunctie. | with voltages ranging from 25 to 50 kV are indicated in green. The networks at these voltage levels have a transport function. | operators (RNB). The boundary between the network of the national network operator (LNB) and the networks of the regional network operators (RNB) is at the primary transformer terminals. Het tussenspanningsniveau
Het | Het | is at the primary transformer terminals. Het tussenspanningsniveau with voltages ranging from 25 to 50 kV are indicated in green. The networks at these voltage levels have a transport function.
middenspanningsniveau | middenspanningsniveau | at the primary transformer terminals. Het tussenspanningsniveau with voltages ranging from 25 to 50 kV are indicated in green. The networks at these voltage levels have a transport function. Het
met spanningen van 10 tot en met 20 kV is met een zwarte kleur aangegeven. Sporadisch komen ook nog spanningen van 3 en 6 kV voor maar die worden niet meer toegepast in nieuwe netten. | with voltages ranging from 10 to 20 kV are indicated in black. Occasionally, voltages of 3 and 6 kV are also encountered, but these are no longer used in new networks. | the primary transformer terminals. Het tussenspanningsniveau with voltages ranging from 25 to 50 kV are indicated in green. The networks at these voltage levels have a transport function. Het middenspanningsniveau
Het | Het | voltages ranging from 10 to 20 kV are indicated in black. Occasionally, voltages of 3 and 6 kV are also encountered, but these are no longer used in new networks.
laagspanningsniveau | laagspanningsniveau | ranging from 10 to 20 kV are indicated in black. Occasionally, voltages of 3 and 6 kV are also encountered, but these are no longer used in new networks. Het
met een spanning van 400 V is met een blauwe kleur aangegeven. | with a voltage of 400 V is indicated in blue. | from 10 to 20 kV are indicated in black. Occasionally, voltages of 3 and 6 kV are also encountered, but these are no longer used in new networks. Het laagspanningsniveau
De netten van verschillende spanningsniveaus zijn met behulp van transformatorstations onderling gekoppeld. Om een indruk te krijgen van de omvang van de netten op de verschillende spanningsniveaus kan gekeken worden naar de transportcapaciteit. De capaciteit van de transformatorstations tussen het koppelnet en de transportnetten is meer dan 500 MVA. In het koppelnet zijn enkele tientallen van deze stations. De capaciteit van een transformatorstation tussen het transportnet en het distributienet, van hoogspanning naar middenspanning, ligt in de ordegrootte van 100 MVA. Hiervan zijn er ongeveer 200 in Nederland. De capaciteit van een transformatorstation tussen het middenspannings- en laagspanningsniveau ligt in de ordegrootte van 0,2 tot 1 MVA. | The networks of different voltage levels are interconnected using transformer stations. To get an impression of the scale of the networks at the various voltage levels, one can look at the transport capacity. The capacity of the transformer stations between the coupling network and the transport networks is more than 500 MVA. There are several dozen of these stations in the coupling network. The capacity of a transformer station between the transport network and the distribution network, from high voltage to medium voltage, is in the order of 100 MVA. There are approximately 200 of these in the Netherlands. The capacity of a transformer station between the medium voltage and low voltage levels is in the order of 0.2 to 1 MVA. | voltages of 3 and 6 kV are also encountered, but these are no longer used in new networks. Het laagspanningsniveau with a voltage of 400 V is indicated in blue.
Ook de afstand tussen de stations op de verschillende spanningsniveaus geeft een indruk van de omvang van de netten. De afstand tussen twee stations in het koppelnet is 35-50 km. De gemiddelde afstand tussen twee stations in het hoogspanningsnet is 15 km (Kling, 1999). De gemiddelde afstand tussen twee stations in het middenspanningsnet is ongeveer 500 m. Er kunnen 250 tot 500 netstations op een onderstation zijn aangesloten. Een netstation verzorgt via het laagspanningsnet de aansluiting van 50 tot 250 aangeslotenen, meestal industrie en woningen. | The distance between stations at different voltage levels also gives an impression of the network's size. The distance between two stations in the coupling network is 35-50 km. The average distance between two stations in the high-voltage network is 15 km (Kling, 1999). The average distance between two stations in the medium-voltage network is approximately 500 m. There can be 250 to 500 network stations connected to a substation. A network station provides connections for 50 to 250 consumers, usually industries and residences, via the low-voltage network. | approximately 200 of these in the Netherlands. The capacity of a transformer station between the medium voltage and low voltage levels is in the order of 0.2 to 1 MVA.
Tabel 2.2 geeft een beeld van de omvang van de transport- en distributienetten in Nederland en is ontleend aan Netbeheer Nederland (Netbeheer, 2010). Hierin is te zien dat in 2009 bijna alle verbindingen van het hoogste spanningsniveau bovengronds zijn uitgevoerd en dat bijna het gehele distributienet ondergronds is uitgevoerd. Ook is goed te zien dat de omvang van het totale distributienet ongeveer 20 maal zo groot is als het koppelnet en het transportnet. | Table 2.2 provides an overview of the size of the transport and distribution networks in the Netherlands and is derived from Netbeheer Nederland (Netbeheer, 2010). It shows that in 2009, almost all connections at the highest voltage level were above ground, while nearly the entire distribution network was underground. It is also clear that the total distribution network is approximately 20 times larger than the coupling network and the transport network. | There can be 250 to 500 network stations connected to a substation. A network station provides connections for 50 to 250 consumers, usually industries and residences, via the low-voltage network.
Tabel 2.2 Transport- en distributienetten in Nederland, 2009 | Table 2.2 Transport and Distribution Networks in the Netherlands, 2009 | while nearly the entire distribution network was underground. It is also clear that the total distribution network is approximately 20 times larger than the coupling network and the transport network.
Functie | Functie | also clear that the total distribution network is approximately 20 times larger than the coupling network and the transport network. Table 2.2 Transport and Distribution Networks in the Netherlands, 2009
Niveau | Niveau | clear that the total distribution network is approximately 20 times larger than the coupling network and the transport network. Table 2.2 Transport and Distribution Networks in the Netherlands, 2009 Functie
Bovengronds (km) | Above ground (km) | that the total distribution network is approximately 20 times larger than the coupling network and the transport network. Table 2.2 Transport and Distribution Networks in the Netherlands, 2009 Functie Niveau
Ondergronds (km) | Underground (km) | distribution network is approximately 20 times larger than the coupling network and the transport network. Table 2.2 Transport and Distribution Networks in the Netherlands, 2009 Functie Niveau Above ground (km)
Koppelnet | Koppelnet | is approximately 20 times larger than the coupling network and the transport network. Table 2.2 Transport and Distribution Networks in the Netherlands, 2009 Functie Niveau Above ground (km) Underground (km)
Hoogspanning | Hoogspanning | approximately 20 times larger than the coupling network and the transport network. Table 2.2 Transport and Distribution Networks in the Netherlands, 2009 Functie Niveau Above ground (km) Underground (km) Koppelnet
(220/380 kV) | (220/380 kV) | 20 times larger than the coupling network and the transport network. Table 2.2 Transport and Distribution Networks in the Netherlands, 2009 Functie Niveau Above ground (km) Underground (km) Koppelnet Hoogspanning
2682 | 2682 | larger than the coupling network and the transport network. Table 2.2 Transport and Distribution Networks in the Netherlands, 2009 Functie Niveau Above ground (km) Underground (km) Koppelnet Hoogspanning (220/380 kV)
3 | 3 | than the coupling network and the transport network. Table 2.2 Transport and Distribution Networks in the Netherlands, 2009 Functie Niveau Above ground (km) Underground (km) Koppelnet Hoogspanning (220/380 kV) 2682
Transportnet | Transportnet | the coupling network and the transport network. Table 2.2 Transport and Distribution Networks in the Netherlands, 2009 Functie Niveau Above ground (km) Underground (km) Koppelnet Hoogspanning (220/380 kV) 2682 3
Hoogspanning | Hoogspanning | coupling network and the transport network. Table 2.2 Transport and Distribution Networks in the Netherlands, 2009 Functie Niveau Above ground (km) Underground (km) Koppelnet Hoogspanning (220/380 kV) 2682 3 Transportnet
(50/110/150 kV) | (50/110/150 kV) | network and the transport network. Table 2.2 Transport and Distribution Networks in the Netherlands, 2009 Functie Niveau Above ground (km) Underground (km) Koppelnet Hoogspanning (220/380 kV) 2682 3 Transportnet Hoogspanning
5492 | 5492 | the transport network. Table 2.2 Transport and Distribution Networks in the Netherlands, 2009 Functie Niveau Above ground (km) Underground (km) Koppelnet Hoogspanning (220/380 kV) 2682 3 Transportnet Hoogspanning (50/110/150 kV)
3760 | 3760 | transport network. Table 2.2 Transport and Distribution Networks in the Netherlands, 2009 Functie Niveau Above ground (km) Underground (km) Koppelnet Hoogspanning (220/380 kV) 2682 3 Transportnet Hoogspanning (50/110/150 kV) 5492
Distributie, regionaal | Distribution, regional | network. Table 2.2 Transport and Distribution Networks in the Netherlands, 2009 Functie Niveau Above ground (km) Underground (km) Koppelnet Hoogspanning (220/380 kV) 2682 3 Transportnet Hoogspanning (50/110/150 kV) 5492 3760
Middenspanning | Middenspanning | 2.2 Transport and Distribution Networks in the Netherlands, 2009 Functie Niveau Above ground (km) Underground (km) Koppelnet Hoogspanning (220/380 kV) 2682 3 Transportnet Hoogspanning (50/110/150 kV) 5492 3760 Distribution, regional
(3 t/m 25 kV) | (3 to 25 kV) | Transport and Distribution Networks in the Netherlands, 2009 Functie Niveau Above ground (km) Underground (km) Koppelnet Hoogspanning (220/380 kV) 2682 3 Transportnet Hoogspanning (50/110/150 kV) 5492 3760 Distribution, regional Middenspanning
0 | 0 | in the Netherlands, 2009 Functie Niveau Above ground (km) Underground (km) Koppelnet Hoogspanning (220/380 kV) 2682 3 Transportnet Hoogspanning (50/110/150 kV) 5492 3760 Distribution, regional Middenspanning (3 to 25 kV)
101965 | 101965 | the Netherlands, 2009 Functie Niveau Above ground (km) Underground (km) Koppelnet Hoogspanning (220/380 kV) 2682 3 Transportnet Hoogspanning (50/110/150 kV) 5492 3760 Distribution, regional Middenspanning (3 to 25 kV) 0
Distributie, lokaal | Distribution, local | Netherlands, 2009 Functie Niveau Above ground (km) Underground (km) Koppelnet Hoogspanning (220/380 kV) 2682 3 Transportnet Hoogspanning (50/110/150 kV) 5492 3760 Distribution, regional Middenspanning (3 to 25 kV) 0 101965
Laagspanning | Laagspanning | Functie Niveau Above ground (km) Underground (km) Koppelnet Hoogspanning (220/380 kV) 2682 3 Transportnet Hoogspanning (50/110/150 kV) 5492 3760 Distribution, regional Middenspanning (3 to 25 kV) 0 101965 Distribution, local
(0,4 kV) | (0.4 kV) | Niveau Above ground (km) Underground (km) Koppelnet Hoogspanning (220/380 kV) 2682 3 Transportnet Hoogspanning (50/110/150 kV) 5492 3760 Distribution, regional Middenspanning (3 to 25 kV) 0 101965 Distribution, local Laagspanning
174 | 174 | ground (km) Underground (km) Koppelnet Hoogspanning (220/380 kV) 2682 3 Transportnet Hoogspanning (50/110/150 kV) 5492 3760 Distribution, regional Middenspanning (3 to 25 kV) 0 101965 Distribution, local Laagspanning (0.4 kV)
145165 | 145165 | (km) Underground (km) Koppelnet Hoogspanning (220/380 kV) 2682 3 Transportnet Hoogspanning (50/110/150 kV) 5492 3760 Distribution, regional Middenspanning (3 to 25 kV) 0 101965 Distribution, local Laagspanning (0.4 kV) 174
De regionale en lokale netten tot aan de meterkast van de aangeslotenen worden beheerd door regionale netwerk beheerders (RNB). Het jaarverslag van Alliander (2009) geeft een voorbeeld van de omvang van de netten op de diverse spanningsniveaus van een grote RNB: | The regional and local networks up to the meter box of the connected customers are managed by regional network operators (RNO). The annual report of Alliander (2009) provides an example of the extent of the networks at various voltage levels of a large RNO: | Underground (km) Koppelnet Hoogspanning (220/380 kV) 2682 3 Transportnet Hoogspanning (50/110/150 kV) 5492 3760 Distribution, regional Middenspanning (3 to 25 kV) 0 101965 Distribution, local Laagspanning (0.4 kV) 174 145165
Tussenspanning (50 kV): 2300 km | Medium voltage (50 kV): 2300 km | are managed by regional network operators (RNO). The annual report of Alliander (2009) provides an example of the extent of the networks at various voltage levels of a large RNO:
Middenspanning (3, 10, 20 kV): 35300 km | Medium voltage (3, 10, 20 kV): 35,300 km | (RNO). The annual report of Alliander (2009) provides an example of the extent of the networks at various voltage levels of a large RNO: Medium voltage (50 kV): 2300 km
Laagspanning (400 V): 47700 km | Low voltage (400 V): 47,700 km | an example of the extent of the networks at various voltage levels of a large RNO: Medium voltage (50 kV): 2300 km Medium voltage (3, 10, 20 kV): 35,300 km
De netten op het middenspanningsniveau en het laagspanningsniveau zijn het meest vertakt en daardoor in omvang het grootst. Om die reden is de aandacht in dit boek vooral gericht op de Nederlandse midden- en laagspanningsnetten en het optimale netontwerp ervan. | The networks at the medium voltage level and the low voltage level are the most branched and therefore the largest in size. For that reason, the focus in this book is primarily on the Dutch medium and low voltage networks and their optimal network design. | the networks at various voltage levels of a large RNO: Medium voltage (50 kV): 2300 km Medium voltage (3, 10, 20 kV): 35,300 km Low voltage (400 V): 47,700 km
2.3 Kwaliteit en beschikbaarheid | 2.3 Quality and Availability | branched and therefore the largest in size. For that reason, the focus in this book is primarily on the Dutch medium and low voltage networks and their optimal network design.
In de elektriciteitswet is geregeld aan welke kwaliteitseisen een aansluiting moet voldoen. Onder kwaliteit worden de beschikbaarheid en de kwaliteit van de spanning en de stroom verstaan. De kwaliteit van de spanning en de stroom voor aangeslotenen op de distributienetten is in detail geregeld in de internationale norm IEC 50160 en wordt verder behandeld in hoofdstuk 11 over ‘Power Quality’. De beschikbaarheid van de levering volgt uit de betrouwbaarheid van het elektriciteitsnet en wordt behandeld in hoofdstuk 12. De beschikbaarheid wordt gekarakteriseerd door het aantal onderbrekingen per jaar, de gemiddelde onderbrekingsduur en de gemiddelde jaarlijkse onderbrekingsduur. Bij het ontwerp van een elektriciteitsnet wordt erop gelet dat de gevolgen van een storing in een bedrijfsmiddel, door een eigen defect of een externe oorzaak, voor de beschikbaarheid van de levering zo klein mogelijk zijn. Zo zal bij een kortsluiting het gestoorde bedrijfsmiddel direct moeten worden afgeschakeld. Het hangt af van de functie of het spanningsniveau van het net of alleen het bedrijfsmiddel zelf of een gedeelte van het net wordt afgeschakeld. Met het oog op de beschikbaarheid is redundantie in het elektriciteitsnet aanwezig. De mate van redundantie hangt af van het ontwerp en de bedrijfsvoering en is het resultaat van een kosten/batenafweging. In de transportnetten is het aantal storingen dat leidt tot een onderbreking door de hoge mate van redundantie zeer klein. Er is veel redundantie aanwezig omdat bij elke onderbreking zeer veel aangeslotenen getroffen worden. Zo leidt bijvoorbeeld de onderbreking van een onderstation, dat 500 netstations voedt met ieder gemiddeld 50 aangeslotenen, tot een onderbreking van in totaal 25000 aangeslotenen. In de distributienetten is minder redundantie ingebouwd, zodat een kortsluiting meestal zal leiden tot een onderbreking in een deel van het net. In de middenspanningsdistributienetten is bij een kortsluiting het aantal getroffen aangeslotenen in de ordegrootte van 1000 en wordt de levering redelijk snel hersteld door omschakelacties, waarbij gebruik wordt gemaakt van de redundantie in de transportcapaciteit van de overige verbindingen. In de laagspanningsnetten is het aantal getroffenen meestal niet meer dan enkele tientallen en is geen redundantie aanwezig. Men moet wachten op reparatie of een noodstroomvoorziening. | The Electricity Act stipulates the quality requirements that a connection must meet. Quality refers to the availability and quality of the voltage and current. The quality of the voltage and current for consumers connected to the distribution networks is detailed in the international standard IEC 50160 and is further discussed in Chapter 11 on 'Power Quality.' The availability of the supply is derived from the reliability of the electricity network and is covered in Chapter 12. Availability is characterized by the number of interruptions per year, the average interruption duration, and the average annual interruption duration. When designing an electricity network, care is taken to minimize the impact of a failure in an asset, whether due to an internal defect or an external cause, on the availability of the supply. For instance, in the event of a short circuit, the faulty asset must be immediately disconnected. Depending on the function or voltage level of the network, either only the asset itself or a portion of the network will be disconnected. To ensure availability, redundancy is built into the electricity network. The degree of redundancy depends on the design and operation and is the result of a cost-benefit analysis. In transmission networks, the number of failures leading to an interruption is very small due to the high level of redundancy. There is significant redundancy because each interruption affects a large number of consumers. For example, the interruption of a substation that feeds 500 network stations, each with an average of 50 consumers, results in an interruption affecting a total of 25,000 consumers. In distribution networks, less redundancy is built in, so a short circuit usually leads to an interruption in part of the network. In medium voltage distribution networks, a short circuit typically affects around 1,000 consumers, and the supply is reasonably quickly restored through switching actions, utilizing the redundancy in the transport capacity of the remaining connections. In low voltage networks, the number of affected consumers is usually no more than a few dozen, and there is no redundancy. One must wait for repairs or an emergency power supply. | largest in size. For that reason, the focus in this book is primarily on the Dutch medium and low voltage networks and their optimal network design. 2.3 Quality and Availability
Bij het beoordelen van de beschikbaarheid en de benodigde redundantie wordt meestal gekeken naar de ‘Enkelvoudige storing’. Dit is de uitval van een productie-eenheid of een willekeurig element in het elektriciteitsvoorzieningsysteem. De NMa hanteert ten aanzien van de bedrijfszekerheid het begrip ‘Enkelvoudige storingsreserve’ (EVSR): de toestand van een net waarin de normale bedrijfstoestand blijft gehandhaafd wanneer een enkelvoudige storing optreedt (Begrippenlijst, 2009). Voor het beschrijven van de bedrijfszekerheid zijn dan onderstaande vier gradaties gedefinieerd: | When assessing availability and the required redundancy, the focus is usually on the 'Single Failure'. This refers to the failure of a production unit or any element within the electricity supply system. The NMa uses the term 'Single Failure Reserve' (EVSR) concerning operational reliability: the state of a network in which the normal operating condition is maintained when a single failure occurs (Glossary, 2009). The following four levels are defined for describing operational reliability: | voltage networks, the number of affected consumers is usually no more than a few dozen, and there is no redundancy. One must wait for repairs or an emergency power supply.
Enkelvoudige storingsreserve zonder energieonderbreking (ook wel n | Single failure reserve without energy interruption (also known as n | the state of a network in which the normal operating condition is maintained when a single failure occurs (Glossary, 2009). The following four levels are defined for describing operational reliability:
–1 reserve genoemd): | referred to as –1 reserve): | condition is maintained when a single failure occurs (Glossary, 2009). The following four levels are defined for describing operational reliability: Single failure reserve without energy interruption (also known as n
dit betekent dat er voor alle enkelvoudige storingen een reserve aanwezig is, waarbij uitval van één object niet leidt tot een onderbreking. In dit geval bestaan parallelle paden naar de voeding, die de energielevering ononderbroken kunnen overnemen. De reserve staat ogenblikkelijk ter beschikking. | This means that for all single failures, a reserve is available, where the failure of one object does not lead to an interruption. In this case, parallel paths to the power supply exist, which can take over the energy delivery without interruption. The reserve is immediately available. | single failure occurs (Glossary, 2009). The following four levels are defined for describing operational reliability: Single failure reserve without energy interruption (also known as n referred to as –1 reserve):
Enkelvoudige storingsreserve met energieonderbreking: | Single fault reserve with energy interruption: | does not lead to an interruption. In this case, parallel paths to the power supply exist, which can take over the energy delivery without interruption. The reserve is immediately available.
dit betekent dat er voor alle enkelvoudige storingen een reserve aanwezig is, waarbij uitval van één object wel leidt tot een onderbreking. In dit geval hebben meerdere objecten één gezamenlijke reserve waarmee door middel van (om)schakelen de energielevering hersteld kan worden. De reserve staat stand-by. Indien de foutplaats bekend is en de omschakelacties van verre (vanuit het bedrijfsvoeringscentrum) uitgevoerd kunnen worden, is de levering redelijk snel (enkele minuten tot een kwartier) hersteld. In het geval van door personeel uitgevoerde inspecties en handbediende schakelacties moet rekening gehouden worden met een herstelduur van een half tot anderhalf uur. | This means that for all single faults, a reserve is available, where the failure of one object does lead to an interruption. In this case, multiple objects share a common reserve, which can restore the energy supply through switching. The reserve is on standby. If the fault location is known and the switching actions can be performed remotely (from the operations center), the supply is restored fairly quickly (a few minutes to a quarter of an hour). In the case of inspections and manual switching actions performed by personnel, a recovery time of half an hour to an hour and a half should be expected. | In this case, parallel paths to the power supply exist, which can take over the energy delivery without interruption. The reserve is immediately available. Single fault reserve with energy interruption:
Geen storingsreserve, herstel door inzet van aggregaat: | No fault reserve, recovery through the use of a generator: | an hour). In the case of inspections and manual switching actions performed by personnel, a recovery time of half an hour to an hour and a half should be expected.
Uitval van een object leidt tot onderbreking van de energielevering, die niet door middel van omschakelen kan worden hersteld. De energielevering kan worden hersteld door inzet van een aggregaat. | Failure of an object leads to an interruption of the power supply, which cannot be restored by switching. The power supply can be restored by using a generator. | actions performed by personnel, a recovery time of half an hour to an hour and a half should be expected. No fault reserve, recovery through the use of a generator:
Geen storingsreserve: | No fault reserve: | a generator: Failure of an object leads to an interruption of the power supply, which cannot be restored by switching. The power supply can be restored by using a generator.
Uitval van een object leidt tot onderbreking van de energielevering, die niet door middel van omschakelen kan worden hersteld. De energielevering kan ook niet worden hersteld door inzet van een aggregaat. | Failure of an object leads to an interruption of the power supply, which cannot be restored by switching. The power supply also cannot be restored by using a generator. | of an object leads to an interruption of the power supply, which cannot be restored by switching. The power supply can be restored by using a generator. No fault reserve:
2.3.1 Transportnet | 2.3.1 Transmission Network | reserve: Failure of an object leads to an interruption of the power supply, which cannot be restored by switching. The power supply also cannot be restored by using a generator.
Een transportnet verplaatst grote elektrische vermogens over lange afstanden. Omdat de gevolgen van een onderbreking van de energielevering bij toenemend spanningsniveau in omvang toenemen en daarmee al snel als onaanvaardbaar worden ervaren, worden transportnetten ontworpen en bedreven met ‘enkelvoudige storingsreserve zonder energieonderbreking’ (n-1). Ook tijdens onderhoud aan primaire objecten uit het transportnet moet er sprake zijn van deze enkelvoudige storingsreserve. Slechts in bijzondere situaties mag soms sprake zijn van bedrijfsvoering met een kans op een energieonderbreking ten gevolge van een storing. | A transmission network transfers large amounts of electrical power over long distances. Because the consequences of an interruption in power supply increase with higher voltage levels and are quickly deemed unacceptable, transmission networks are designed and operated with a 'single contingency without power interruption' (n-1). This single contingency must also be in place during maintenance of primary objects in the transmission network. Only in exceptional situations is it sometimes permissible to operate with a risk of power interruption due to a fault. | an object leads to an interruption of the power supply, which cannot be restored by switching. The power supply also cannot be restored by using a generator. 2.3.1 Transmission Network
Hoogspanningsnetten | Hoogspanningsnetten | place during maintenance of primary objects in the transmission network. Only in exceptional situations is it sometimes permissible to operate with a risk of power interruption due to a fault.
Transport vindt voornamelijk plaats via hoogspanningsnetten, waarvan de spanning vaak hoger is dan de opgewekte of afgenomen spanning. Doordat de netten op nationaal en internationaal niveau met elkaar gekoppeld zijn, verkrijgt men een stabiel transportnet met een hoge bedrijfszekerheid. De internationale connectie maakt het mogelijk om energie uit te wisselen tussen verschillende landen. De elektriciteitcentrales worden op het hoogspanningsnet aangesloten. Dit geldt ook voor grote decentrale opwekkers, zoals clusters van warmte/krachtcentrales en windmolenparken. De regionale tussenspannings- of middenspanningsnetten en grote industriële netten zijn via transformatoren aan het hoogspanningsnet gekoppeld. De meest voorkomende spanningsniveaus zijn: | Transport mainly takes place via high-voltage networks, where the voltage is often higher than the generated or consumed voltage. Because the networks are interconnected at both national and international levels, a stable transmission network with high operational reliability is achieved. The international connection makes it possible to exchange energy between different countries. The power plants are connected to the high-voltage network. This also applies to large decentralized generators, such as clusters of combined heat and power plants and wind farms. The regional medium-voltage or intermediate-voltage networks and large industrial networks are connected to the high-voltage network via transformers. The most common voltage levels are: | during maintenance of primary objects in the transmission network. Only in exceptional situations is it sometimes permissible to operate with a risk of power interruption due to a fault. Hoogspanningsnetten
380 kV voor het landelijk koppelnet en de internationale koppelingen | 380 kV for the national grid and international connections | and power plants and wind farms. The regional medium-voltage or intermediate-voltage networks and large industrial networks are connected to the high-voltage network via transformers. The most common voltage levels are:
220 kV voor het landelijk koppelnet | 220 kV for the national coupling network | or intermediate-voltage networks and large industrial networks are connected to the high-voltage network via transformers. The most common voltage levels are: 380 kV for the national grid and international connections
150 kV voor de regionale transportnetten | 150 kV for the regional transmission networks | are connected to the high-voltage network via transformers. The most common voltage levels are: 380 kV for the national grid and international connections 220 kV for the national coupling network
110 kV voor de regionale transportnetten | 110 kV for the regional transmission networks | transformers. The most common voltage levels are: 380 kV for the national grid and international connections 220 kV for the national coupling network 150 kV for the regional transmission networks
Tussenspanningsnetten | Tussenspanningsnetten | 380 kV for the national grid and international connections 220 kV for the national coupling network 150 kV for the regional transmission networks 110 kV for the regional transmission networks
Een tussenspanningsnet transporteert relatief grote elektrische vermogens (ordegrootte 50 tot 100 MVA) vanuit het hoogspanningsnet naar voedingspunten voor middenspanningsnetten. Het tussenspanningsnet is een schakel tussen de hoog- en middenspanningsnetten maar wordt niet altijd toegepast. Veel voorkomende spanningsniveaus zijn 25 kV en 50 kV. Vanwege de hoge eisen aan de leveringszekerheid heeft het TS-transportnet veelal een enkelvoudige storingsreserve zonder energie onderbreking. Enkelvoudige storingreserve met energie onderbreking kan echter ook voorkomen. | An intermediate voltage network transports relatively large electrical power (on the order of 50 to 100 MVA) from the high-voltage grid to supply points for medium-voltage networks. The intermediate voltage network serves as a link between the high-voltage and medium-voltage networks but is not always used. Common voltage levels are 25 kV and 50 kV. Due to the high demands for supply reliability, the TS transmission network often has a single fault reserve without energy interruption. However, a single fault reserve with energy interruption can also occur. | kV for the national grid and international connections 220 kV for the national coupling network 150 kV for the regional transmission networks 110 kV for the regional transmission networks Tussenspanningsnetten
Middenspanningstransportnetten | Middenspanningstransportnetten | the high demands for supply reliability, the TS transmission network often has a single fault reserve without energy interruption. However, a single fault reserve with energy interruption can also occur.
Een MS-transportnet brengt een vermogen groter dan 5 MVA over vanuit een onderstation naar een station verder in het net. Zo een station wordt een schakelstation genoemd. Als de afstand van het onderstation naar het schakelstation te groot is, wordt, afhankelijk van de grootte van het transportvermogen, in het schakelstation een regeltransformator geplaatst en wijzigt de naam van schakelstation in regelstation. In een middenspanningstransportnet wordt geen spanning getransformeerd naar laagspanningsniveau. Vanwege de hoge eisen aan de bedrijfszekerheid bestaat het transportnet uit parallel geschakelde kabels met voldoende reserve capaciteit, die zodanig beveiligd zijn, dat het uitvallen van één kabel de energie levering niet onderbreekt (een enkelvoudige storingsreserve zonder energie onderbreking). | An MS transmission network transfers a power greater than 5 MVA from a substation to a station further in the network. Such a station is called a switching station. If the distance from the substation to the switching station is too great, depending on the size of the transmission power, a regulating transformer is placed in the switching station, and the name of the switching station changes to regulating station. In a medium voltage transmission network, voltage is not transformed to a low voltage level. Due to the high demands for operational reliability, the transmission network consists of parallel-connected cables with sufficient reserve capacity, which are secured in such a way that the failure of one cable does not interrupt the energy supply (a single fault reserve without energy interruption). | high demands for supply reliability, the TS transmission network often has a single fault reserve without energy interruption. However, a single fault reserve with energy interruption can also occur. Middenspanningstransportnetten
2.3.2 Distributienet | 2.3.2 Distribution Network | with sufficient reserve capacity, which are secured in such a way that the failure of one cable does not interrupt the energy supply (a single fault reserve without energy interruption).
Een distributienet verspreidt het elektrische vermogen van het onderstation, regelstation of schakelstation naar de aangeslotenen (de uiteindelijke afnemers). Hierbij wordt de spanning (in verschillende stappen) omgezet naar het niveau dat uiteindelijk benodigd is. De laatste transformatiestap tussen middenspanning en laagspanning vindt plaats in het netstation, van waaruit de laagspanningskabels naar de aangeslotenen vetrekken. Lange tijd verspreidde het distributienetwerk het elektrische vermogen enkel vanaf het onderstation, regelstation, schakelstation of netstation naar de klanten. Nu leidt decentrale opwekking, zoals windmolens, WKK’s, micro-WKK’s en zonnepanelen, mogelijk tot teruglevering naar het distributienet, waarna er sprake is van elektriciteitsdistributie in twee richtingen. | A distribution network distributes the electrical power from the substation, control station, or switch station to the connected users (the end consumers). During this process, the voltage is converted (in various steps) to the level that is ultimately required. The final transformation step between medium voltage and low voltage takes place in the network station, from which the low-voltage cables depart to the connected users. For a long time, the distribution network only distributed electrical power from the substation, control station, switch station, or network station to the customers. Now, decentralized generation, such as wind turbines, CHP units, micro-CHP units, and solar panels, may lead to feedback into the distribution network, resulting in two-way electricity distribution. | capacity, which are secured in such a way that the failure of one cable does not interrupt the energy supply (a single fault reserve without energy interruption). 2.3.2 Distribution Network
Middenspanningsdistributienetten | Middenspanningsdistributienetten | to the customers. Now, decentralized generation, such as wind turbines, CHP units, micro-CHP units, and solar panels, may lead to feedback into the distribution network, resulting in two-way electricity distribution.
Deze netten distribueren vanuit de hoog- en tussenspanningsnetten het gevraagde elektrische vermogen naar netstations waar transformatie plaatsvindt naar de laagspanningsnetten. De middenspanningsdistributienetten zijn ontworpen voor spanningsniveaus tussen 1 kV en 25 kV. Het meest gebruikte spanningniveau is 10 kV. Recente ontwikkelingen, met name vanwege de toename van grote concentraties van decentrale opwekking of belasting, zijn de oorzaak dat netten op een hoger spanningsniveau zoals 20 kV kunnen worden ontworpen. Het voordeel van dit spanningsniveau is dat de techniek en de prijs van de commercieel verkrijgbare bedrijfsmiddelen niet veel verschilt van die op 10 kV-niveau, terwijl het dubbele vermogen overgebracht kan worden. | These networks distribute the required electrical power from the high- and medium-voltage networks to substations where transformation to low-voltage networks occurs. The medium-voltage distribution networks are designed for voltage levels between 1 kV and 25 kV. The most commonly used voltage level is 10 kV. Recent developments, particularly due to the increase in large concentrations of decentralized generation or load, have led to the design of networks at a higher voltage level such as 20 kV. The advantage of this voltage level is that the technology and cost of commercially available equipment do not differ much from those at the 10 kV level, while double the power can be transmitted. | the customers. Now, decentralized generation, such as wind turbines, CHP units, micro-CHP units, and solar panels, may lead to feedback into the distribution network, resulting in two-way electricity distribution. Middenspanningsdistributienetten
Het MS-distributienet is meestal als een ring aangelegd. In normaal bedrijf is deze ring niet gesloten. Hierdoor heeft het net een enkelvoudige storingsreserve met energie onderbreking. De energielevering kan meestal door omschakelen en soms alleen met behulp van een aggregaat worden hersteld. | The medium voltage distribution network is usually configured as a ring. In normal operation, this ring is not closed. As a result, the network has a single fault reserve with energy interruption. The power supply can usually be restored by switching and sometimes only with the help of a generator. | voltage level is that the technology and cost of commercially available equipment do not differ much from those at the 10 kV level, while double the power can be transmitted.
Laagspanningsdistributienetten | Laagspanningsdistributienetten | a result, the network has a single fault reserve with energy interruption. The power supply can usually be restored by switching and sometimes only with the help of a generator.
De MS/LS-netstations voeden de laagspanningsdistributienetten, die het elektrische vermogen voor de meeste aangeslotenen verdelen. De laagspanningsnetten zijn ontworpen voor spanningsniveaus tot 1 kV. Het meest gebruikte spanningsniveau is 400 V met een fasespanning van 230 V. | The medium voltage/low voltage substations feed the low voltage distribution networks, which distribute electrical power to most of the connected users. The low voltage networks are designed for voltage levels up to 1 kV. The most commonly used voltage level is 400 V with a phase voltage of 230 V. | result, the network has a single fault reserve with energy interruption. The power supply can usually be restored by switching and sometimes only with the help of a generator. Laagspanningsdistributienetten
Het laagspanningsnet is meestal zonder schakelmogelijkheden aangelegd en er is dan sprake van ‘geen storingsreserve’. Bij een storing is dan de voorziening van de aangeslotenen onderbroken. In bijzondere situaties is het net ontworpen voor herstel van de levering, bijvoorbeeld door inzet van een aggregaat. Dit geldt eveneens voor industriële netten. Afhankelijk van het belang van de continuïteit van de levering kan in het ontwerp rekening worden gehouden met ‘enkelvoudige storingsreserve met energieonderbreking’. De distributienetten in Nederland zijn veelal ook op deze wijze ontworpen. | The low voltage network is usually constructed without switching capabilities, resulting in 'no fault reserve'. In the event of a fault, the supply to the connected users is interrupted. In special situations, the network is designed for the restoration of supply, for example, by using a generator. This also applies to industrial networks. Depending on the importance of the continuity of supply, the design can take into account a 'single fault reserve with power interruption'. Distribution networks in the Netherlands are often designed in this manner as well. | users. The low voltage networks are designed for voltage levels up to 1 kV. The most commonly used voltage level is 400 V with a phase voltage of 230 V.
2.4 Netstructuren | 2.4 Network Structures | the continuity of supply, the design can take into account a 'single fault reserve with power interruption'. Distribution networks in the Netherlands are often designed in this manner as well.
Een netstructuur is het geheel van verbindingen tussen onderstations, regelstations, schakelstations en netstations. Daarnaast verbindt de structuur deze stations aan de uiteindelijke afnemers. De verbindingen zijn doorgaans ondergrondse kabels. Qua uitvoeringsvorm van de netten wordt onderscheid gemaakt in een radiaal net (of stralennet), een ringnet en een vermaasd net. Deze begrippen worden hierna uitgewerkt, evenals het begrip streng. | A network structure is the entirety of connections between substations, control stations, switching stations, and network stations. Additionally, the structure connects these stations to the end consumers. The connections are typically underground cables. In terms of network configurations, a distinction is made between a radial network (or star network), a ring network, and a meshed network. These concepts will be elaborated on below, as well as the concept of a string. | supply, the design can take into account a 'single fault reserve with power interruption'. Distribution networks in the Netherlands are often designed in this manner as well. 2.4 Network Structures
Radiaal net | Radial network | made between a radial network (or star network), a ring network, and a meshed network. These concepts will be elaborated on below, as well as the concept of a string.
Een radiaal net (ook wel stervormig net of stralennet genoemd) heeft een netstructuur waarbij een afnamepunt via één verbinding het netstation bereikt. Er zijn geen omschakelmogelijkheden. Figuur 2.6 geeft een voorbeeld voor een radiaal MS-net. | A radial network (also known as a star network or radial grid) has a network structure where a consumption point reaches the substation through a single connection. There are no switching options. Figure 2.6 provides an example of a radial medium voltage network. | a radial network (or star network), a ring network, and a meshed network. These concepts will be elaborated on below, as well as the concept of a string. Radial network
Een onderbreking in het radiaal net leidt tot uitval van de levering. | An interruption in the radial network leads to a loss of supply. | a network structure where a consumption point reaches the substation through a single connection. There are no switching options. Figure 2.6 provides an example of a radial medium voltage network.
Ringvormig net | Ring network | single connection. There are no switching options. Figure 2.6 provides an example of a radial medium voltage network. An interruption in the radial network leads to a loss of supply.
In een ringvormig net kan een afnamepunt via twee verbindingen het voedende onderstation, regelstation of schakelstation bereiken. In distributienetten worden ringvormige netten meestal radiaal bedreven. Daartoe wordt de ring ongeveer halverwege geopend, in de zogenaamde netopening. Figuur 2.7 geeft een voorbeeld. Een storing in een verbinding leidt dan tot uitval van de levering en verplaatsing van de netopening herstelt de energieonderbreking. In een ringnet kunnen vertakkingen voorkomen. | In a ring network, a load point can reach the feeding substation, control station, or switching station via two connections. In distribution networks, ring networks are usually operated radially. To achieve this, the ring is opened approximately halfway, in the so-called network opening. Figure 2.7 provides an example. A fault in a connection then leads to a supply outage, and relocating the network opening restores the power interruption. Branches can occur in a ring network. | There are no switching options. Figure 2.6 provides an example of a radial medium voltage network. An interruption in the radial network leads to a loss of supply. Ring network
Vermaasd net | Meshed network | provides an example. A fault in a connection then leads to a supply outage, and relocating the network opening restores the power interruption. Branches can occur in a ring network.
In een vermaasd net kan een afnamepunt via meer dan twee verbindingen het voedende onderstation, regelstation of schakelstation bereiken. Indien een vermaasd net radiaal wordt bedreven, worden de netopeningen vaak gesitueerd in knooppunten waar meerdere verbindingen samenkomen. Figuur 2.9 geeft een voorbeeld. | In a meshed network, a consumption point can reach the feeding substation, control station, or switching station via more than two connections. If a meshed network is operated radially, the network openings are often situated at nodes where multiple connections converge. Figure 2.9 provides an example. | example. A fault in a connection then leads to a supply outage, and relocating the network opening restores the power interruption. Branches can occur in a ring network. Meshed network
Een onderbreking in een verbinding leidt tot uitval van de levering en verplaatsing van de netopening herstelt de energieonderbreking. | An interruption in a connection leads to a delivery outage, and relocating the network opening restores the power interruption. | station via more than two connections. If a meshed network is operated radially, the network openings are often situated at nodes where multiple connections converge. Figure 2.9 provides an example.
Uitloper | Uitloper | at nodes where multiple connections converge. Figure 2.9 provides an example. An interruption in a connection leads to a delivery outage, and relocating the network opening restores the power interruption.
In een ringvormig of vermaasd net kan men radiale kabeldelen aantreffen. Deze worden meestal aangeduid met de naam ‘uitlopers‘. | In a ring-shaped or meshed network, one can encounter radial cable sections. These are usually referred to as 'spurs'. | nodes where multiple connections converge. Figure 2.9 provides an example. An interruption in a connection leads to a delivery outage, and relocating the network opening restores the power interruption. Uitloper
Een onderbreking in een uitloper leidt tot uitval van de levering. | An interruption in a spur leads to a loss of supply. | outage, and relocating the network opening restores the power interruption. Uitloper In a ring-shaped or meshed network, one can encounter radial cable sections. These are usually referred to as 'spurs'.
Streng | Streng | In a ring-shaped or meshed network, one can encounter radial cable sections. These are usually referred to as 'spurs'. An interruption in a spur leads to a loss of supply.
Een streng is een keten van primaire objecten die met één gemeenschappelijke beveiliging afgeschakeld kunnen worden. | A strand is a chain of primary objects that can be disconnected with a single common protection. | a ring-shaped or meshed network, one can encounter radial cable sections. These are usually referred to as 'spurs'. An interruption in a spur leads to a loss of supply. Streng
In de volgende paragrafen worden de structuren besproken van transportnetten (HS, TS en MS) en distributienetten (MS en LS). Ook wordt kort ingegaan op een gecombineerde structuur voor MS-netten met meerdere spanningsniveaus. | The following paragraphs discuss the structures of transmission networks (HS, TS, and MS) and distribution networks (MS and LS). Additionally, a combined structure for MS networks with multiple voltage levels is briefly addressed. | 'spurs'. An interruption in a spur leads to a loss of supply. Streng A strand is a chain of primary objects that can be disconnected with a single common protection.
2.4.1 Structuur van transportnetten | 2.4.1 Structure of Transmission Networks | discuss the structures of transmission networks (HS, TS, and MS) and distribution networks (MS and LS). Additionally, a combined structure for MS networks with multiple voltage levels is briefly addressed.
Transportnetten zijn meestal zodanig ontworpen dat zij, zelfs in geval van een storing, zonder onderbreking de elektrische energie leveren. Hierbij is sprake van een enkelvoudige storingsreserve zonder energieonderbreking. Het net blijft bij storing van een enkele component goed functioneren en is daarmee n-1 veilig. Het net heeft meerdere wegen van de voedingsbron naar de belastingen. Dit stelt eisen aan de beveiliging, die ervoor moet zorgen dat de gestoorde component direct afgeschakeld wordt, waarbij de elektriciteitsvoorziening zonder onderbreking gehandhaafd blijft. Figuur 2.3 toont een vermaasd 50 kV transportnet met HS-voeding en TS/MS-onderstations. De kleuren geven het spanningsniveau aan (rood: HS; groen: TS; zwart: MS). | Transmission networks are usually designed in such a way that they deliver electrical energy without interruption, even in the event of a fault. This involves a single fault reserve without energy interruption. The network continues to function well in the event of a single component failure and is therefore n-1 secure. The network has multiple paths from the power source to the loads. This imposes requirements on the protection system, which must ensure that the faulty component is immediately disconnected, maintaining the electricity supply without interruption. Figure 2.3 shows a meshed 50 kV transmission network with HS supply and TS/MS substations. The colors indicate the voltage level (red: HS; green: TS; black: MS). | networks (HS, TS, and MS) and distribution networks (MS and LS). Additionally, a combined structure for MS networks with multiple voltage levels is briefly addressed. 2.4.1 Structure of Transmission Networks
Figuur 2.3 Vermaasd 50-kV-transportnet | Figure 2.3 Meshed 50 kV Transmission Network | supply without interruption. Figure 2.3 shows a meshed 50 kV transmission network with HS supply and TS/MS substations. The colors indicate the voltage level (red: HS; green: TS; black: MS).
In bijzondere situaties komt het voor dat een onderstation aan hoogspanningszijde geen railsysteem bevat maar dat de transportverbindingen van het voedende net rechtstreeks op de hoogspanningszijde van de transformator zijn aangesloten. In deze netten wordt soms toegestaan dat de energielevering wordt onderbroken bij een enkelvoudige storing (zie figuur 2.4). Deze situatie komt zowel op TS- als op HS-niveau voor. Deze configuratie wordt ook wel een ‘transformator op een steeltje’ genoemd. | In special situations, it occurs that a substation on the high-voltage side does not contain a busbar system, but the transmission connections from the feeding network are directly connected to the high-voltage side of the transformer. In these networks, it is sometimes allowed for the power supply to be interrupted in the event of a single fault (see figure 2.4). This situation occurs at both TS and HS levels. This configuration is also known as a 'transformer on a stick.' | meshed 50 kV transmission network with HS supply and TS/MS substations. The colors indicate the voltage level (red: HS; green: TS; black: MS). Figure 2.3 Meshed 50 kV Transmission Network
Figuur 2.4 Parallel voedende kabels in het 50-kV-transportnet | Figure 2.4 Parallel feeder cables in the 50 kV transmission network | in the event of a single fault (see figure 2.4). This situation occurs at both TS and HS levels. This configuration is also known as a 'transformer on a stick.'
Op MS-niveau zijn de transportnetten meestal niet vermaasd. Zij bestaan uit twee of meer parallelle kabelverbindingen van een onderstation naar een schakelstation. In het schakelstation kan een regeltransformator worden toegepast om het spanningsverlies, dat ontstaat doordat een vermogen over een grote afstand moet worden getransporteerd, te compenseren. De toegepaste spanning is meestal 20 of 10 kV (zie Figuur 2.5). | At the medium voltage (MV) level, the transmission networks are usually not meshed. They consist of two or more parallel cable connections from a substation to a switching station. In the switching station, a regulating transformer can be used to compensate for the voltage drop that occurs because power needs to be transmitted over a long distance. The applied voltage is usually 20 or 10 kV (see Figure 2.5). | situation occurs at both TS and HS levels. This configuration is also known as a 'transformer on a stick.' Figure 2.4 Parallel feeder cables in the 50 kV transmission network
Figuur 2.5 Parallel voedende kabels in het 10-kV-transportnet | Figure 2.5 Parallel feeding cables in the 10 kV transmission network | to compensate for the voltage drop that occurs because power needs to be transmitted over a long distance. The applied voltage is usually 20 or 10 kV (see Figure 2.5).
2.4.2 Structuur van middenspanningsdistributienetten | 2.4.2 Structure of Medium Voltage Distribution Networks | to be transmitted over a long distance. The applied voltage is usually 20 or 10 kV (see Figure 2.5). Figure 2.5 Parallel feeding cables in the 10 kV transmission network
Het toegepaste spanningsniveau bij middenspanningsdistributienetten is meestal 10 kV. In sommige netten wordt ook 20 kV toegepast. De keuze voor een bepaald spanningsniveau is meestal historisch bepaald. De meeste MS-distributienetten zijn ringvormig of vermaasd aangelegd, maar worden radiaal bedreven. Hieronder worden drie structuren van radiaal bedreven distributienetten toegelicht. | The applied voltage level in medium voltage distribution networks is usually 10 kV. In some networks, 20 kV is also used. The choice for a specific voltage level is usually historically determined. Most medium voltage distribution networks are designed in a ring or meshed configuration but are operated radially. Below, three structures of radially operated distribution networks are explained. | The applied voltage is usually 20 or 10 kV (see Figure 2.5). Figure 2.5 Parallel feeding cables in the 10 kV transmission network 2.4.2 Structure of Medium Voltage Distribution Networks
In het onderstation zijn de strengen van het MS-distributienet door middel van een vermogenschakelaar (symbool X in de schema’s) en vervolgens via een lastscheider met het voedende MS-railsysteem van het OS verbonden. Ieder achterliggend netstation in de streng heeft lastscheiders voor de inkomende en de uitgaande kabels. | In the substation, the branches of the medium voltage distribution network are connected to the feeding medium voltage bus system of the substation through a circuit breaker (symbol X in the diagrams) and then via a load switch. Each downstream network station in the branch has load switches for the incoming and outgoing cables. | usually historically determined. Most medium voltage distribution networks are designed in a ring or meshed configuration but are operated radially. Below, three structures of radially operated distribution networks are explained.
Radiale netstructuur | Radial network structure | a circuit breaker (symbol X in the diagrams) and then via a load switch. Each downstream network station in the branch has load switches for the incoming and outgoing cables.
Het radiale net van figuur 2.6 is de meest eenvoudige uitvoering. In dit net is geen storingsreserve aanwezig. Vanuit het onderstation vertrekken strengen geografisch in alle richtingen van het verzorgingsgebied. Deze uitvoering wordt gebruikt in gebieden met lage concentraties van klanten. De netten zijn daar vaak vrij uitgestrekt. In deze uitvoering zijn er geen mogelijkheden voor omschakelen in geval van een storing. In wezen zijn de strengen uitlopers. Deze bevatten veelal meer netstations dan de uitlopers in ringvormige netten in de stedelijke omgeving. Deze structuur wordt in Nederland niet vaak toegepast. | The radial network in figure 2.6 is the simplest configuration. This network does not have any fault reserve. From the substation, feeders extend geographically in all directions of the service area. This configuration is used in areas with low customer concentrations. The networks there are often quite extensive. In this configuration, there are no options for switching in case of a fault. Essentially, the feeders are dead ends. These often contain more network stations than the dead ends in ring-shaped networks in urban areas. This structure is not often used in the Netherlands. | (symbol X in the diagrams) and then via a load switch. Each downstream network station in the branch has load switches for the incoming and outgoing cables. Radial network structure
Figuur 2.6 Radiaal 10-kV-distributienet; voeding vanuit één onderstation; geen storingsreserve | Figure 2.6 Radial 10 kV distribution network; supply from one substation; no fault reserve | the feeders are dead ends. These often contain more network stations than the dead ends in ring-shaped networks in urban areas. This structure is not often used in the Netherlands.
Ringvormige netstructuur | Ring-shaped network structure | ends in ring-shaped networks in urban areas. This structure is not often used in the Netherlands. Figure 2.6 Radial 10 kV distribution network; supply from one substation; no fault reserve
De meeste distributienetten worden zodanig aangelegd dat de uiteinden van de strengen elkaar ontmoeten en dat een ringvormige structuur ontstaat (zie figuur 2.7). Ergens in de ring wordt een lastscheider geopend (de netopening). Op deze manier ontstaat een radiaal of open bedreven ringvormige structuur. Op de grens van de verzorgingsgebieden van twee onderstations kan ook een verbinding gemaakt worden. De netopening op die plaats wordt dan netscheiding genoemd. | Most distribution networks are constructed in such a way that the ends of the branches meet, forming a ring-shaped structure (see figure 2.7). Somewhere in the ring, a load switch is opened (the network opening). This creates a radial or open-operated ring-shaped structure. A connection can also be made at the boundary of the service areas of two substations. The network opening at that location is then called a network separation. | networks in urban areas. This structure is not often used in the Netherlands. Figure 2.6 Radial 10 kV distribution network; supply from one substation; no fault reserve Ring-shaped network structure
Figuur 2.7 Ringvormig 10-kV-distributienet; enkelvoudige storingsreserve | Figure 2.7 Ring-shaped 10 kV distribution network; single fault reserve | ring-shaped structure. A connection can also be made at the boundary of the service areas of two substations. The network opening at that location is then called a network separation.
Hoofdring, subring en uitloper | Main ring, sub-ring, and spur | boundary of the service areas of two substations. The network opening at that location is then called a network separation. Figure 2.7 Ring-shaped 10 kV distribution network; single fault reserve
Bij netten met deze structuur wordt vaak gesproken over hoofdring, subring en uitloper. Een hoofdring begint bij het onderstation en loopt via een netopening terug naar het onderstation. De hoofdring bestaat dan uit twee strengen. | In networks with this structure, terms like main ring, sub-ring, and spur are often used. A main ring starts at the substation and loops back to the substation via a network opening. The main ring then consists of two branches. | of two substations. The network opening at that location is then called a network separation. Figure 2.7 Ring-shaped 10 kV distribution network; single fault reserve Main ring, sub-ring, and spur
Een aftakking van een hoofdring, die aan het uiteinde door het sluiten van een netopening kan worden verbonden met dezelfde voedende kabel, wordt ook wel met de term subring aangeduid. | A branch of a main ring, which at the end can be connected to the same feeder cable by closing a network opening, is also referred to as a subring. | and spur are often used. A main ring starts at the substation and loops back to the substation via a network opening. The main ring then consists of two branches.
Een aftakking van een hoofdring of subring, waarvan het uiteinde niet door het sluiten van een netopening kan worden verbonden met een andere voedende kabel, wordt een uitloper genoemd. Deze zijn afgebeeld in figuur 2.8. | A branch of a main ring or subring, whose end cannot be connected to another feeder cable by closing a network opening, is called a spur. These are depicted in figure 2.8. | A branch of a main ring, which at the end can be connected to the same feeder cable by closing a network opening, is also referred to as a subring.
Figuur 2.8 Distributienet met hoofdring, subring en uitloper | Figure 2.8 Distribution network with main ring, subring, and spur | of a main ring or subring, whose end cannot be connected to another feeder cable by closing a network opening, is called a spur. These are depicted in figure 2.8.
In praktijk bevat een hoofdring ongeveer 20 tot 40 netstations. Een subring bevat ongeveer 5 tot 10 netstations. Uitlopers in ringvormige en vermaasde netten bevatten 1 tot 3 netstations. De kabels van subringen en uitlopers hebben meestal een kleinere geleiderdiameter dan de kabels in de hoofdring. | In practice, a main ring contains approximately 20 to 40 network stations. A subring contains about 5 to 10 network stations. Spurs in ring-shaped and meshed networks contain 1 to 3 network stations. The cables of subrings and spurs usually have a smaller conductor diameter than the cables in the main ring. | connected to another feeder cable by closing a network opening, is called a spur. These are depicted in figure 2.8. Figure 2.8 Distribution network with main ring, subring, and spur
Vermaasde netstructuur | Meshed network structure | in ring-shaped and meshed networks contain 1 to 3 network stations. The cables of subrings and spurs usually have a smaller conductor diameter than the cables in the main ring.
In de ringvormige netten van figuur 2.7 is sprake van een enkelvoudige storingsreserve met storingsonderbreking. Het voordeel van de open bedreven ringvormige structuur is dat in geval van storingen na isolatie van de fout door sluiten van de netopening kan worden omgeschakeld naar een andere streng, zodat de elektriciteitsvoorziening relatief snel kan worden hersteld. Voorwaarde is dat de capaciteit van de strengen toereikend is om het vermogen van een over te nemen streng te voeden. | In the ring-shaped networks of figure 2.7, there is a single fault reserve with fault interruption. The advantage of the open-operated ring-shaped structure is that in case of faults, after isolating the fault by closing the network opening, it can be switched to another section, so that the power supply can be restored relatively quickly. The condition is that the capacity of the sections is sufficient to feed the power of the section being taken over. | meshed networks contain 1 to 3 network stations. The cables of subrings and spurs usually have a smaller conductor diameter than the cables in the main ring. Meshed network structure
De ringvormige structuur van figuur 2.7 kan nog verder worden uitgebreid, zodanig dat meerdere strengen vanuit eenzelfde of diverse onderstations elkaar ontmoeten in punten waar netopeningen zijn aangebracht. Op die manier ontstaat een vermaasde structuur, waar in geval van storingen meer omschakelmogelijkheden zijn dan in een net met ringvormige structuur. Het voordeel van deze structuur is dat het vermogen van zwaar belaste delen van het net kan worden verdeeld over meerdere strengen. Met name in grote steden of industriegebieden kan dit wenselijk zijn. Figuur 2.9 illustreert dit. | The ring-shaped structure of figure 2.7 can be further expanded so that multiple strands from the same or different substations meet at points where network openings are created. In this way, a meshed structure is formed, providing more switching options in case of failures than a network with a ring-shaped structure. The advantage of this structure is that the power of heavily loaded parts of the network can be distributed over multiple strands. This can be particularly desirable in large cities or industrial areas. Figure 2.9 illustrates this. | that the power supply can be restored relatively quickly. The condition is that the capacity of the sections is sufficient to feed the power of the section being taken over.
Figuur 2.9 Vermaasd 10-kV-distributienet; enkelvoudige storingsreserve | Figure 2.9 Meshed 10 kV distribution network; single fault reserve | the power of heavily loaded parts of the network can be distributed over multiple strands. This can be particularly desirable in large cities or industrial areas. Figure 2.9 illustrates this.
Het komt bijna nooit voor dat ringvormige of vermaasde distributienetten vermaasd bedreven worden. In vermaasd bedrijf zou een kortsluiting namelijk vanuit meerdere richtingen gevoed kunnen worden. De kortsluitstroom moet dan op twee of meer plaatsen worden uitgeschakeld, hetgeen de beveiliging complex en kostbaar maakt. | It is almost never the case that ring-shaped or meshed distribution networks are operated in a meshed manner. In meshed operation, a short circuit could be fed from multiple directions. The short-circuit current would then need to be interrupted at two or more locations, which makes the protection complex and expensive. | be distributed over multiple strands. This can be particularly desirable in large cities or industrial areas. Figure 2.9 illustrates this. Figure 2.9 Meshed 10 kV distribution network; single fault reserve
In tegenstelling tot de transportnetten zijn de MS-distributienetten met de ringvormige of vermaasde structuur niet geschikt voor n-1 veilige bedrijfsvoering maar alleen voor een enkelvoudige storingsreserve met energieonderbreking. De beveiliging is ontworpen om in geval van een kortsluiting in een van de bedrijfsmiddelen van een streng die gehele streng uit te schakelen. | In contrast to the transmission networks, the medium-voltage distribution networks with a ring or meshed structure are not suitable for n-1 secure operation but only for a single fault reserve with energy interruption. The protection is designed to shut down the entire section in the event of a short circuit in one of the assets of a section. | a short circuit could be fed from multiple directions. The short-circuit current would then need to be interrupted at two or more locations, which makes the protection complex and expensive.
Hoofdring, subring en uitloper zijn meestal op hun voedingspunt beveiligd. In geval van een enkelvoudige storing zal de streng, waarin zich de gestoorde component bevindt, in zijn geheel worden afgeschakeld. Indien de storing zich in een beveiligde subring of uitloper bevindt, zal alleen dat gedeelte selectief worden afgeschakeld. Na het isoleren van de defecte component (door deze vrij te schakelen) en het verplaatsen van de netopeningen kan de elektriciteitsvoorziening worden hersteld. Het faal- en herstelproces is nader beschreven in hoofdstuk 12 (betrouwbaarheid). | Main ring, subring, and spur are usually protected at their feed point. In the event of a single fault, the entire section containing the faulty component will be shut down. If the fault is in a protected subring or spur, only that section will be selectively shut down. After isolating the defective component (by disconnecting it) and relocating the network openings, the power supply can be restored. The failure and recovery process is further described in Chapter 12 (reliability). | fault reserve with energy interruption. The protection is designed to shut down the entire section in the event of a short circuit in one of the assets of a section.
2.4.3 Onderzoek naar nieuwe netstructuren | 2.4.3 Research into New Network Structures | isolating the defective component (by disconnecting it) and relocating the network openings, the power supply can be restored. The failure and recovery process is further described in Chapter 12 (reliability).
Met de sterke groei van de belasting in stedelijke omgeving wordt gezocht naar methodes om bestaande MS-netten zodanig uit te breiden dat zij voorbereid zijn voor de toekomstige eisen voor energietransport. De te verwachten ontwikkeling van de belasting in de jaren van 2010 tot 2025 omvat: | With the strong growth of the load in urban environments, methods are being sought to expand existing medium voltage networks in such a way that they are prepared for future energy transport requirements. The expected development of the load from 2010 to 2025 includes: | it) and relocating the network openings, the power supply can be restored. The failure and recovery process is further described in Chapter 12 (reliability). 2.4.3 Research into New Network Structures
een autonome groei van 2% per jaar | an autonomous growth of 2% per year | to expand existing medium voltage networks in such a way that they are prepared for future energy transport requirements. The expected development of the load from 2010 to 2025 includes:
de opkomst van de elektrische auto, leidend tot een verdubbeling van het verbruik per huishouden | the rise of the electric car, leading to a doubling of consumption per household | such a way that they are prepared for future energy transport requirements. The expected development of the load from 2010 to 2025 includes: an autonomous growth of 2% per year
de opkomst van de warmtepompen, leidend tot een verdubbeling van het verbruik per huishouden | the rise of heat pumps, leading to a doubling of consumption per household | development of the load from 2010 to 2025 includes: an autonomous growth of 2% per year the rise of the electric car, leading to a doubling of consumption per household
de groei van de decentrale opwekking, naar verwachting leidend tot 20% toename van het maximale verbruik | the growth of decentralized generation, expected to lead to a 20% increase in maximum consumption | 2% per year the rise of the electric car, leading to a doubling of consumption per household the rise of heat pumps, leading to a doubling of consumption per household
een toenemende prioriteit voor duurzaam en maatschappelijk verantwoord ondernemen. | an increasing priority for sustainable and socially responsible business practices. | per household the rise of heat pumps, leading to a doubling of consumption per household the growth of decentralized generation, expected to lead to a 20% increase in maximum consumption
De mogelijkheden om de bestaande MS-netten in stedelijk gebied uit te breiden zijn in toenemende mate beperkt. Bij het zoeken naar de oplossingsrichting moet ook de flexibiliteit van het distributienet ruime aandacht krijgen. Daarom moeten oplossingen gevonden worden waarmee met weinig extra maatregelen het bestaande net beter benut kan worden. Een mogelijkheid is het creëren van extra steunpunten in het MS-net, die gevoed worden vanuit een vermaasd bedreven MS-transportnet. Hierbij ontstaan kortere radiaal bedreven MS-structuren en nemen de flexibiliteit en de capaciteit toe. Ten opzichte van de traditionele netstructuren omvat de toegenomen flexibiliteit onder andere het sneller aansluiten van nieuwe klanten, het faciliteren van decentrale opwekking en het beter bestand zijn tegen storingen. Storingen moeten ook sneller opgelost kunnen worden dan bij de traditionele netstructuren. | The possibilities for expanding existing medium-voltage (MV) networks in urban areas are increasingly limited. When seeking solutions, the flexibility of the distribution network must also receive considerable attention. Therefore, solutions must be found that allow the existing network to be better utilized with minimal additional measures. One possibility is to create additional support points in the MV network, which are fed from a meshed-operated MV transport network. This results in shorter radial-operated MV structures, increasing both flexibility and capacity. Compared to traditional network structures, the increased flexibility includes faster connection of new customers, facilitating decentralized generation, and being more resilient to disruptions. Disruptions must also be resolved more quickly than with traditional network structures. | doubling of consumption per household the growth of decentralized generation, expected to lead to a 20% increase in maximum consumption an increasing priority for sustainable and socially responsible business practices.
In de te realiseren gecombineerde netstructuur dienen onder meer de volgende zaken mogelijk te zijn: | In the combined network structure to be realized, the following aspects, among others, must be possible: | the increased flexibility includes faster connection of new customers, facilitating decentralized generation, and being more resilient to disruptions. Disruptions must also be resolved more quickly than with traditional network structures.
grote capaciteit | large capacity | to disruptions. Disruptions must also be resolved more quickly than with traditional network structures. In the combined network structure to be realized, the following aspects, among others, must be possible:
tweerichtingsverkeer van het elektrisch vermogen | bidirectional flow of electrical power | Disruptions must also be resolved more quickly than with traditional network structures. In the combined network structure to be realized, the following aspects, among others, must be possible: large capacity
monitoring en comptabel meten op afstand | remote monitoring and accounting measurement | more quickly than with traditional network structures. In the combined network structure to be realized, the following aspects, among others, must be possible: large capacity bidirectional flow of electrical power
afstandsbediening van schakelaars en scheiders | remote control of switches and disconnectors | network structures. In the combined network structure to be realized, the following aspects, among others, must be possible: large capacity bidirectional flow of electrical power remote monitoring and accounting measurement
verlaging van de netverliezen | reduction of grid losses | structure to be realized, the following aspects, among others, must be possible: large capacity bidirectional flow of electrical power remote monitoring and accounting measurement remote control of switches and disconnectors
verlaging van de hoeveelheid storingsminuten | reduction of the number of outage minutes | the following aspects, among others, must be possible: large capacity bidirectional flow of electrical power remote monitoring and accounting measurement remote control of switches and disconnectors reduction of grid losses
sneller aansluiten van nieuwe klanten. | faster connection of new customers. | possible: large capacity bidirectional flow of electrical power remote monitoring and accounting measurement remote control of switches and disconnectors reduction of grid losses reduction of the number of outage minutes
Het idee over de configuratie van de gecombineerde netstructuur is hierna uitgewerkt. De gecombineerde netstructuur bestaat uit een gesloten transportring en gesloten of open bedreven subringen tussen de stations van de transportring. Dit concept is nieuw en kan in zwaar belaste netten in stedelijke omgeving goed worden toegepast (Karakoc, 2009). Het spanningsniveau van de transportring kan hoger liggen dan dat van de subringen. | The idea regarding the configuration of the combined network structure is elaborated below. The combined network structure consists of a closed transport ring and closed or open-operated sub-rings between the stations of the transport ring. This concept is new and can be effectively applied in heavily loaded networks in urban environments (Karakoc, 2009). The voltage level of the transport ring can be higher than that of the sub-rings. | of electrical power remote monitoring and accounting measurement remote control of switches and disconnectors reduction of grid losses reduction of the number of outage minutes faster connection of new customers.
Figuur 2.10 Gecombineerde 20/10 kV structuur | Figure 2.10 Combined 20/10 kV structure | new and can be effectively applied in heavily loaded networks in urban environments (Karakoc, 2009). The voltage level of the transport ring can be higher than that of the sub-rings.
Het voorbeeld in figuur 2.10 toont een gesloten ringvormig 20 kV-transportnet (groen) met 6 schakelstations of netstations (MSR 1 t/m MSR 6). Het transportnet is ontworpen op een enkelvoudige storingsreserve zonder energieonderbreking, zodat een van de transportverbindingen buiten bedrijf kan zijn. De beveiliging is vergelijkbaar met die van een MS-transportnet. Het distributiegedeelte wordt gevormd door strengen die telkens tussen twee schakelstations of netstations zijn aangebracht. In deze strengen kunnen al dan niet netopeningen zijn aangebracht. Indien er geen netopeningen zijn aangebracht, zoals in de bovenste twee vermaasde 20 kV-strengen tussen MSR 1 en MSR 2 en tussen MSR 2 en MSR 3 (groen), worden dezelfde eisen aan de beveiliging en vermogenschakelaars gesteld als bij vermaasd bedreven transportnetten. Het transportnet voedt ook vier open bedreven subringen op 10 kV-niveau (zwart). | The example in figure 2.10 shows a closed ring-shaped 20 kV transport network (green) with 6 switching stations or substations (MSR 1 through MSR 6). The transport network is designed with a single fault reserve without energy interruption, so that one of the transport connections can be out of service. The protection is similar to that of an MV transport network. The distribution section is formed by feeders that are installed between two switching stations or substations. These feeders may or may not have network openings. If there are no network openings, as in the upper two meshed 20 kV feeders between MSR 1 and MSR 2 and between MSR 2 and MSR 3 (green), the same requirements for protection and circuit breakers apply as in meshed operated transport networks. The transport network also feeds four open operated sub-rings at the 10 kV level (black). | in heavily loaded networks in urban environments (Karakoc, 2009). The voltage level of the transport ring can be higher than that of the sub-rings. Figure 2.10 Combined 20/10 kV structure
De flexibiliteit wordt vergroot indien de schakelstations en netstations op afstand kunnen worden bemeten en bestuurd. In dit voorbeeld hebben het 20 kV-transportnet en de 20 kV-subringen een enkelvoudige storingsreserve zonder energieonderbreking. De open bedreven subringen op 10 kV-niveau hebben een enkelvoudige storingsreserve met energieonderbreking. | Flexibility is increased if the switching stations and network stations can be remotely measured and controlled. In this example, the 20 kV transmission network and the 20 kV sub-rings have a single fault reserve without energy interruption. The open-operated sub-rings at the 10 kV level have a single fault reserve with energy interruption. | the same requirements for protection and circuit breakers apply as in meshed operated transport networks. The transport network also feeds four open operated sub-rings at the 10 kV level (black).
2.4.4 Structuur van laagspanningsdistributienetten | 2.4.4 Structure of Low Voltage Distribution Networks | network and the 20 kV sub-rings have a single fault reserve without energy interruption. The open-operated sub-rings at the 10 kV level have a single fault reserve with energy interruption.
Laagspanningsnetten hebben als functie alle klanten met een laagspanningsaansluiting voor vermogens tot 300 kVA (bij 3 fasen, 400 V, maximaal 435 A) op het elektriciteitsnet aan te sluiten. De netopbouw is sterk afhankelijk van de lokale situatie. Laagspanningsnetten zijn in principe vanaf een netstation stervormig aangelegd en hebben meestal geen verbinding met een ander netstation. Er bestaan echter ook situaties van ringvormige en vermaasde structuur. | Low voltage networks function to connect all customers with a low voltage connection for capacities up to 300 kVA (at 3 phases, 400 V, maximum 435 A) to the electricity grid. The network configuration is highly dependent on the local situation. In principle, low voltage networks are radially laid out from a substation and usually have no connection to another substation. However, there are also situations with ring-shaped and meshed structures. | a single fault reserve without energy interruption. The open-operated sub-rings at the 10 kV level have a single fault reserve with energy interruption. 2.4.4 Structure of Low Voltage Distribution Networks
Figuur 2.11 illustreert de radiale structuur. De netstations zijn aangegeven met dichte vierkanten. Er is sprake van geen storingsreserve. Eventueel kan een generatorwagen worden ingezet om de levering te herstellen. | Figure 2.11 illustrates the radial structure. The substations are indicated with solid squares. There is no fault reserve. If necessary, a generator truck can be used to restore the supply. | In principle, low voltage networks are radially laid out from a substation and usually have no connection to another substation. However, there are also situations with ring-shaped and meshed structures.
Figuur 2.11 Radiaal LS-net; voeding vanuit één netstation; geen storingsreserve | Figure 2.11 Radial LV network; supply from one substation; no fault reserve | Figure 2.11 illustrates the radial structure. The substations are indicated with solid squares. There is no fault reserve. If necessary, a generator truck can be used to restore the supply.
In oudere stedelijke distributienetten komen soms vermaasde LS-netten voor, die ook vermaasd worden bedreven. Figuur 2.12 geeft een voorbeeld hiervan. Bij deze netten moeten de voedende distributiestations zich in dezelfde MS-streng bevinden. | In older urban distribution networks, meshed LV networks are sometimes found, which are also operated in a meshed manner. Figure 2.12 provides an example of this. In these networks, the feeding distribution substations must be located in the same MV string. | squares. There is no fault reserve. If necessary, a generator truck can be used to restore the supply. Figure 2.11 Radial LV network; supply from one substation; no fault reserve
Figuur 2.12 Vermaasd LS-net; voeding vanuit meerdere netstations; geen storingsreserve | Figure 2.12 Meshed LV network; supply from multiple substations; no fault reserve | which are also operated in a meshed manner. Figure 2.12 provides an example of this. In these networks, the feeding distribution substations must be located in the same MV string.
In het algemeen leidt vermaasd bedrijf tot een betere spanningshuishouding en tot minder netverlies. Een groot nadeel hierbij is dat dit in geval van een storing leidt tot grotere kortsluitstromen. Er is ook een complexere beveiliging nodig. Er is daarom een trend om nieuwe laagspanningsnetten radiaal aan te leggen. | In general, meshed operation leads to better voltage regulation and less network loss. A major disadvantage, however, is that in the event of a fault, it results in larger short-circuit currents. More complex protection is also required. Therefore, there is a trend to lay out new low-voltage networks radially. | example of this. In these networks, the feeding distribution substations must be located in the same MV string. Figure 2.12 Meshed LV network; supply from multiple substations; no fault reserve
2.4.5 Stations | 2.4.5 Stations | in the event of a fault, it results in larger short-circuit currents. More complex protection is also required. Therefore, there is a trend to lay out new low-voltage networks radially.
In alle netten, op plaatsen waar verbindingen samenkomen of worden opgesplitst en waar transformatie naar een ander spanningsniveau plaatsvindt, komen stations voor. Afhankelijk van de functie van het net en de impact van uitval op de energievoorziening is in het ontwerp veel tot weinig redundantie ingebouwd. Ook de mate van stationsautomatisering en de omvang van de beveiliging hangt af van de functie. De belangrijkste stations zijn onderstation (OS), schakelstation (SS), regelstation (RS) en netstation. Een onderstation wordt gevoed vanuit het HS- of TS-net en voedt een MS-transportnet of MS-distributienet. Een schakelstation en een regelstation worden gevoed vanuit het MS-transportnet en voeden een MS-distributienet. Een netstation wordt gevoed vanuit het MS-distributienet en voedt een LS-net. Deze stations worden in dit hoofdstuk verder behandeld. | In all networks, at places where connections converge or split and where transformation to a different voltage level occurs, stations are present. Depending on the function of the network and the impact of outages on the power supply, the design incorporates varying levels of redundancy. The degree of station automation and the extent of protection also depend on the function. The main stations are substation (OS), switching station (SS), control station (RS), and network station. A substation is fed from the HV or EHV network and supplies an MV transmission network or MV distribution network. A switching station and a control station are fed from the MV transmission network and supply an MV distribution network. A network station is fed from the MV distribution network and supplies an LV network. These stations are further discussed in this chapter. | event of a fault, it results in larger short-circuit currents. More complex protection is also required. Therefore, there is a trend to lay out new low-voltage networks radially. 2.4.5 Stations
Railsysteem | Railsysteem | network and supply an MV distribution network. A network station is fed from the MV distribution network and supplies an LV network. These stations are further discussed in this chapter.
Elk station is gebouwd rondom een railsysteem. Een railsysteem bestaat uit drie (voor elke fase één) stevig uitgevoerde, aluminium of koperen geleiders, waarop alle bedrijfsmiddelen van in- en uitgaande verbindingen zijn aangesloten. In open installaties wordt vaak aluminium buizen voor de rails toegepast en in gesloten installaties koperen strips. | Each station is built around a busbar system. A busbar system consists of three robustly constructed aluminum or copper conductors (one for each phase), to which all equipment for incoming and outgoing connections is attached. In open installations, aluminum tubes are often used for the busbars, while in closed installations, copper strips are used. | and supply an MV distribution network. A network station is fed from the MV distribution network and supplies an LV network. These stations are further discussed in this chapter. Railsysteem
Op basis van eisen ten aanzien van bedrijfsvoering, betrouwbaarheid en de kosten voor installatie en onderhoud wordt gekozen uit enkel- en dubbelrailsystemen. | Based on requirements regarding operation, reliability, and installation and maintenance costs, a choice is made between single and double busbar systems. | to which all equipment for incoming and outgoing connections is attached. In open installations, aluminum tubes are often used for the busbars, while in closed installations, copper strips are used.
Figuur 2.13 Enkelrailsysteem | Figure 2.13 Single Busbar System | busbars, while in closed installations, copper strips are used. Based on requirements regarding operation, reliability, and installation and maintenance costs, a choice is made between single and double busbar systems.
Het enkelrailsysteem, zoals afgebeeld in figuur 2.13, is de meest eenvoudige uitvoeringsvorm. Het grootste nadeel van dit systeem is dat bij onderhoud of storing aan het railsysteem geen reserve aanwezig is. Wel kan het railsysteem in secties worden opgedeeld. De secties zijn dan met een schakelaar met elkaar verbonden. In het geval van een regelstation zijn de twee railsecties via een regeltransformator gekoppeld (zie figuur 2.24). Enkelrailsystemen worden toegepast in MS- en LS distributienetten. | The single busbar system, as shown in figure 2.13, is the simplest configuration. The biggest disadvantage of this system is that there is no backup available during maintenance or failure of the busbar system. However, the busbar system can be divided into sections. These sections are then connected to each other with a switch. In the case of a control station, the two busbar sections are connected via a regulating transformer (see figure 2.24). Single busbar systems are used in medium voltage (MV) and low voltage (LV) distribution networks. | copper strips are used. Based on requirements regarding operation, reliability, and installation and maintenance costs, a choice is made between single and double busbar systems. Figure 2.13 Single Busbar System
Figuur 2.14 Dubbelrailsysteem | Figure 2.14 Double Busbar System | control station, the two busbar sections are connected via a regulating transformer (see figure 2.24). Single busbar systems are used in medium voltage (MV) and low voltage (LV) distribution networks.
In de HS-stations, TS-stations en de belangrijke MS-stations worden dubbelrailsystemen toegepast, zoals afgebeeld in figuur 2.14. Hierbij worden twee railsystemen gebruikt, die onderling gekoppeld kunnen worden. Beide railsystemen kunnen gescheiden van elkaar worden gebruikt, maar het komt ook voor dat slechts één railsysteem wordt gebruikt en de andere als reserve stand-by is. De omschakelmogelijkheid naar het reserverailsysteem vergroot de bedrijfszekerheid aanzienlijk ten opzichte van het enkelrailsysteem. Ook ten aanzien van de bedrijfsvoering biedt het dubbelrailsysteem meer mogelijkheden, waarbij het uitvoeren van onderhoud, beperken van de kortsluitstromen en verdelen van de belasting de belangrijkste zijn. | In the HV stations, TS stations, and the important MV stations, double busbar systems are used, as shown in figure 2.14. In this setup, two busbar systems are used, which can be interconnected. Both busbar systems can be used separately, but it is also common for only one busbar system to be used while the other is on standby as a reserve. The ability to switch to the reserve busbar system significantly increases operational reliability compared to a single busbar system. Additionally, the double busbar system offers more operational flexibility, with the main advantages being the ability to perform maintenance, limit short-circuit currents, and distribute the load. | sections are connected via a regulating transformer (see figure 2.24). Single busbar systems are used in medium voltage (MV) and low voltage (LV) distribution networks. Figure 2.14 Double Busbar System
Veld | Veld | a single busbar system. Additionally, the double busbar system offers more operational flexibility, with the main advantages being the ability to perform maintenance, limit short-circuit currents, and distribute the load.
In een station worden kabels en transformatoren via velden aan de railsystemen gekoppeld. Een veld kan worden gezien als het elektrische aansluitpunt op een railsysteem voor een kabel, een lijn of een transformator. Ook de koppeling tussen twee railsystemen van een dubbelrailsysteem wordt met een veld gerealiseerd. Een veld bestaat uit een samenstel van objecten die vanuit het oogpunt van bedrijfsvoering functioneel bij elkaar horen, zoals: railscheiders, vermogenschakelaar, aarder (behorend bij een kabel, lijn of transformator). | In a substation, cables and transformers are connected to the bus systems via bays. A bay can be seen as the electrical connection point on a bus system for a cable, a line, or a transformer. The connection between two bus systems in a double busbar system is also realized with a bay. A bay consists of a set of objects that are functionally related from an operational perspective, such as: busbar disconnectors, circuit breakers, and grounding switches (associated with a cable, line, or transformer). | single busbar system. Additionally, the double busbar system offers more operational flexibility, with the main advantages being the ability to perform maintenance, limit short-circuit currents, and distribute the load. Veld
Uitvoeringsvormen | Uitvoeringsvormen | consists of a set of objects that are functionally related from an operational perspective, such as: busbar disconnectors, circuit breakers, and grounding switches (associated with a cable, line, or transformer).
Er bestaan veel uitvoeringsvormen voor de railsystemen, maar met het oog op bedrijfsvoering, betrouwbaarheid en kosten worden slechts enkele typen toegepast. Er zijn vier uitvoeringsvormen te onderscheiden voor de schakelaanleg; de wijze waarop de velden met een railsysteem worden verbonden: | There are many configurations for busbar systems, but with a view to operations, reliability, and costs, only a few types are used. There are four configurations to distinguish for the switchgear layout; the way in which the fields are connected with a busbar system: | of a set of objects that are functionally related from an operational perspective, such as: busbar disconnectors, circuit breakers, and grounding switches (associated with a cable, line, or transformer). Uitvoeringsvormen
vermogenschakelaars, gecombineerd met scheiders (op HS- en TS-niveau), | circuit breakers, combined with disconnectors (at HV and MV levels), | and costs, only a few types are used. There are four configurations to distinguish for the switchgear layout; the way in which the fields are connected with a busbar system:
uitrijdbare vermogenschakelaars (op MS-niveau), | withdrawable circuit breakers (at MV level), | four configurations to distinguish for the switchgear layout; the way in which the fields are connected with a busbar system: circuit breakers, combined with disconnectors (at HV and MV levels),
lastscheiders (op MS-niveau), | load break switches (at MV level), | switchgear layout; the way in which the fields are connected with a busbar system: circuit breakers, combined with disconnectors (at HV and MV levels), withdrawable circuit breakers (at MV level),
smeltpatronen (in MS-netstations en LS-verdeelkasten). | fuse links (in MV substations and LV distribution panels). | the fields are connected with a busbar system: circuit breakers, combined with disconnectors (at HV and MV levels), withdrawable circuit breakers (at MV level), load break switches (at MV level),
Figuur 2.15 Uitrijdbare vermogenschakelaar in een MS-ruimte | Figure 2.15 Withdrawable circuit breaker in an MV room | breakers, combined with disconnectors (at HV and MV levels), withdrawable circuit breakers (at MV level), load break switches (at MV level), fuse links (in MV substations and LV distribution panels).
Wanneer op MS-niveau een dubbelrailsysteem is toegepast, zijn er twee uitvoeringsvormen voor het koppelen op het railsysteem mogelijk: | When a double busbar system is applied at MV level, there are two possible configurations for coupling to the busbar system: | withdrawable circuit breakers (at MV level), load break switches (at MV level), fuse links (in MV substations and LV distribution panels). Figure 2.15 Withdrawable circuit breaker in an MV room
Met railkeuzeschakelaars, waarbij per veld één vermogenschakelaar aanwezig is, die door middel van een railkeuzeschakelaar of een railscheider met één van beide rails verbonden wordt. Beide rails kunnen worden gekoppeld met een dwarskoppelveld en een vermogenschakelaar. | With busbar selection switches, where each field has one circuit breaker, which is connected to one of the two busbars by means of a busbar selection switch or a busbar disconnector. Both busbars can be coupled with a cross-coupling field and a circuit breaker. | Figure 2.15 Withdrawable circuit breaker in an MV room When a double busbar system is applied at MV level, there are two possible configurations for coupling to the busbar system:
Met een duplex-systeem, waarbij per veld een uitrijdbare vermogenschakelaar (zie figuur 2.15) op een door de railkeuze bepaalde positie wordt ingereden. Ten behoeve van het omschakelen worden tijdelijk twee vermogenschakelaars gebruikt: één voor het inschakelen en één voor het uitschakelen. | With a duplex system, where a withdrawable circuit breaker (see figure 2.15) is inserted into a position determined by the busbar selection for each field. For the purpose of switching, two circuit breakers are temporarily used: one for switching on and one for switching off. | to one of the two busbars by means of a busbar selection switch or a busbar disconnector. Both busbars can be coupled with a cross-coupling field and a circuit breaker.
De uitvoeringsvorm met railkeuzeschakelaars wordt toegepast bij dubbelrailsystemen voor MS-transportnetten. | The design with busbar selectors is used in double busbar systems for medium voltage (MV) transport networks. | a position determined by the busbar selection for each field. For the purpose of switching, two circuit breakers are temporarily used: one for switching on and one for switching off.
Beveiliging | Beveiliging | breakers are temporarily used: one for switching on and one for switching off. The design with busbar selectors is used in double busbar systems for medium voltage (MV) transport networks.
Het railsysteem en de daaraan gekoppelde primaire objecten in het onderstation worden beveiligd met relais voor het detecteren van de fout en een vermogenschakelaar om de fout af te schakelen. Hoofdstuk 6 gaat nader in op de componenten en de concepten voor de beveiliging. Figuur 2.16 toont de stroombeveiliging van de drie fasen van een MS-veld in een onderstation. De beveiliging is hier uitgevoerd met elektromechanische relais. Bij modernisering worden elektronische en digitale relais toegepast. In toenemende mate zijn de stations bovendien geautomatiseerd, waardoor zij op afstand bestuurbaar zijn. | The busbar system and the connected primary objects in the substation are protected with relays for fault detection and a circuit breaker to disconnect the fault. Chapter 6 delves deeper into the components and concepts of protection. Figure 2.16 shows the current protection of the three phases of an MV field in a substation. The protection here is implemented with electromechanical relays. During modernization, electronic and digital relays are used. Increasingly, the stations are also automated, making them remotely controllable. | are temporarily used: one for switching on and one for switching off. The design with busbar selectors is used in double busbar systems for medium voltage (MV) transport networks. Beveiliging
Figuur 2.16 Stroombeveiliging van een veld in een onderstation | Figure 2.16 Current protection of a field in a substation | field in a substation. The protection here is implemented with electromechanical relays. During modernization, electronic and digital relays are used. Increasingly, the stations are also automated, making them remotely controllable.
2.4.6 Onderstation (OS) | 2.4.6 Substation (SS) | electromechanical relays. During modernization, electronic and digital relays are used. Increasingly, the stations are also automated, making them remotely controllable. Figure 2.16 Current protection of a field in a substation
In een onderstation (OS) wordt de spanning van het HS- of TS-niveau, waarop de elektrische energie wordt getransporteerd, getransformeerd naar een lager spanningsniveau. Na de spanningstransformatie voedt het OS een MS transport- of distributienet met doorgaans een twintigtal afgaande kabels. In veel gevallen wordt het MS-net door het OS direct vanuit een HS-net gevoed, zonder tussenkomst van een TS-niveau. Een onderstation voedt een MS-net voor een regio met een vermogen dat in de ordegrootte van 30 tot 100 MW ligt (Tabel 2.1). Vanwege deze belangrijke functie zijn onderstations in het algemeen zodanig uitgevoerd dat er voldoende reserve-elementen aanwezig zijn om na een enkelvoudige storing onmiddellijk om te schakelen, waardoor geen langdurige onderbreking in de levering ontstaat. | In a substation (SS), the voltage from the HV or MV level, at which electrical energy is transported, is transformed to a lower voltage level. After the voltage transformation, the SS feeds an MV transport or distribution network with typically around twenty outgoing cables. In many cases, the MV network is fed directly from an HV network by the SS, without the intervention of an MV level. A substation feeds an MV network for a region with a power capacity in the range of 30 to 100 MW (Table 2.1). Due to this important function, substations are generally designed with sufficient reserve elements to immediately switch over after a single fault, preventing prolonged interruptions in supply. | modernization, electronic and digital relays are used. Increasingly, the stations are also automated, making them remotely controllable. Figure 2.16 Current protection of a field in a substation 2.4.6 Substation (SS)
Figuur 2.17 geeft een schematisch overzicht van een HS/MS-onderstation. Het OS wordt aan de bovenzijde door twee verbindingen gevoed vanuit het HS-net. De 150 kV-verbindingen zijn ieder via een veld met het dubbelrailsysteem verbonden. Het veld bevat een vermogenschakelaar en twee railkeuzescheiders. Een koppelveld maakt het mogelijk om de twee 150 kV-railsystemen met elkaar te koppelen. Het OS bevat drie transformatoren, waarvan er één als reserve stand-by staat. De linker en rechter transformatoren voeden ieder, meestal via een gesloten installatie, een deel van het MS-distributienet. De middelste transformator kan zowel op het linker- als op het rechterdeel van de MS-installatie worden geschakeld. | Figure 2.17 provides a schematic overview of a high-voltage/medium-voltage (HV/MV) substation. The substation is fed from the top by two connections from the HV network. The 150 kV connections are each linked to the double busbar system through a bay. The bay contains a circuit breaker and two busbar selector switches. A coupling bay allows the two 150 kV busbar systems to be interconnected. The substation contains three transformers, one of which is on standby as a reserve. The left and right transformers each feed a part of the MV distribution network, usually through a closed installation. The middle transformer can be switched to either the left or right part of the MV installation. | 100 MW (Table 2.1). Due to this important function, substations are generally designed with sufficient reserve elements to immediately switch over after a single fault, preventing prolonged interruptions in supply.
Figuur 2.17 Schema van een HS/MS-onderstation | Figure 2.17 Diagram of a HV/MV substation | feed a part of the MV distribution network, usually through a closed installation. The middle transformer can be switched to either the left or right part of the MV installation.
De hierboven genoemde zaken worden nader toegelicht aan de hand van het 150/50/10 kV onderstation Kattenberg bij Arnhem. Het station is op HS-niveau in vijf richtingen met het HS-transportnet verbonden. Op het extra tussenspanningsniveau voedt het station in drie richtingen het regionale transportnet. Op middenspanningsniveau wordt het regionale distributienet vanuit dit station gevoed. Figuur 2.18 geeft de schematische opbouw van het onderstation. Ten opzichte van figuur 2.17 is het schema vereenvoudigd. De vermogenschakelaars zijn weggelaten. De railkeuzescheiders zijn weergegeven met open en gesloten bolletjes die de stand van de contacten representeren. De HS-rails en TS-rails zijn parallel bedreven en de MS-rails zijn gescheiden bedreven. In het schema zijn beide HS/TS-transformatoren parallel bedreven. Van de drie TS/MS-transformatoren is de middelste als reserve stand-by. Het MS-dubbelrailsysteem en de MS-kabelvelden zijn vereenvoudigd weergegeven. De voeding van het MS-distributienet is over de twee in werking zijnde transformatoren verdeeld. | The aforementioned matters are further explained using the 150/50/10 kV Kattenberg substation near Arnhem. The station is connected to the high-voltage (HV) transmission network in five directions. At the extra intermediate voltage level, the station feeds the regional transmission network in three directions. At the medium-voltage (MV) level, the regional distribution network is fed from this station. Figure 2.18 shows the schematic layout of the substation. Compared to Figure 2.17, the diagram is simplified. The circuit breakers are omitted. The busbar selectors are represented with open and closed circles indicating the position of the contacts. The HV busbars and intermediate voltage busbars are operated in parallel, and the MV busbars are operated separately. In the diagram, both HV/intermediate voltage transformers are operated in parallel. Of the three intermediate voltage/MV transformers, the middle one is on standby as a reserve. The MV double busbar system and the MV cable fields are shown in a simplified manner. The supply of the MV distribution network is divided between the two transformers in operation. | network, usually through a closed installation. The middle transformer can be switched to either the left or right part of the MV installation. Figure 2.17 Diagram of a HV/MV substation
Figuur 2.18 Schema van 150/50/10 kV-onderstation Kattenberg | Figure 2.18 Diagram of 150/50/10 kV substation Kattenberg | MV double busbar system and the MV cable fields are shown in a simplified manner. The supply of the MV distribution network is divided between the two transformers in operation.
Figuur 2.19 biedt een mooi overzicht van het gehele onderstation. Het bestaat ruwweg uit een HS-deel, links op de foto, en een TS-deel, rechtsboven op de foto. Midden op het HS-deel bevindt zich het dubbelrailsysteem, dat is uitgevoerd in een U-vorm: het ene railsysteem is als het ware gevouwen rondom het andere railsysteem. | Figure 2.19 provides a nice overview of the entire substation. It roughly consists of a high-voltage section, on the left in the photo, and a transformer section, at the top right in the photo. In the middle of the high-voltage section is the double busbar system, which is configured in a U-shape: one busbar system is essentially folded around the other busbar system. | fields are shown in a simplified manner. The supply of the MV distribution network is divided between the two transformers in operation. Figure 2.18 Diagram of 150/50/10 kV substation Kattenberg
Figuur 2.19 HS/TS/MS-onderstation Kattenberg bij Arnhem | Figure 2.19 HV/TS/MV substation Kattenberg near Arnhem | photo. In the middle of the high-voltage section is the double busbar system, which is configured in a U-shape: one busbar system is essentially folded around the other busbar system.
Het voordeel van de U-vorm is dat dit ruimte bespaart. De rails zelf zijn gemaakt van stevige aluminium buizen, die met isolatoren op hun plaats worden gehouden. | The advantage of the U-shape is that it saves space. The busbars themselves are made of sturdy aluminum tubes, which are held in place with insulators. | section is the double busbar system, which is configured in a U-shape: one busbar system is essentially folded around the other busbar system. Figure 2.19 HV/TS/MV substation Kattenberg near Arnhem
Beide railsystemen zijn gekoppeld met het koppelveld, linksboven op de foto. In dit onderstation worden beide railsystemen normaal gekoppeld bedreven. In geval van een storing in het onderstation wordt het koppelveld direct geopend. | Both busbar systems are connected with the coupling field, located at the top left of the photo. In this substation, both busbar systems are normally operated in a coupled manner. In the event of a fault in the substation, the coupling field is immediately opened. | substation Kattenberg near Arnhem The advantage of the U-shape is that it saves space. The busbars themselves are made of sturdy aluminum tubes, which are held in place with insulators.
De in- en uitgaande HS-lijnen en HS-kabels bevinden zich op de foto links en rechts ten opzichte van het dubbelrailsysteem. Elke lijn of kabel is via een scheider, een vermogenschakelaar en de railkeuzescheiders aangesloten op een van de twee railsystemen. | The incoming and outgoing high-voltage (HV) lines and HV cables are located on the left and right of the double busbar system in the photo. Each line or cable is connected to one of the two busbar systems via a disconnector, a circuit breaker, and the busbar selection disconnectors. | the photo. In this substation, both busbar systems are normally operated in a coupled manner. In the event of a fault in the substation, the coupling field is immediately opened.
In het midden van de foto zijn twee HS/TS-transformatoren zichtbaar van elk 100 MVA. De transformatoren zijn met scheider, vermogenschakelaar en railkeuzescheiders aangesloten op het HS-dubbelrailsysteem en op het TS-dubbelrailsysteem. | In the middle of the photo, two HS/TS transformers of 100 MVA each are visible. The transformers are connected to the HS double busbar system and the TS double busbar system via a disconnector, a circuit breaker, and busbar selection disconnectors. | double busbar system in the photo. Each line or cable is connected to one of the two busbar systems via a disconnector, a circuit breaker, and the busbar selection disconnectors.
Het TS-dubbelrailsysteem is op dezelfde wijze samengesteld als het HS-dubbelrailsysteem. Vanwege de lagere spanning is het compacter uitgevoerd dan het HS-dubbelrailsysteem. Op het TS-dubbelrailsysteem zijn kabels aangesloten die de regio rond het noorden van Arnhem voeden. Rechts van het TS-dubbelrailsysteem zijn drie TS/MS-transformatoren zichtbaar van elk 14 MVA. Deze transformatoren worden niet parallel bedreven en een van de drie staat als reserve stand-by. | The TS double busbar system is assembled in the same way as the HS double busbar system. Due to the lower voltage, it is more compact than the HS double busbar system. Cables are connected to the TS double busbar system that supply the region around the northern part of Arnhem. To the right of the TS double busbar system, three TS/MS transformers, each with a capacity of 14 MVA, are visible. These transformers are not operated in parallel, and one of the three is kept on standby as a reserve. | MVA each are visible. The transformers are connected to the HS double busbar system and the TS double busbar system via a disconnector, a circuit breaker, and busbar selection disconnectors.
De MS-zijde van elke TS/MS-transformator is verbonden met de gesloten MS-schakelinstallatie, die zich bevindt in de MS-ruimte. Deze is boven op de foto zichtbaar. Vanuit de MS-ruimte vertrekken de MS-strengen, die zijn weergegeven met de gekleurde lijnen. | The medium-voltage side of each TS/MS transformer is connected to the enclosed medium-voltage switchgear, which is located in the medium-voltage room. This is visible at the top of the photo. From the medium-voltage room, the medium-voltage cables, represented by the colored lines, depart. | TS/MS transformers, each with a capacity of 14 MVA, are visible. These transformers are not operated in parallel, and one of the three is kept on standby as a reserve.
Figuur 2.20 HS-deel onderstation Kattenberg bij Arnhem | Figure 2.20 High-voltage section of Kattenberg substation near Arnhem | switchgear, which is located in the medium-voltage room. This is visible at the top of the photo. From the medium-voltage room, the medium-voltage cables, represented by the colored lines, depart.
In de foto van figuur 2.19 geven twee pijlen (A en B) de kijkrichting aan van foto’s die in het onderstation zijn gemaakt. De foto van figuur 2.20 is gemaakt in de kijkrichting die met A is aangegeven. De foto toont het HS-dubbelrailsysteem en de HS/TS-transformatoren. Rechts op de foto is nog net de kopse kant van de U-vorm van HS-railsysteem A zichtbaar. Onder de buizen van het dubbelrailsysteem bevinden zich de railkeuzescheiders van de velden. Rechts van het midden van de foto is zichtbaar dat de drie railkeuzescheiders van de voorste HS/TS-transformator gekoppeld zijn aan HS-railsysteem A. In het midden van de foto zijn de drie vermogenschakelaars van de HS-zijde van de voorste HS/TS-transformator zichtbaar. De vermogenschakelaars zijn met drie aluminium geleiders (uitgevoerd met buizen) met de transformator verbonden. Om milieu- en veiligheidsredenen zijn de transformatoren in betonnen omhullingen geplaatst. | In the photo of figure 2.19, two arrows (A and B) indicate the viewing direction of photos taken in the substation. The photo of figure 2.20 is taken in the viewing direction indicated by A. The photo shows the high-voltage double busbar system and the high-voltage/medium-voltage transformers. On the right side of the photo, the end of the U-shape of high-voltage busbar system A is just visible. Under the pipes of the double busbar system are the busbar selection switches of the fields. To the right of the center of the photo, it is visible that the three busbar selection switches of the front high-voltage/medium-voltage transformer are connected to high-voltage busbar system A. In the center of the photo, the three circuit breakers of the high-voltage side of the front high-voltage/medium-voltage transformer are visible. The circuit breakers are connected to the transformer with three aluminum conductors (implemented with pipes). For environmental and safety reasons, the transformers are placed in concrete enclosures. | is visible at the top of the photo. From the medium-voltage room, the medium-voltage cables, represented by the colored lines, depart. Figure 2.20 High-voltage section of Kattenberg substation near Arnhem
Figuur 2.21 TS-deel onderstation Kattenberg bij Arnhem | Figure 2.21 TS section substation Kattenberg near Arnhem | transformer are visible. The circuit breakers are connected to the transformer with three aluminum conductors (implemented with pipes). For environmental and safety reasons, the transformers are placed in concrete enclosures.
Figuur 2.21 toont het TS-deel van het onderstation, gezien in kijkrichting B op de overzichtsfoto van figuur 2.19. Rechts op de foto zijn de twee maal drie, in buizen uitgevoerde, aluminium geleiders zichtbaar, die van de twee HS/TS-transformatoren komen. Deze zijn via velden (scheider, vermogenschakelaar en railkeuzescheiders) met het TS-dubbelrailsysteem verbonden. | Figure 2.21 shows the TS section of the substation, viewed in direction B from the overview photo in Figure 2.19. On the right side of the photo, the two sets of three aluminum conductors, implemented with pipes, are visible, which come from the two HS/TS transformers. These are connected to the TS double busbar system via fields (disconnector, circuit breaker, and busbar selection disconnectors). | to the transformer with three aluminum conductors (implemented with pipes). For environmental and safety reasons, the transformers are placed in concrete enclosures. Figure 2.21 TS section substation Kattenberg near Arnhem
Het dubbelrailsysteem is uitgevoerd in de I-vorm en bestaat uit twee maal drie aluminium buizen, die door isolatoren op hun plaats worden gehouden. De railkeuzescheiders bevinden zich onder het dubbelrailsysteem. In het midden van de foto zijn de vermogenschakelaars en de scheiders van de inkomende en uitgaande kabelverbindingen zichtbaar. Op de voorgrond is een 50 kV circuit zichtbaar dat is uitgevoerd met enkeladerige kabels en daarnaast een 50 kV circuit dat is uitgevoerd met een drieaderige kabel. Op de achtergrond zijn de drie TS/MS-transformatoren zichtbaar. | The double busbar system is configured in an I-shape and consists of two sets of three aluminum tubes, which are held in place by insulators. The busbar selection disconnectors are located beneath the double busbar system. In the center of the photo, the circuit breakers and disconnectors for the incoming and outgoing cable connections are visible. In the foreground, a 50 kV circuit with single-core cables is visible, alongside a 50 kV circuit with a three-core cable. In the background, the three TS/MS transformers are visible. | implemented with pipes, are visible, which come from the two HS/TS transformers. These are connected to the TS double busbar system via fields (disconnector, circuit breaker, and busbar selection disconnectors).
Figuur 2.22 Detail TS-deel onderstation Kattenberg bij Arnhem | Figure 2.22 Detail of TS section substation Kattenberg near Arnhem | In the foreground, a 50 kV circuit with single-core cables is visible, alongside a 50 kV circuit with a three-core cable. In the background, the three TS/MS transformers are visible.
Figuur 2.22 toont de uitvoering van een veld. Van rechts naar links zijn achtereenvolgens zichtbaar: steunisolator, spanningstransformator, scheider, vermogenschakelaar, stroomtransformator, geopende railkeuzescheiders voor het voorste railsysteem en gesloten railkeuzescheiders voor het achterste railsysteem. | Figure 2.22 shows the implementation of a field. From right to left, the following are visible in sequence: support insulator, voltage transformer, disconnector, circuit breaker, current transformer, open busbar selector switches for the front bus system, and closed busbar selector switches for the rear bus system. | is visible, alongside a 50 kV circuit with a three-core cable. In the background, the three TS/MS transformers are visible. Figure 2.22 Detail of TS section substation Kattenberg near Arnhem
2.4.7 Schakelstation (SS) | 2.4.7 Switching Station (SS) | in sequence: support insulator, voltage transformer, disconnector, circuit breaker, current transformer, open busbar selector switches for the front bus system, and closed busbar selector switches for the rear bus system.
Een schakelstation (SS), ook wel verdeelstation genoemd, koppelt een MS-distributienet aan het MS-transportnet, zoals afgebeeld in figuur 2.23. In een schakelstation worden de inkomende velden van de transportverbindingen bij gelijkblijvend spanningsniveau omgezet naar een veelvoud van afgaande velden voor distributie. | A switching station (SS), also known as a distribution station, connects an MV distribution network to the MV transmission network, as shown in figure 2.23. In a switching station, the incoming fields of the transmission connections are converted at a constant voltage level into multiple outgoing fields for distribution. | voltage transformer, disconnector, circuit breaker, current transformer, open busbar selector switches for the front bus system, and closed busbar selector switches for the rear bus system. 2.4.7 Switching Station (SS)
Het SS is meestal voorzien van een enkelrailsysteem dat uit twee delen bestaat, die met behulp van een railkoppeling met elkaar verbonden kunnen worden. Het schakelstation is zonder redundantie aangelegd en er zijn geen reserve componenten aanwezig. In geval van een storing moet worden omgeschakeld naar omliggende onderstations en schakelstations. | The SS is usually equipped with a single busbar system that consists of two parts, which can be connected to each other using a bus coupler. The switching station is designed without redundancy and there are no spare components available. In case of a failure, switching must be done to surrounding substations and switching stations. | network, as shown in figure 2.23. In a switching station, the incoming fields of the transmission connections are converted at a constant voltage level into multiple outgoing fields for distribution.
Figuur 2.23 Schakelstation | Figure 2.23 Switching Station | coupler. The switching station is designed without redundancy and there are no spare components available. In case of a failure, switching must be done to surrounding substations and switching stations.
2.4.8 Regelstation (RS) | 2.4.8 Control Station (CS) | is designed without redundancy and there are no spare components available. In case of a failure, switching must be done to surrounding substations and switching stations. Figure 2.23 Switching Station
In een regelstation worden de inkomende velden bij gelijkblijvend spanningsniveau omgezet naar een veelvoud van afgaande velden. In het regelstation is een regeltransformator geplaatst die het spanningsverlies in de inkomende kabels compenseert. Het regelstation is, net als het schakelstation, zonder redundantie aangelegd en er zijn geen reserve componenten aanwezig. In geval van een storing moet worden omgeschakeld naar omliggende onderstations en schakelstations. | In a control station, the incoming fields are converted to a multiple of outgoing fields at a constant voltage level. A regulating transformer is installed in the control station to compensate for the voltage loss in the incoming cables. The control station, like the switching station, is designed without redundancy, and there are no spare components available. In case of a failure, switching must be done to surrounding substations and switching stations. | and there are no spare components available. In case of a failure, switching must be done to surrounding substations and switching stations. Figure 2.23 Switching Station 2.4.8 Control Station (CS)
De regeltransformator kan met een ‘bypass’ verbinding buiten bedrijf worden genomen. Bij een storing in de regeltransformator wordt deze uitgeschakeld. De energielevering wordt hersteld door het sluiten van de vermogenschakelaar van de bypass. Figuur 2.24 illustreert dit. | The regulating transformer can be taken out of service with a 'bypass' connection. In case of a failure in the regulating transformer, it is switched off. The power supply is restored by closing the circuit breaker of the bypass. Figure 2.24 illustrates this. | like the switching station, is designed without redundancy, and there are no spare components available. In case of a failure, switching must be done to surrounding substations and switching stations.
Figuur 2.24 Regelstation met regeltransformator | Figure 2.24 Control station with regulating transformer | In case of a failure in the regulating transformer, it is switched off. The power supply is restored by closing the circuit breaker of the bypass. Figure 2.24 illustrates this.
2.4.9 Netstation | 2.4.9 Network Station | regulating transformer, it is switched off. The power supply is restored by closing the circuit breaker of the bypass. Figure 2.24 illustrates this. Figure 2.24 Control station with regulating transformer
In een netstation, ook wel distributiestation, middenspanningsruimte (MSR) of Ring Main Unit (RMU) genoemd, wordt het laagspanningsnet gevoed vanuit het middenspanningsnet. Deze stations zijn altijd enkelvoudig opgebouwd zonder reserve componenten. Een storing in het station leidt tot energieonderbreking, die hersteld kan worden door het inzetten van een aggregaat. | In a network station, also known as a distribution station, medium voltage room (MSR), or Ring Main Unit (RMU), the low voltage network is powered from the medium voltage network. These stations are always constructed as single units without spare components. A malfunction in the station leads to a power interruption, which can be restored by deploying a generator. | is switched off. The power supply is restored by closing the circuit breaker of the bypass. Figure 2.24 illustrates this. Figure 2.24 Control station with regulating transformer 2.4.9 Network Station
Netstations bestaan in principe uit: | Network stations essentially consist of: | network. These stations are always constructed as single units without spare components. A malfunction in the station leads to a power interruption, which can be restored by deploying a generator.
een enkelrail MS-installatie met lastscheiders | a single-busbar medium-voltage installation with load break switches | constructed as single units without spare components. A malfunction in the station leads to a power interruption, which can be restored by deploying a generator. Network stations essentially consist of:
een transformator | a transformer | malfunction in the station leads to a power interruption, which can be restored by deploying a generator. Network stations essentially consist of: a single-busbar medium-voltage installation with load break switches
een LS-verdeelrek | a low-voltage distribution rack | the station leads to a power interruption, which can be restored by deploying a generator. Network stations essentially consist of: a single-busbar medium-voltage installation with load break switches a transformer
Een netstation bevindt zich in een MS-streng tussen het voedingspunt en de netopening. Op de MS-rail zijn de in- en uitgaande MS-kabels aangesloten. In sommige gevallen is de MS-rail voorzien van een B-veld (beveiligd veld) met een vermogenschakelaar om een nieuwe streng in het MS-net te beveiligen. Deze netopbouw vermindert het aantal storingsverbruikersminuten. De transformator is beveiligd met hoogspanningssmeltveiligheid en een lastscheider of met een vermogenschakelaar met maximum stroom/tijd-relais. Het LS-verdeelrek is een enkelvoudig railsysteem met smeltveiligheden voor de transformator en de afgaande distributiekabels. Het station voedt een LS-distributienet met maximaal 12 afgaande kabels. Figuur 2.25 illustreert dit. | A network station is located in an MV string between the power supply point and the network opening. The incoming and outgoing MV cables are connected to the MV busbar. In some cases, the MV busbar is equipped with a B-field (protected field) with a circuit breaker to secure a new string in the MV network. This network configuration reduces the number of outage consumer minutes. The transformer is protected with high-voltage fuses and a load break switch or with a circuit breaker with maximum current/time relays. The LV distribution rack is a single busbar system with fuses for the transformer and the outgoing distribution cables. The station supplies an LV distribution network with up to 12 outgoing cables. Figure 2.25 illustrates this. | a power interruption, which can be restored by deploying a generator. Network stations essentially consist of: a single-busbar medium-voltage installation with load break switches a transformer a low-voltage distribution rack
Figuur 2.25 Netstation, met een beveiligde aftakking | Figure 2.25 Substation, with a protected branch | single busbar system with fuses for the transformer and the outgoing distribution cables. The station supplies an LV distribution network with up to 12 outgoing cables. Figure 2.25 illustrates this.
2.5 Aansluitingen, gebaseerd op aansluitcategorieën | 2.5 Connections, based on connection categories | transformer and the outgoing distribution cables. The station supplies an LV distribution network with up to 12 outgoing cables. Figure 2.25 illustrates this. Figure 2.25 Substation, with a protected branch
In de Tarievencode Elektriciteit van de NMa is vastgelegd op welke wijze een aansluiting gerealiseerd moet worden (Tarievencode, 2009). Hierin is vastgelegd op welke wijze de knip, de verbinding en de beveiliging moeten worden uitgevoerd en waar zich het overdrachtspunt bevindt. De volgende definities worden hierbij gebruikt: | The Electricity Tariff Code of the NMa specifies how a connection must be realized (Tariff Code, 2009). It outlines how the cut, the connection, and the protection must be implemented and where the transfer point is located. The following definitions are used in this context: | The station supplies an LV distribution network with up to 12 outgoing cables. Figure 2.25 illustrates this. Figure 2.25 Substation, with a protected branch 2.5 Connections, based on connection categories
De knip is de fysieke aftakking van het elektriciteitsnet. | The cut is the physical branching of the electrical grid. | Code, 2009). It outlines how the cut, the connection, and the protection must be implemented and where the transfer point is located. The following definitions are used in this context:
De verbinding is de elektriciteitskabel vanaf de knip tot aan de ontvangstruimte van de klant. | The connection is the electrical cable from the cut to the customer's receiving room. | the protection must be implemented and where the transfer point is located. The following definitions are used in this context: The cut is the physical branching of the electrical grid.
De beveiliging is het onderdeel van de aansluiting waarmee kan worden geschakeld om veilig te kunnen werken aan de aansluiting. De beveiliging voorkomt tevens schade aan het net, het station en de installatie van de aangeslotene in geval van een storing. | The protection is the part of the connection that allows for switching to safely work on the connection. The protection also prevents damage to the grid, the station, and the customer's installation in case of a malfunction. | definitions are used in this context: The cut is the physical branching of the electrical grid. The connection is the electrical cable from the cut to the customer's receiving room.
Het overdrachtspunt is het tussen de netbeheerder en de aangeslotene overeengekomen fysieke punt waar een scheiding tussen de aansluiting van het net en de installatie van de aangeslotene kan worden gerealiseerd. | The transfer point is the physical point agreed upon between the grid operator and the connected party where a separation between the grid connection and the installation of the connected party can be realized. | connection that allows for switching to safely work on the connection. The protection also prevents damage to the grid, the station, and the customer's installation in case of a malfunction.
De tarievencode maakt onderscheid in 7 gewenste aansluitcategorieën: | The tariff code distinguishes between 7 desired connection categories: | the physical point agreed upon between the grid operator and the connected party where a separation between the grid connection and the installation of the connected party can be realized.
A.1: tot en met 1 x 6A op een geschakeld net | A.1: up to and including 1 x 6A on a switched network | and the connected party where a separation between the grid connection and the installation of the connected party can be realized. The tariff code distinguishes between 7 desired connection categories:
A.2: van 3 x 25A tot en met 60 kVA | A.2: from 3 x 25A up to and including 60 kVA | the installation of the connected party can be realized. The tariff code distinguishes between 7 desired connection categories: A.1: up to and including 1 x 6A on a switched network
A.3: van 60 kVA tot en met 300 kVA | A.3: from 60 kVA up to and including 300 kVA | code distinguishes between 7 desired connection categories: A.1: up to and including 1 x 6A on a switched network A.2: from 3 x 25A up to and including 60 kVA
A.4: van 0,3 MVA tot en met 3 MVA met zuivere MS-aansluiting | A.4: from 0.3 MVA up to and including 3 MVA with a pure MV connection | and including 1 x 6A on a switched network A.2: from 3 x 25A up to and including 60 kVA A.3: from 60 kVA up to and including 300 kVA
A.5: van 0,3 MVA tot en met 3 MVA met fysieke levering van LS | A.5: from 0.3 MVA up to and including 3 MVA with physical delivery of LV | to and including 60 kVA A.3: from 60 kVA up to and including 300 kVA A.4: from 0.3 MVA up to and including 3 MVA with a pure MV connection
A.6: van 3 MVA tot en met 10 MVA | A.6: from 3 MVA up to and including 10 MVA | A.4: from 0.3 MVA up to and including 3 MVA with a pure MV connection A.5: from 0.3 MVA up to and including 3 MVA with physical delivery of LV
A.7: meer dan 10 MVA | A.7: more than 10 MVA | with a pure MV connection A.5: from 0.3 MVA up to and including 3 MVA with physical delivery of LV A.6: from 3 MVA up to and including 10 MVA
In de volgende paragrafen worden deze situaties nader toegelicht. Sommige bedrijven hanteren andere grenzen, welke op eigen praktijk en ervaring gebaseerd zijn, en hanteren daarom andere benamingen. | The following paragraphs will further explain these situations. Some companies use different thresholds based on their own practice and experience, and therefore use different terminology. | A.5: from 0.3 MVA up to and including 3 MVA with physical delivery of LV A.6: from 3 MVA up to and including 10 MVA A.7: more than 10 MVA
2.5.1 Gewenste aansluitcapaciteit tot en met 1 x 6A op een geschakeld net (A.1) | 2.5.1 Desired connection capacity up to and including 1 x 6A on a switched network (A.1) | A.7: more than 10 MVA The following paragraphs will further explain these situations. Some companies use different thresholds based on their own practice and experience, and therefore use different terminology.
De standaardmethode voor aansluitingen tot en met 1 x 6A is op de laagspanningskabel, op de hulpader van de laagspanningskabel of op de openbare verlichting (OV) kabel van de netbeheerder. Het net wordt geschakeld door de netbeheerder, bijvoorbeeld voor de openbare verlichting. | The standard method for connections up to and including 1 x 6A is on the low-voltage cable, on the auxiliary conductor of the low-voltage cable, or on the public lighting (PL) cable of the grid operator. The network is switched by the grid operator, for example, for public lighting. | different thresholds based on their own practice and experience, and therefore use different terminology. 2.5.1 Desired connection capacity up to and including 1 x 6A on a switched network (A.1)
knip: aftakmof op de kabel, hulpader of OV-kabel; | cut: branch joint on the cable, auxiliary conductor, or PL cable; | auxiliary conductor of the low-voltage cable, or on the public lighting (PL) cable of the grid operator. The network is switched by the grid operator, for example, for public lighting.
verbinding: laagspanningskabel van aftakmof tot aan de aansluitkast met beveiliging; | connection: low-voltage cable from the branch joint to the connection box with protection; | (PL) cable of the grid operator. The network is switched by the grid operator, for example, for public lighting. cut: branch joint on the cable, auxiliary conductor, or PL cable;
beveiliging: smeltpatroon of automaat in de aansluitkast, die zich bevindt in het aan te sluiten object; | protection: fuse or circuit breaker in the connection box, which is located in the object to be connected; | operator, for example, for public lighting. cut: branch joint on the cable, auxiliary conductor, or PL cable; connection: low-voltage cable from the branch joint to the connection box with protection;
overdrachtspunt: de beveiliging. | transfer point: the protection. | low-voltage cable from the branch joint to the connection box with protection; protection: fuse or circuit breaker in the connection box, which is located in the object to be connected;
Figuur 2.26, figuur 2.27 en figuur 2.28 illustreren de drie uitvoeringsvormen voor deze aansluitingen. | Figure 2.26, Figure 2.27, and Figure 2.28 illustrate the three configurations for these connections. | branch joint to the connection box with protection; protection: fuse or circuit breaker in the connection box, which is located in the object to be connected; transfer point: the protection.
Figuur 2.26 Aansluiting op een LS-hoofdkabel | Figure 2.26 Connection to a low-voltage main cable | the connection box, which is located in the object to be connected; transfer point: the protection. Figure 2.26, Figure 2.27, and Figure 2.28 illustrate the three configurations for these connections.
Figuur 2.27 Aansluiting op de hulpaders van een LS-combikabel | Figure 2.27 Connection to the auxiliary conductors of a low-voltage combined cable | object to be connected; transfer point: the protection. Figure 2.26, Figure 2.27, and Figure 2.28 illustrate the three configurations for these connections. Figure 2.26 Connection to a low-voltage main cable
Figuur 2.28 Aansluiting op een OV-hoofdkabel met aftaksysteem en met rijgsysteem | Figure 2.28 Connection to a low-voltage main cable with a tap-off system and a daisy-chain system | and Figure 2.28 illustrate the three configurations for these connections. Figure 2.26 Connection to a low-voltage main cable Figure 2.27 Connection to the auxiliary conductors of a low-voltage combined cable
2.5.2 Gewenste aansluitcapaciteit van 3 x 25A tot en met 60 kVA (A.2) | 2.5.2 Desired connection capacity from 3 x 25A up to 60 kVA (A.2) | main cable Figure 2.27 Connection to the auxiliary conductors of a low-voltage combined cable Figure 2.28 Connection to a low-voltage main cable with a tap-off system and a daisy-chain system
De standaardmethode voor aansluitingen van 3 x 25A tot en met 60 kVA is op de laagspanningskabel: | The standard method for connections from 3 x 25A up to 60 kVA is on the low-voltage cable: | cable Figure 2.28 Connection to a low-voltage main cable with a tap-off system and a daisy-chain system 2.5.2 Desired connection capacity from 3 x 25A up to 60 kVA (A.2)
knip: aftakmof op de kabel; | cut: branch joint on the cable; | Desired connection capacity from 3 x 25A up to 60 kVA (A.2) The standard method for connections from 3 x 25A up to 60 kVA is on the low-voltage cable:
verbinding: laagspanningskabel van aftakmof tot aan de aansluitkast met beveiliging; | connection: low-voltage cable from the branch joint to the connection box with protection; | 25A up to 60 kVA (A.2) The standard method for connections from 3 x 25A up to 60 kVA is on the low-voltage cable: cut: branch joint on the cable;
beveiliging: smeltpatroon of automaat in de aansluitkast, die zich bevindt in het aan te sluiten object; | protection: fuse or circuit breaker in the connection box, which is located in the object to be connected; | x 25A up to 60 kVA is on the low-voltage cable: cut: branch joint on the cable; connection: low-voltage cable from the branch joint to the connection box with protection;
overdrachtspunt: de beveiliging. | transfer point: the protection. | low-voltage cable from the branch joint to the connection box with protection; protection: fuse or circuit breaker in the connection box, which is located in the object to be connected;
De aansluitkast, het meterbord en de kWh-meter behoren tot de aansluitdienst van de netbeheerder. De klant kan kiezen uit een meerdere uitvoeringsvormen voor de aansluiting, zoals 3 x 25A, 1 x 35A en 1 x 25A. Figuur 2.29 illustreert de uitvoeringsvormen voor deze aansluitingen. | The connection box, the meter board, and the kWh meter are part of the connection service provided by the network operator. The customer can choose from several configurations for the connection, such as 3 x 25A, 1 x 35A, and 1 x 25A. Figure 2.29 illustrates the configurations for these connections. | branch joint to the connection box with protection; protection: fuse or circuit breaker in the connection box, which is located in the object to be connected; transfer point: the protection.
Figuur 2.29 Aansluiting op een LS-hoofdkabel | Figure 2.29 Connection to a low-voltage main cable | The customer can choose from several configurations for the connection, such as 3 x 25A, 1 x 35A, and 1 x 25A. Figure 2.29 illustrates the configurations for these connections.
2.5.3 Gewenste aansluitcapaciteit van 60 kVA tot en met 300 kVA (A.3) | 2.5.3 Desired connection capacity from 60 kVA up to and including 300 kVA (A.3) | the connection, such as 3 x 25A, 1 x 35A, and 1 x 25A. Figure 2.29 illustrates the configurations for these connections. Figure 2.29 Connection to a low-voltage main cable
De standaardmethode voor aansluitingen van 60 kVA tot en met 300 kVA is op het dichtstbijzijnde netstation in het net van de netbeheerder: | The standard method for connections from 60 kVA up to and including 300 kVA is at the nearest substation in the network of the grid operator: | Figure 2.29 illustrates the configurations for these connections. Figure 2.29 Connection to a low-voltage main cable 2.5.3 Desired connection capacity from 60 kVA up to and including 300 kVA (A.3)
knip: in het distributiestation vanaf de strook op het laagspaningsrek; | cut: in the distribution station from the strip on the low voltage rack; | including 300 kVA (A.3) The standard method for connections from 60 kVA up to and including 300 kVA is at the nearest substation in the network of the grid operator:
verbinding: laagspanningskabel van aftakmof tot aan de aansluitkast met beveiliging; | connection: low voltage cable from the branch joint to the connection box with protection; | to and including 300 kVA is at the nearest substation in the network of the grid operator: cut: in the distribution station from the strip on the low voltage rack;
beveiliging: smeltpatroon of automaat in de aansluitkast, die zich bevindt in het aan te sluiten object; | protection: fuse or circuit breaker in the connection box, which is located in the object to be connected; | the grid operator: cut: in the distribution station from the strip on the low voltage rack; connection: low voltage cable from the branch joint to the connection box with protection;
overdrachtspunt: de beveiliging. | transfer point: the protection. | voltage cable from the branch joint to the connection box with protection; protection: fuse or circuit breaker in the connection box, which is located in the object to be connected;
De aansluitkast, het meterbord en de kWh-meter behoren tot de aansluitdienst van de netbeheerder. Figuur 2.30 illustreert de uitvoeringsvormen voor deze aansluitingen. | The connection box, the meter board, and the kWh meter are part of the connection service provided by the network operator. Figure 2.30 illustrates the implementation forms for these connections. | branch joint to the connection box with protection; protection: fuse or circuit breaker in the connection box, which is located in the object to be connected; transfer point: the protection.
Figuur 2.30 Aansluiting op het LS-rek van een distributiestation | Figure 2.30 Connection to the low-voltage rack of a distribution station | The connection box, the meter board, and the kWh meter are part of the connection service provided by the network operator. Figure 2.30 illustrates the implementation forms for these connections.
2.5.4 Gewenste aansluitcapaciteit van 0,3 MVA tot en met 3 MVA met zuivere MS-aansluiting (A.4) | 2.5.4 Desired connection capacity from 0.3 MVA to 3 MVA with pure medium voltage connection (A.4) | part of the connection service provided by the network operator. Figure 2.30 illustrates the implementation forms for these connections. Figure 2.30 Connection to the low-voltage rack of a distribution station
De standaardmethode voor aansluitingen van 0,3 MVA tot en met 3 MVA is het inlussen in het middenspanningsnet van de netbeheerder: | The standard method for connections from 0.3 MVA to 3 MVA is looping into the medium voltage network of the grid operator: | for these connections. Figure 2.30 Connection to the low-voltage rack of a distribution station 2.5.4 Desired connection capacity from 0.3 MVA to 3 MVA with pure medium voltage connection (A.4)
knip: twee verbindingsmoffen die de twee MS-aansluitkabels verbinden met de doorgaande MS-hoofdkabel; | cut: two connection sleeves that connect the two medium voltage connection cables to the main medium voltage cable; | 3 MVA with pure medium voltage connection (A.4) The standard method for connections from 0.3 MVA to 3 MVA is looping into the medium voltage network of the grid operator:
verbinding: twee MS-kabels van gelijke capaciteit als de doorgaande MS-hoofdkabel, van verbindingsmoffen tot aan de aansluitkast met beveiliging; | connection: two medium voltage cables with the same capacity as the main medium voltage cable, from connection sleeves to the junction box with protection; | MVA is looping into the medium voltage network of the grid operator: cut: two connection sleeves that connect the two medium voltage connection cables to the main medium voltage cable;
beveiliging: MS-schakelinstallatie met twee kabelscheiders en een vermogenschakelaar, die zich bevindt in het aan te sluiten object; | protection: medium voltage switchgear with two cable isolators and a circuit breaker, located in the object to be connected; | to the main medium voltage cable; connection: two medium voltage cables with the same capacity as the main medium voltage cable, from connection sleeves to the junction box with protection;
overdrachtspunt: tussen het MS-meetveld en de MS-schakelinstallatie van de klant. | transfer point: between the medium voltage measuring field and the customer's medium voltage switchgear. | voltage cable, from connection sleeves to the junction box with protection; protection: medium voltage switchgear with two cable isolators and a circuit breaker, located in the object to be connected;
Figuur 2.31 Zuivere MS-aansluiting | Figure 2.31 Pure MV Connection | switchgear with two cable isolators and a circuit breaker, located in the object to be connected; transfer point: between the medium voltage measuring field and the customer's medium voltage switchgear.
Beide MS-aansluitkabels liggen in hetzelfde tracé. In de aansluitkast is een MS-meetveld met meettransformatoren aangebracht. De MS-schakelinstallatie is ondergebracht in een ruimte die de klant ter beschikking stelt. Figuur 2.31 illustreert de uitvoeringsvormen voor deze aansluitingen. | Both medium voltage (MV) connection cables are laid in the same route. In the connection box, an MV measuring field with measuring transformers is installed. The MV switchgear is housed in a space provided by the customer. Figure 2.31 illustrates the configurations for these connections. | and a circuit breaker, located in the object to be connected; transfer point: between the medium voltage measuring field and the customer's medium voltage switchgear. Figure 2.31 Pure MV Connection
Tot 630 kVA wordt vaak een compactstation gebruikt waarin transformator, schakelinstallatie en laagspanningsrek bijeen zijn geplaatst. Deze oplossing is voor de afnemer voordeliger dan het aanvragen van een ‘zuivere’ middenspanningsaansluiting, waarbij eveneens een middenspanningsmeting en een vermogenschakelaar worden geplaatst. | Up to 630 kVA, a compact station is often used in which the transformer, switchgear, and low-voltage rack are placed together. This solution is more cost-effective for the consumer than requesting a 'pure' medium-voltage connection, which also requires a medium-voltage measurement and a circuit breaker to be installed. | box, an MV measuring field with measuring transformers is installed. The MV switchgear is housed in a space provided by the customer. Figure 2.31 illustrates the configurations for these connections.
2.5.5 Gewenste aansluitcapaciteit van 0,3 MVA tot en met 3 MVA met fysieke levering van LS (A.5) | 2.5.5 Desired connection capacity from 0.3 MVA up to 3 MVA with physical delivery of LV (A.5) | are placed together. This solution is more cost-effective for the consumer than requesting a 'pure' medium-voltage connection, which also requires a medium-voltage measurement and a circuit breaker to be installed.
Deze aansluiting wordt gerealiseerd door een transformatiestap aan te bieden en te meten op het laagspanningsniveau. Deze meting wordt teruggerekend naar een meting op middenspanningsniveau. Tot 630 kVA wordt vaak een compactstation gebruikt waarin transformator, schakelinstallatie en laagspanningsrek in een kleine behuizing bijeen zijn geplaatst. Deze oplossing is voor de afnemer voordeliger dan het aanschaffen van een zuivere middenspanningsaansluiting met een middenspanningsmeting en een vermogenschakelaar. Bij realisatie van de aansluiting zorgt de klant zelf voor een transformator en bijbehorende behuizing (het compactstation). De netbeheerder stemt het aanleggen van de aansluiting af met de installateur. | This connection is realized by offering a transformation step and measuring at the low-voltage level. This measurement is then recalculated to a medium-voltage level measurement. Up to 630 kVA, a compact station is often used, in which the transformer, switchgear, and low-voltage rack are placed together in a small housing. This solution is more cost-effective for the consumer than purchasing a pure medium-voltage connection with a medium-voltage measurement and a circuit breaker. When establishing the connection, the customer is responsible for providing a transformer and the corresponding housing (the compact station). The grid operator coordinates the installation of the connection with the installer. | which also requires a medium-voltage measurement and a circuit breaker to be installed. 2.5.5 Desired connection capacity from 0.3 MVA up to 3 MVA with physical delivery of LV (A.5)
knip: twee verbindingsmoffen die de twee MS-aansluitkabels verbinden met de doorgaande MS-hoofdkabel; | splice: two connection sleeves that connect the two medium-voltage connection cables to the main medium-voltage cable; | establishing the connection, the customer is responsible for providing a transformer and the corresponding housing (the compact station). The grid operator coordinates the installation of the connection with the installer.
verbinding: twee MS-kabels van gelijke capaciteit als de doorgaande MS-hoofdkabel, van verbindingsmoffen tot aan de aansluitkast met beveiliging; | connection: two medium-voltage cables of equal capacity as the main medium-voltage cable, from the connection sleeves to the junction box with protection; | compact station). The grid operator coordinates the installation of the connection with the installer. splice: two connection sleeves that connect the two medium-voltage connection cables to the main medium-voltage cable;
Figuur 2.32 MS-aansluiting met fysieke levering van LS | Figure 2.32 MV connection with physical delivery of LV | medium-voltage connection cables to the main medium-voltage cable; connection: two medium-voltage cables of equal capacity as the main medium-voltage cable, from the connection sleeves to the junction box with protection;
beveiliging: MS-schakelinstallatie met twee kabelscheiders en een transformatorveld (KKT-installatie), die zich bevindt in het aan te sluiten object; | protection: MV switchgear with two cable isolators and a transformer field (KKT installation), located in the object to be connected; | two medium-voltage cables of equal capacity as the main medium-voltage cable, from the connection sleeves to the junction box with protection; Figure 2.32 MV connection with physical delivery of LV
overdrachtspunt: tussen de MS-smeltpatroon en de primaire klemmen van de transformator. | transfer point: between the MV fuse and the primary terminals of the transformer. | protection; Figure 2.32 MV connection with physical delivery of LV protection: MV switchgear with two cable isolators and a transformer field (KKT installation), located in the object to be connected;
De MS-aansluitkabels bevinden zich in hetzelfde tracé. In de aansluitkast is een MS-meetveld met meettransformatoren aangebracht. De MS-schakelinstallatie is ondergebracht in een compactstation of een ruimte die de klant ter beschikking stelt. Figuur 2.32 illustreert de uitvoeringsvormen voor deze aansluitingen. | The MV connection cables are located in the same route. In the connection box, an MV metering field with measuring transformers is installed. The MV switchgear is housed in a compact station or a space provided by the customer. Figure 2.32 illustrates the configurations for these connections. | with two cable isolators and a transformer field (KKT installation), located in the object to be connected; transfer point: between the MV fuse and the primary terminals of the transformer.
2.5.6 Gewenste aansluitcapaciteit van 3 MVA tot en met 10 MVA (A.6) | 2.5.6 Desired connection capacity from 3 MVA to 10 MVA (A.6) | field with measuring transformers is installed. The MV switchgear is housed in a compact station or a space provided by the customer. Figure 2.32 illustrates the configurations for these connections.
De standaard aansluitmethode is op een middenspanningsrail van een voedings- of schakelstation: | The standard connection method is to a medium-voltage busbar of a supply or switching station: | in a compact station or a space provided by the customer. Figure 2.32 illustrates the configurations for these connections. 2.5.6 Desired connection capacity from 3 MVA to 10 MVA (A.6)
knip: twee of meer afgaande velden van een middenspanningsrail; | split: two or more outgoing fields from a medium-voltage busbar; | configurations for these connections. 2.5.6 Desired connection capacity from 3 MVA to 10 MVA (A.6) The standard connection method is to a medium-voltage busbar of a supply or switching station:
verbinding: enkelvoudige storingsreserve zonder energieonderbreking, bestaande uit twee of meer kabels in een tracé; | connection: single fault reserve without power interruption, consisting of two or more cables in a route; | MVA to 10 MVA (A.6) The standard connection method is to a medium-voltage busbar of a supply or switching station: split: two or more outgoing fields from a medium-voltage busbar;
beveiliging: minimaal twee vermogenschakelaars en een scheider; | protection: at least two circuit breakers and a disconnector; | supply or switching station: split: two or more outgoing fields from a medium-voltage busbar; connection: single fault reserve without power interruption, consisting of two or more cables in a route;
overdrachtspunt: tussen het MS-meetveld en de MS-schakelinstallatie van de klant. | transfer point: between the medium-voltage measuring field and the customer's medium-voltage switchgear. | fields from a medium-voltage busbar; connection: single fault reserve without power interruption, consisting of two or more cables in a route; protection: at least two circuit breakers and a disconnector;
Er is een meetveld aanwezig in het inkoopstation van de klant. Figuur 2.33 illustreert de uitvoeringsvorm. | There is a measuring field present in the customer's purchasing station. Figure 2.33 illustrates the implementation. | consisting of two or more cables in a route; protection: at least two circuit breakers and a disconnector; transfer point: between the medium-voltage measuring field and the customer's medium-voltage switchgear.
Figuur 2.33 MS-aansluiting op MS-rail | Figure 2.33 MV connection to MV busbar | a disconnector; transfer point: between the medium-voltage measuring field and the customer's medium-voltage switchgear. There is a measuring field present in the customer's purchasing station. Figure 2.33 illustrates the implementation.
2.5.7 Gewenste aansluitcapaciteit meer dan 10 MVA (A.7) | 2.5.7 Desired connection capacity more than 10 MVA (A.7) | measuring field and the customer's medium-voltage switchgear. There is a measuring field present in the customer's purchasing station. Figure 2.33 illustrates the implementation. Figure 2.33 MV connection to MV busbar
Voor vermogens boven de 10 MVA bestaat geen voorgeschreven standaard aansluitmethode. Uitgangspunt is aansluiting op het dichtstbijzijnde punt in het net van de netbeheerder waar voldoende capaciteit aanwezig is. De klant voert met de netbeheerder een onderzoek uit voor het ontwerp van de aansluiting. Uiteindelijk realiseert de netbeheerder de knip, de verbinding en de beveiliging. | For capacities above 10 MVA, there is no prescribed standard connection method. The basic principle is to connect at the nearest point in the network of the grid operator where sufficient capacity is available. The customer conducts a study with the grid operator for the design of the connection. Ultimately, the grid operator implements the cut, the connection, and the protection. | a measuring field present in the customer's purchasing station. Figure 2.33 illustrates the implementation. Figure 2.33 MV connection to MV busbar 2.5.7 Desired connection capacity more than 10 MVA (A.7)
De tarieven worden op basis van voorcalculatorische projectkosten in rekening gebracht. Deze bepaling in de Tarievencode geeft aan nieuw aan te sluiten klanten met een vermogensvraag boven 10 MVA enigszins een locatieprikkel. Wanneer een aan te sluiten klant zich op een ‘net-technisch’ gezien minder gunstige plaats wil vestigen en zich wil laten aansluiten, wordt deze klant geconfronteerd met hoge kosten. Wellicht kiest deze klant er om deze reden toch voor zich op een andere (‘net-technisch’ gezien gunstigere) plaats te vestigen. | The rates are charged based on pre-calculated project costs. This provision in the Tariff Code gives new customers with a power demand above 10 MVA a slight location incentive. When a customer wants to establish themselves in a technically less favorable location and get connected, they are confronted with high costs. For this reason, the customer might choose to establish themselves in a technically more favorable location instead. | capacity is available. The customer conducts a study with the grid operator for the design of the connection. Ultimately, the grid operator implements the cut, the connection, and the protection.
2.6 Keuzes bij het ontwerpen van een net | 2.6 Choices in Network Design | technically less favorable location and get connected, they are confronted with high costs. For this reason, the customer might choose to establish themselves in a technically more favorable location instead.
Er zijn veel mogelijkheden om een nieuw netontwerp te maken. In praktijk echter is het ontwerp al voor een groot deel bepaald door de randvoorwaarden. Zo worden de meeste netontwerpen gemaakt voor een uitbreiding op een bestaande situatie. In die gevallen ligt de inpassing vast door de voeding en de aansluiting op andere bestaande delen van het distributienet. | There are many possibilities for creating a new network design. In practice, however, the design is largely determined by the constraints. For instance, most network designs are made for an expansion of an existing situation. In those cases, the integration is fixed by the power supply and the connection to other existing parts of the distribution network. | get connected, they are confronted with high costs. For this reason, the customer might choose to establish themselves in a technically more favorable location instead. 2.6 Choices in Network Design
De dichtheid van de HS-onderstations beïnvloedt de voedingswijze van het MS-distributienet. Het distributienet kan direct gevoed worden vanuit een onderstation of via schakel- of regelstation. Andere factoren zijn: | The density of the high-voltage substations affects the supply method of the medium-voltage distribution network. The distribution network can be directly supplied from a substation or via a switching or control station. Other factors include: | made for an expansion of an existing situation. In those cases, the integration is fixed by the power supply and the connection to other existing parts of the distribution network.
de belastingsdichtheid van het te voeden gebied en de lokale spreiding van de belastingen; | the load density of the area to be supplied and the local distribution of the loads; | substations affects the supply method of the medium-voltage distribution network. The distribution network can be directly supplied from a substation or via a switching or control station. Other factors include:
de technische en economische eisen die aan de oplossingen worden gesteld, zoals spanningshuishouding, waardering van de netverliezen en de gewenste betrouwbaarheid; | the technical and economic requirements imposed on the solutions, such as voltage regulation, evaluation of network losses, and the desired reliability; | supplied from a substation or via a switching or control station. Other factors include: the load density of the area to be supplied and the local distribution of the loads;
het gevoerde beleid en de gebruikelijke methoden binnen het bedrijf van de netbeheerder op het gebied van het netontwerp. | the implemented policies and the customary methods within the grid operator's company in the field of network design. | be supplied and the local distribution of the loads; the technical and economic requirements imposed on the solutions, such as voltage regulation, evaluation of network losses, and the desired reliability;
Het aantal netstations wordt voornamelijk bepaald door de elektriciteitsbehoefte op laagspanningsniveau. Een logisch gevolg hiervan is dat het distributienet op MS-niveau voor het grootste gedeelte wordt bepaald door de aansluitbehoefte op LS-niveau en voor grote klanten op MS-niveau en niet door de structuur op een hoger spanningsniveau. | The number of substations is primarily determined by the electricity demand at the low voltage level. A logical consequence of this is that the distribution network at the medium voltage level is largely determined by the connection needs at the low voltage level and for large customers at the medium voltage level, rather than by the structure at a higher voltage level. | such as voltage regulation, evaluation of network losses, and the desired reliability; the implemented policies and the customary methods within the grid operator's company in the field of network design.