## Sheet1
Original Text | Translated Text | Previous Context
Rekentechnische basis | Computational basis
Deel 2 begint in hoofdstuk 7 met een korte uiteenzetting van enkele belangrijke basisbegrippen die nodig zijn voor het rekenen aan elektriciteitsnetten. De basis wordt gelegd met de beschrijving van het wisselspanningsysteem en de toepassing van de complexe rekenwijze. Vervolgens wordt de voor het doen van kortsluitberekeningen zo belangrijke symmetrische componentenmethode toegelicht. | Part 2 begins in Chapter 7 with a brief explanation of some important basic concepts necessary for calculations in electrical networks. The foundation is laid with the description of the alternating current system and the application of complex calculation methods. Next, the symmetrical components method, which is crucial for performing short-circuit calculations, is explained. | Computational basis
7 Rekentechnische basis | 7 Computational Basis | laid with the description of the alternating current system and the application of complex calculation methods. Next, the symmetrical components method, which is crucial for performing short-circuit calculations, is explained.
7.1 Tekenafspraken belasting en opwekking | 7.1 Sign Conventions for Load and Generation | description of the alternating current system and the application of complex calculation methods. Next, the symmetrical components method, which is crucial for performing short-circuit calculations, is explained. 7 Computational Basis
7.2 Het wisselspanningsysteem | 7.2 The Alternating Current System | the application of complex calculation methods. Next, the symmetrical components method, which is crucial for performing short-circuit calculations, is explained. 7 Computational Basis 7.1 Sign Conventions for Load and Generation
7.3 Fasor-notatie in het complexe vlak | 7.3 Phasor Notation in the Complex Plane | methods. Next, the symmetrical components method, which is crucial for performing short-circuit calculations, is explained. 7 Computational Basis 7.1 Sign Conventions for Load and Generation 7.2 The Alternating Current System
7.4 Driefasen wisselstroomsysteem | 7.4 Three-Phase Alternating Current System | is crucial for performing short-circuit calculations, is explained. 7 Computational Basis 7.1 Sign Conventions for Load and Generation 7.2 The Alternating Current System 7.3 Phasor Notation in the Complex Plane
7.5 Methode symmetrische componenten | 7.5 Symmetrical Components Method | calculations, is explained. 7 Computational Basis 7.1 Sign Conventions for Load and Generation 7.2 The Alternating Current System 7.3 Phasor Notation in the Complex Plane 7.4 Three-Phase Alternating Current System
7.5.1 Een nieuwe fasor-notatie | 7.5.1 A New Phasor Notation | Computational Basis 7.1 Sign Conventions for Load and Generation 7.2 The Alternating Current System 7.3 Phasor Notation in the Complex Plane 7.4 Three-Phase Alternating Current System 7.5 Symmetrical Components Method
7.5.2 Splitsing in drie spanningsstelsels | 7.5.2 Division into Three Voltage Systems | for Load and Generation 7.2 The Alternating Current System 7.3 Phasor Notation in the Complex Plane 7.4 Three-Phase Alternating Current System 7.5 Symmetrical Components Method 7.5.1 A New Phasor Notation
7.5.3 Wiskundige decompositie | 7.5.3 Mathematical Decomposition | Alternating Current System 7.3 Phasor Notation in the Complex Plane 7.4 Three-Phase Alternating Current System 7.5 Symmetrical Components Method 7.5.1 A New Phasor Notation 7.5.2 Division into Three Voltage Systems
7.6 Asymmetrisch stroomstelsel en homopolaire impedantie | 7.6 Asymmetrical Current System and Homopolar Impedance | 7.3 Phasor Notation in the Complex Plane 7.4 Three-Phase Alternating Current System 7.5 Symmetrical Components Method 7.5.1 A New Phasor Notation 7.5.2 Division into Three Voltage Systems 7.5.3 Mathematical Decomposition
7.7 Rekenen met behulp van genormeerde grootheden | 7.7 Calculations Using Normalized Quantities | 7.4 Three-Phase Alternating Current System 7.5 Symmetrical Components Method 7.5.1 A New Phasor Notation 7.5.2 Division into Three Voltage Systems 7.5.3 Mathematical Decomposition 7.6 Asymmetrical Current System and Homopolar Impedance
7 Rekentechnische basis | 7 Computational Basis | 7.5 Symmetrical Components Method 7.5.1 A New Phasor Notation 7.5.2 Division into Three Voltage Systems 7.5.3 Mathematical Decomposition 7.6 Asymmetrical Current System and Homopolar Impedance 7.7 Calculations Using Normalized Quantities
7.1 Tekenafspraken belasting en opwekking | 7.1 Sign Conventions for Load and Generation | Method 7.5.1 A New Phasor Notation 7.5.2 Division into Three Voltage Systems 7.5.3 Mathematical Decomposition 7.6 Asymmetrical Current System and Homopolar Impedance 7.7 Calculations Using Normalized Quantities 7 Computational Basis
Bij de netberekeningen wordt veel gewerkt met vervangingsschema’s voor belastingen en elektrische machines. Een elektrische machine kan zowel een motor als een generator zijn. Een motor neemt elektrische energie uit het net op en een generator levert elektrische energie. Voor de duidelijkheid wordt eerst afgesproken welke richting voor stroom, spanning en vermogen positief of negatief is. Hiervoor kan worden gekozen uit de motorconventie en de generatorconventie. Figuur 7.1 illustreert dit voor een belasting of motor en een generator die aangesloten zijn op een netwerk. Kenmerkend voor de tekenafspraak is: | In network calculations, replacement diagrams for loads and electrical machines are frequently used. An electrical machine can be either a motor or a generator. A motor draws electrical energy from the grid, while a generator supplies electrical energy. For clarity, it is first agreed upon which direction for current, voltage, and power is considered positive or negative. This can be chosen from the motor convention and the generator convention. Figure 7.1 illustrates this for a load or motor and a generator connected to a network. Characteristic of the drawing convention is: | Division into Three Voltage Systems 7.5.3 Mathematical Decomposition 7.6 Asymmetrical Current System and Homopolar Impedance 7.7 Calculations Using Normalized Quantities 7 Computational Basis 7.1 Sign Conventions for Load and Generation
motorconventie: het aangesloten apparaat neemt actief vermogen (P, wattvermogen) uit het net op | motor convention: the connected device draws active power (P, watt power) from the network | from the motor convention and the generator convention. Figure 7.1 illustrates this for a load or motor and a generator connected to a network. Characteristic of the drawing convention is:
generatorconventie: het aangesloten apparaat levert actief vermogen (P, wattvermogen) aan het net. | generator convention: the connected device supplies active power (P, watt power) to the network. | load or motor and a generator connected to a network. Characteristic of the drawing convention is: motor convention: the connected device draws active power (P, watt power) from the network
Figuur 7.1 Tekenafspraken voor motorconventie (links) en generatorconventie (rechts) | Figure 7.1 Drawing conventions for motor convention (left) and generator convention (right) | convention is: motor convention: the connected device draws active power (P, watt power) from the network generator convention: the connected device supplies active power (P, watt power) to the network.
Indien het aangesloten apparaat een zuivere weerstand is, vloeit in de motorconventie de stroom van het netwerk naar het apparaat en is het teken positief. Ook het opgenomen vermogen is positief. In de generatorconventie is het teken van de stroom negatief. Het aan het netwerk afgegeven vermogen is dan ook negatief. | If the connected device is a pure resistance, in the motor convention, the current flows from the network to the device and the sign is positive. The power consumed is also positive. In the generator convention, the sign of the current is negative. The power delivered to the network is therefore negative. | power) from the network generator convention: the connected device supplies active power (P, watt power) to the network. Figure 7.1 Drawing conventions for motor convention (left) and generator convention (right)
Spanning en stroom kunnen in het complexe vlak als wijzers worden afgebeeld. Ook de impedanties van de componenten kunnen in datzelfde vlak worden afgebeeld. De impedantie van een zuivere weerstand wordt dan gerepresenteerd met een vector op de positieve reële as. De impedantie van een zuivere spoel zonder weerstand wordt afgebeeld met een vector langs de positieve imaginaire as. De impedantie van een zuivere condensator wordt afgebeeld met een vector langs de negatieve imaginaire as. Alle fysieke componenten hebben een positieve weerstand en een positieve of negatieve reactantie. Als gevolg worden hun impedanties afgebeeld in de kwadranten | Voltage and current can be represented as phasors in the complex plane. The impedances of the components can also be represented in the same plane. The impedance of a pure resistor is then represented by a vector on the positive real axis. The impedance of a pure inductor without resistance is represented by a vector along the positive imaginary axis. The impedance of a pure capacitor is represented by a vector along the negative imaginary axis. All physical components have a positive resistance and a positive or negative reactance. As a result, their impedances are represented in the quadrants. | the sign is positive. The power consumed is also positive. In the generator convention, the sign of the current is negative. The power delivered to the network is therefore negative.
I | I | a vector along the negative imaginary axis. All physical components have a positive resistance and a positive or negative reactance. As a result, their impedances are represented in the quadrants.
en | en | vector along the negative imaginary axis. All physical components have a positive resistance and a positive or negative reactance. As a result, their impedances are represented in the quadrants. I
IV | IV | along the negative imaginary axis. All physical components have a positive resistance and a positive or negative reactance. As a result, their impedances are represented in the quadrants. I en
in het rechtervlak van figuur 7.2. Een belasting in kwadrant | in the right plane of figure 7.2. A load in quadrant | the negative imaginary axis. All physical components have a positive resistance and a positive or negative reactance. As a result, their impedances are represented in the quadrants. I en IV
I | I | and a positive or negative reactance. As a result, their impedances are represented in the quadrants. I en IV in the right plane of figure 7.2. A load in quadrant
wordt inductief genoemd en een belasting in kwadrant | is called inductive, and a load in quadrant | a positive or negative reactance. As a result, their impedances are represented in the quadrants. I en IV in the right plane of figure 7.2. A load in quadrant I
IV | IV | their impedances are represented in the quadrants. I en IV in the right plane of figure 7.2. A load in quadrant I is called inductive, and a load in quadrant
capacitief. | capacitive. | impedances are represented in the quadrants. I en IV in the right plane of figure 7.2. A load in quadrant I is called inductive, and a load in quadrant IV
Figuur 7.2 Tekenafspraken voor de motorconventie | Figure 7.2 Drawing Conventions for the Motor Convention | are represented in the quadrants. I en IV in the right plane of figure 7.2. A load in quadrant I is called inductive, and a load in quadrant IV capacitive.
Een generator wordt meestal niet met een impedantie gemodelleerd. In hetzelfde vlak worden daarom ook actief vermogen en reactief vermogen (blindvermogen) afgebeeld. In het complexe vlak wordt daarbij gebruik gemaakt van de vier kwadranten. De eigenschappen voor de motor- en generatorconventie zijn samengevat in tabel 7.1. | A generator is usually not modeled with an impedance. Therefore, in the same plane, active power and reactive power (apparent power) are also depicted. In the complex plane, the four quadrants are used for this purpose. The properties for the motor and generator conventions are summarized in Table 7.1. | in the right plane of figure 7.2. A load in quadrant I is called inductive, and a load in quadrant IV capacitive. Figure 7.2 Drawing Conventions for the Motor Convention
Tabel 7.1 Tekenafspraken | Table 7.1 Sign Conventions | (apparent power) are also depicted. In the complex plane, the four quadrants are used for this purpose. The properties for the motor and generator conventions are summarized in Table 7.1.
Kwadrant | Kwadrant | depicted. In the complex plane, the four quadrants are used for this purpose. The properties for the motor and generator conventions are summarized in Table 7.1. Table 7.1 Sign Conventions
Motorconventie | Motorconventie | In the complex plane, the four quadrants are used for this purpose. The properties for the motor and generator conventions are summarized in Table 7.1. Table 7.1 Sign Conventions Kwadrant
Generatorconventie | Generatorconventie | the complex plane, the four quadrants are used for this purpose. The properties for the motor and generator conventions are summarized in Table 7.1. Table 7.1 Sign Conventions Kwadrant Motorconventie
P | P | complex plane, the four quadrants are used for this purpose. The properties for the motor and generator conventions are summarized in Table 7.1. Table 7.1 Sign Conventions Kwadrant Motorconventie Generatorconventie
Q | Q | plane, the four quadrants are used for this purpose. The properties for the motor and generator conventions are summarized in Table 7.1. Table 7.1 Sign Conventions Kwadrant Motorconventie Generatorconventie P
P | P | the four quadrants are used for this purpose. The properties for the motor and generator conventions are summarized in Table 7.1. Table 7.1 Sign Conventions Kwadrant Motorconventie Generatorconventie P Q
Q | Q | four quadrants are used for this purpose. The properties for the motor and generator conventions are summarized in Table 7.1. Table 7.1 Sign Conventions Kwadrant Motorconventie Generatorconventie P Q P
I | I | quadrants are used for this purpose. The properties for the motor and generator conventions are summarized in Table 7.1. Table 7.1 Sign Conventions Kwadrant Motorconventie Generatorconventie P Q P Q
> 0 | > 0 | are used for this purpose. The properties for the motor and generator conventions are summarized in Table 7.1. Table 7.1 Sign Conventions Kwadrant Motorconventie Generatorconventie P Q P Q I
(verbruik, motor) | (consumption, motor) | for this purpose. The properties for the motor and generator conventions are summarized in Table 7.1. Table 7.1 Sign Conventions Kwadrant Motorconventie Generatorconventie P Q P Q I > 0
> 0 | > 0 | purpose. The properties for the motor and generator conventions are summarized in Table 7.1. Table 7.1 Sign Conventions Kwadrant Motorconventie Generatorconventie P Q P Q I > 0 (consumption, motor)
(verbruik, spoel) | (consumption, coil) | properties for the motor and generator conventions are summarized in Table 7.1. Table 7.1 Sign Conventions Kwadrant Motorconventie Generatorconventie P Q P Q I > 0 (consumption, motor) > 0
> 0 | > 0 | the motor and generator conventions are summarized in Table 7.1. Table 7.1 Sign Conventions Kwadrant Motorconventie Generatorconventie P Q P Q I > 0 (consumption, motor) > 0 (consumption, coil)
(opwekking, generator) | (generation, generator) | and generator conventions are summarized in Table 7.1. Table 7.1 Sign Conventions Kwadrant Motorconventie Generatorconventie P Q P Q I > 0 (consumption, motor) > 0 (consumption, coil) > 0
> 0 | > 0 | conventions are summarized in Table 7.1. Table 7.1 Sign Conventions Kwadrant Motorconventie Generatorconventie P Q P Q I > 0 (consumption, motor) > 0 (consumption, coil) > 0 (generation, generator)
(opwekking, condensator) | (generation, capacitor) | summarized in Table 7.1. Table 7.1 Sign Conventions Kwadrant Motorconventie Generatorconventie P Q P Q I > 0 (consumption, motor) > 0 (consumption, coil) > 0 (generation, generator) > 0
II | II | Table 7.1. Table 7.1 Sign Conventions Kwadrant Motorconventie Generatorconventie P Q P Q I > 0 (consumption, motor) > 0 (consumption, coil) > 0 (generation, generator) > 0 (generation, capacitor)
< 0 | < 0 | 7.1. Table 7.1 Sign Conventions Kwadrant Motorconventie Generatorconventie P Q P Q I > 0 (consumption, motor) > 0 (consumption, coil) > 0 (generation, generator) > 0 (generation, capacitor) II
(opwekking, generator) | (generation, generator) | 7.1 Sign Conventions Kwadrant Motorconventie Generatorconventie P Q P Q I > 0 (consumption, motor) > 0 (consumption, coil) > 0 (generation, generator) > 0 (generation, capacitor) II < 0
> 0 | > 0 | Conventions Kwadrant Motorconventie Generatorconventie P Q P Q I > 0 (consumption, motor) > 0 (consumption, coil) > 0 (generation, generator) > 0 (generation, capacitor) II < 0 (generation, generator)
(verbruik, spoel) | (consumption, coil) | Motorconventie Generatorconventie P Q P Q I > 0 (consumption, motor) > 0 (consumption, coil) > 0 (generation, generator) > 0 (generation, capacitor) II < 0 (generation, generator) > 0
< 0 | < 0 | P Q P Q I > 0 (consumption, motor) > 0 (consumption, coil) > 0 (generation, generator) > 0 (generation, capacitor) II < 0 (generation, generator) > 0 (consumption, coil)
(verbruik, motor) | (consumption, motor) | P Q I > 0 (consumption, motor) > 0 (consumption, coil) > 0 (generation, generator) > 0 (generation, capacitor) II < 0 (generation, generator) > 0 (consumption, coil) < 0
> 0 | > 0 | I > 0 (consumption, motor) > 0 (consumption, coil) > 0 (generation, generator) > 0 (generation, capacitor) II < 0 (generation, generator) > 0 (consumption, coil) < 0 (consumption, motor)
(opwekking, condensator) | (generation, capacitor) | 0 (consumption, motor) > 0 (consumption, coil) > 0 (generation, generator) > 0 (generation, capacitor) II < 0 (generation, generator) > 0 (consumption, coil) < 0 (consumption, motor) > 0
III | III | motor) > 0 (consumption, coil) > 0 (generation, generator) > 0 (generation, capacitor) II < 0 (generation, generator) > 0 (consumption, coil) < 0 (consumption, motor) > 0 (generation, capacitor)
< 0 | < 0 | > 0 (consumption, coil) > 0 (generation, generator) > 0 (generation, capacitor) II < 0 (generation, generator) > 0 (consumption, coil) < 0 (consumption, motor) > 0 (generation, capacitor) III
(opwekking, generator) | (generation, generator) | (consumption, coil) > 0 (generation, generator) > 0 (generation, capacitor) II < 0 (generation, generator) > 0 (consumption, coil) < 0 (consumption, motor) > 0 (generation, capacitor) III < 0
< 0 | < 0 | > 0 (generation, generator) > 0 (generation, capacitor) II < 0 (generation, generator) > 0 (consumption, coil) < 0 (consumption, motor) > 0 (generation, capacitor) III < 0 (generation, generator)
(opwekking, condensator) | (generation, capacitor) | (generation, generator) > 0 (generation, capacitor) II < 0 (generation, generator) > 0 (consumption, coil) < 0 (consumption, motor) > 0 (generation, capacitor) III < 0 (generation, generator) < 0
< 0 | less than 0 | > 0 (generation, capacitor) II < 0 (generation, generator) > 0 (consumption, coil) < 0 (consumption, motor) > 0 (generation, capacitor) III < 0 (generation, generator) < 0 (generation, capacitor)
(verbruik, motor) | (consumption, motor) | capacitor) II < 0 (generation, generator) > 0 (consumption, coil) < 0 (consumption, motor) > 0 (generation, capacitor) III < 0 (generation, generator) < 0 (generation, capacitor) less than 0
< 0 | < 0 | < 0 (generation, generator) > 0 (consumption, coil) < 0 (consumption, motor) > 0 (generation, capacitor) III < 0 (generation, generator) < 0 (generation, capacitor) less than 0 (consumption, motor)
(verbruik, spoel) | (consumption, coil) | (generation, generator) > 0 (consumption, coil) < 0 (consumption, motor) > 0 (generation, capacitor) III < 0 (generation, generator) < 0 (generation, capacitor) less than 0 (consumption, motor) < 0
IV | IV | > 0 (consumption, coil) < 0 (consumption, motor) > 0 (generation, capacitor) III < 0 (generation, generator) < 0 (generation, capacitor) less than 0 (consumption, motor) < 0 (consumption, coil)
> 0 | > 0 | 0 (consumption, coil) < 0 (consumption, motor) > 0 (generation, capacitor) III < 0 (generation, generator) < 0 (generation, capacitor) less than 0 (consumption, motor) < 0 (consumption, coil) IV
(verbruik, motor) | (consumption, motor) | coil) < 0 (consumption, motor) > 0 (generation, capacitor) III < 0 (generation, generator) < 0 (generation, capacitor) less than 0 (consumption, motor) < 0 (consumption, coil) IV > 0
< 0 | less than 0 | 0 (consumption, motor) > 0 (generation, capacitor) III < 0 (generation, generator) < 0 (generation, capacitor) less than 0 (consumption, motor) < 0 (consumption, coil) IV > 0 (consumption, motor)
(opwekking, condensator) | (generation, capacitor) | > 0 (generation, capacitor) III < 0 (generation, generator) < 0 (generation, capacitor) less than 0 (consumption, motor) < 0 (consumption, coil) IV > 0 (consumption, motor) less than 0
> 0 | > 0 | (generation, capacitor) III < 0 (generation, generator) < 0 (generation, capacitor) less than 0 (consumption, motor) < 0 (consumption, coil) IV > 0 (consumption, motor) less than 0 (generation, capacitor)
(opwekking, generator) | (generation, generator) | III < 0 (generation, generator) < 0 (generation, capacitor) less than 0 (consumption, motor) < 0 (consumption, coil) IV > 0 (consumption, motor) less than 0 (generation, capacitor) > 0
< 0 | < 0 | 0 (generation, generator) < 0 (generation, capacitor) less than 0 (consumption, motor) < 0 (consumption, coil) IV > 0 (consumption, motor) less than 0 (generation, capacitor) > 0 (generation, generator)
(verbruik, spoel) | (consumption, coil) | generator) < 0 (generation, capacitor) less than 0 (consumption, motor) < 0 (consumption, coil) IV > 0 (consumption, motor) less than 0 (generation, capacitor) > 0 (generation, generator) < 0
Het is voor de eenduidigheid in de netberekeningen belangrijk om eenmalig te kiezen voor motor- of generatorconventie. | For consistency in network calculations, it is important to choose either the motor or generator convention once and for all. | 0 (generation, capacitor) less than 0 (consumption, motor) < 0 (consumption, coil) IV > 0 (consumption, motor) less than 0 (generation, capacitor) > 0 (generation, generator) < 0 (consumption, coil)
Ter verduidelijking van de samenhang wordt het volgende voorbeeld gegeven. Het actieve vermogen en het blindvermogen dat in de motorconventie in kwadrant | To clarify the relationship, the following example is given. The active power and the reactive power in the motor convention in quadrant | (generation, capacitor) > 0 (generation, generator) < 0 (consumption, coil) For consistency in network calculations, it is important to choose either the motor or generator convention once and for all.
III | III | motor or generator convention once and for all. To clarify the relationship, the following example is given. The active power and the reactive power in the motor convention in quadrant
door een synchrone generator is opgewekt, wordt door een motor in kwadrant | generated by a synchronous generator, is consumed by a motor in quadrant | or generator convention once and for all. To clarify the relationship, the following example is given. The active power and the reactive power in the motor convention in quadrant III
I | I | following example is given. The active power and the reactive power in the motor convention in quadrant III generated by a synchronous generator, is consumed by a motor in quadrant
verbruikt. | consumed. | example is given. The active power and the reactive power in the motor convention in quadrant III generated by a synchronous generator, is consumed by a motor in quadrant I
Een synchrone machine kan zowel als motor of als generator werken en kan daarbij blindvermogen opnemen en leveren. Deze machine is daarmee in staat om in alle kwadranten te werken. Maar het blijft belangrijk om ook in dit geval voor elk werkpunt eenmalig te kiezen voor hetzij de motorconventie dan wel de generatorconventie. | A synchronous machine can operate both as a motor or as a generator and can absorb and supply reactive power. This machine is therefore capable of operating in all quadrants. However, it remains important to choose either the motor convention or the generator convention for each operating point once. | is given. The active power and the reactive power in the motor convention in quadrant III generated by a synchronous generator, is consumed by a motor in quadrant I consumed.
Ook een asynchrone machine kan zowel als motor of als generator werken maar kan daarbij alleen blindvermogen opnemen. In de motorconventie kan de asynchrone machine dan werken in de kwadranten | An asynchronous machine can also operate both as a motor and as a generator, but it can only absorb reactive power. In the motor convention, the asynchronous machine can then operate in the quadrants | power. This machine is therefore capable of operating in all quadrants. However, it remains important to choose either the motor convention or the generator convention for each operating point once.
I | I | also operate both as a motor and as a generator, but it can only absorb reactive power. In the motor convention, the asynchronous machine can then operate in the quadrants
en | en | operate both as a motor and as a generator, but it can only absorb reactive power. In the motor convention, the asynchronous machine can then operate in the quadrants I
II | II | both as a motor and as a generator, but it can only absorb reactive power. In the motor convention, the asynchronous machine can then operate in the quadrants I en
. | . | as a motor and as a generator, but it can only absorb reactive power. In the motor convention, the asynchronous machine can then operate in the quadrants I en II
Tabel 7.2 Samenvatting richtingen en tekens van vermogens | Table 7.2 Summary of directions and signs of power | a motor and as a generator, but it can only absorb reactive power. In the motor convention, the asynchronous machine can then operate in the quadrants I en II .
Vermogen | Vermogen | only absorb reactive power. In the motor convention, the asynchronous machine can then operate in the quadrants I en II . Table 7.2 Summary of directions and signs of power
Motor-conventie | Motor convention | absorb reactive power. In the motor convention, the asynchronous machine can then operate in the quadrants I en II . Table 7.2 Summary of directions and signs of power Vermogen
Generator-conventie | Generator convention | power. In the motor convention, the asynchronous machine can then operate in the quadrants I en II . Table 7.2 Summary of directions and signs of power Vermogen Motor convention
Stroom en lasthoek | Current and load angle | the motor convention, the asynchronous machine can then operate in the quadrants I en II . Table 7.2 Summary of directions and signs of power Vermogen Motor convention Generator convention
Diagram | Diagram | asynchronous machine can then operate in the quadrants I en II . Table 7.2 Summary of directions and signs of power Vermogen Motor convention Generator convention Current and load angle
P positief | P positive | machine can then operate in the quadrants I en II . Table 7.2 Summary of directions and signs of power Vermogen Motor convention Generator convention Current and load angle Diagram
actief vermogen opnemen | absorb active power | then operate in the quadrants I en II . Table 7.2 Summary of directions and signs of power Vermogen Motor convention Generator convention Current and load angle Diagram P positive
actief vermogen leveren | deliver active power | the quadrants I en II . Table 7.2 Summary of directions and signs of power Vermogen Motor convention Generator convention Current and load angle Diagram P positive absorb active power
P negatief | P negative | en II . Table 7.2 Summary of directions and signs of power Vermogen Motor convention Generator convention Current and load angle Diagram P positive absorb active power deliver active power
actief vermogen leveren | deliver active power | . Table 7.2 Summary of directions and signs of power Vermogen Motor convention Generator convention Current and load angle Diagram P positive absorb active power deliver active power P negative
actief vermogen opnemen | absorb active power | Summary of directions and signs of power Vermogen Motor convention Generator convention Current and load angle Diagram P positive absorb active power deliver active power P negative deliver active power
Q positief | Q positive | and signs of power Vermogen Motor convention Generator convention Current and load angle Diagram P positive absorb active power deliver active power P negative deliver active power absorb active power
blindvermogen opnemen | absorb reactive power | of power Vermogen Motor convention Generator convention Current and load angle Diagram P positive absorb active power deliver active power P negative deliver active power absorb active power Q positive
(inductieve belasting) | (inductive load) | Motor convention Generator convention Current and load angle Diagram P positive absorb active power deliver active power P negative deliver active power absorb active power Q positive absorb reactive power
blindvermogen leveren | deliver reactive power | Generator convention Current and load angle Diagram P positive absorb active power deliver active power P negative deliver active power absorb active power Q positive absorb reactive power (inductive load)
(overbekrachtigde generator) | (overexcited generator) | and load angle Diagram P positive absorb active power deliver active power P negative deliver active power absorb active power Q positive absorb reactive power (inductive load) deliver reactive power
naijlende stroom | lagging current | angle Diagram P positive absorb active power deliver active power P negative deliver active power absorb active power Q positive absorb reactive power (inductive load) deliver reactive power (overexcited generator)
hoek φ positief | angle φ positive | P positive absorb active power deliver active power P negative deliver active power absorb active power Q positive absorb reactive power (inductive load) deliver reactive power (overexcited generator) lagging current
Q negatief | Q negative | active power deliver active power P negative deliver active power absorb active power Q positive absorb reactive power (inductive load) deliver reactive power (overexcited generator) lagging current angle φ positive
blindvermogen leveren | deliver reactive power | deliver active power P negative deliver active power absorb active power Q positive absorb reactive power (inductive load) deliver reactive power (overexcited generator) lagging current angle φ positive Q negative
(capacitieve belasting) | (capacitive load) | P negative deliver active power absorb active power Q positive absorb reactive power (inductive load) deliver reactive power (overexcited generator) lagging current angle φ positive Q negative deliver reactive power
blindvermogen opnemen | absorb reactive power | deliver active power absorb active power Q positive absorb reactive power (inductive load) deliver reactive power (overexcited generator) lagging current angle φ positive Q negative deliver reactive power (capacitive load)
(onderbekrachtigde generator) | (underexcited generator) | absorb active power Q positive absorb reactive power (inductive load) deliver reactive power (overexcited generator) lagging current angle φ positive Q negative deliver reactive power (capacitive load) absorb reactive power
voorijlende stroom | leading current | power Q positive absorb reactive power (inductive load) deliver reactive power (overexcited generator) lagging current angle φ positive Q negative deliver reactive power (capacitive load) absorb reactive power (underexcited generator)
hoek φ negatief | angle φ negative | positive absorb reactive power (inductive load) deliver reactive power (overexcited generator) lagging current angle φ positive Q negative deliver reactive power (capacitive load) absorb reactive power (underexcited generator) leading current
7.2 Het wisselspanningsysteem | 7.2 The Alternating Current System | power (inductive load) deliver reactive power (overexcited generator) lagging current angle φ positive Q negative deliver reactive power (capacitive load) absorb reactive power (underexcited generator) leading current angle φ negative
De wisselspanning kan in principe een willekeurige vorm hebben die zich elke periode herhaalt. De periode dat de vorm zich herhaalt bepaalt de frequentie f, die gelijk is aan het omgekeerde van de periodeduur. Door deze eigenschap kan de wisselspanning worden beschreven met een functie van de tijd. Het resultaat van deze functie is de momentane waarde van de spanning. In bijna alle elektriciteitssystemen is de wisselspanning sinusvormig. Het is gebruikelijk deze wisselspanning te beschrijven met onderstaande cosinusfunctie: | The alternating voltage can, in principle, have any arbitrary shape that repeats every period. The period during which the shape repeats determines the frequency f, which is equal to the inverse of the period duration. Due to this property, the alternating voltage can be described with a function of time. The result of this function is the instantaneous value of the voltage. In almost all electricity systems, the alternating voltage is sinusoidal. It is customary to describe this alternating voltage with the following cosine function: | power (overexcited generator) lagging current angle φ positive Q negative deliver reactive power (capacitive load) absorb reactive power (underexcited generator) leading current angle φ negative 7.2 The Alternating Current System
[ | [ | is the instantaneous value of the voltage. In almost all electricity systems, the alternating voltage is sinusoidal. It is customary to describe this alternating voltage with the following cosine function:
7.1 | 7.1 | the instantaneous value of the voltage. In almost all electricity systems, the alternating voltage is sinusoidal. It is customary to describe this alternating voltage with the following cosine function: [
] | ] | instantaneous value of the voltage. In almost all electricity systems, the alternating voltage is sinusoidal. It is customary to describe this alternating voltage with the following cosine function: [ 7.1
waarin: | in which: | value of the voltage. In almost all electricity systems, the alternating voltage is sinusoidal. It is customary to describe this alternating voltage with the following cosine function: [ 7.1 ]
û = √2·U | û = √2·U | the voltage. In almost all electricity systems, the alternating voltage is sinusoidal. It is customary to describe this alternating voltage with the following cosine function: [ 7.1 ] in which:
eff | eff | almost all electricity systems, the alternating voltage is sinusoidal. It is customary to describe this alternating voltage with the following cosine function: [ 7.1 ] in which: û = √2·U
topwaarde van de spanning | peak value of the voltage | all electricity systems, the alternating voltage is sinusoidal. It is customary to describe this alternating voltage with the following cosine function: [ 7.1 ] in which: û = √2·U eff
ω = 2πf | ω = 2πf | voltage is sinusoidal. It is customary to describe this alternating voltage with the following cosine function: [ 7.1 ] in which: û = √2·U eff peak value of the voltage
nethoekfrequentie (rad/s) | network angular frequency (rad/s) | It is customary to describe this alternating voltage with the following cosine function: [ 7.1 ] in which: û = √2·U eff peak value of the voltage ω = 2πf
ψ | ψ | describe this alternating voltage with the following cosine function: [ 7.1 ] in which: û = √2·U eff peak value of the voltage ω = 2πf network angular frequency (rad/s)
u | u | this alternating voltage with the following cosine function: [ 7.1 ] in which: û = √2·U eff peak value of the voltage ω = 2πf network angular frequency (rad/s) ψ
spanningfasehoek (rad) | voltage phase angle (rad) | alternating voltage with the following cosine function: [ 7.1 ] in which: û = √2·U eff peak value of the voltage ω = 2πf network angular frequency (rad/s) ψ u
De frequentie wordt uitgedrukt in de hoekfrequentie, in radialen per seconde. De fasehoek wordt uitgedrukt in radialen, door de hoek in graden te vermenigvuldigen met | The frequency is expressed in angular frequency, in radians per second. The phase angle is expressed in radians by multiplying the angle in degrees by | following cosine function: [ 7.1 ] in which: û = √2·U eff peak value of the voltage ω = 2πf network angular frequency (rad/s) ψ u voltage phase angle (rad)
2π/360 | 2π/360 | u voltage phase angle (rad) The frequency is expressed in angular frequency, in radians per second. The phase angle is expressed in radians by multiplying the angle in degrees by
. | . | voltage phase angle (rad) The frequency is expressed in angular frequency, in radians per second. The phase angle is expressed in radians by multiplying the angle in degrees by 2π/360
Figuur 7.3 Spanning als functie van de tijd voor f = 50 Hz en ψ = 20·(2π/360) rad | Figure 7.3 Voltage as a function of time for f = 50 Hz and ψ = 20·(2π/360) rad | phase angle (rad) The frequency is expressed in angular frequency, in radians per second. The phase angle is expressed in radians by multiplying the angle in degrees by 2π/360 .
De functie van formule 7.1 beschrijft de wisselende waarde van de spanning als cosinusfunctie van de tijd. In figuur 7.3 is deze functie getekend, waarbij de fase als voorbeeld 20 graden verschoven is. | The function of formula 7.1 describes the varying value of the voltage as a cosine function of time. In figure 7.3, this function is plotted, with the phase shifted by 20 degrees as an example. | expressed in radians by multiplying the angle in degrees by 2π/360 . Figure 7.3 Voltage as a function of time for f = 50 Hz and ψ = 20·(2π/360) rad
Ook de stroom is wiskundig op vergelijkbare wijze te beschrijven. De stroom heeft veelal een andere fasehoek en een andere grootte dan de spanning. Dit wordt veroorzaakt door de eigenschappen van de componenten in het netwerk en de wet van Ohm. De hoek van de stroom wordt uitgedrukt met behulp van de stroomfasehoek | The current can also be mathematically described in a similar manner. The current often has a different phase angle and magnitude than the voltage. This is caused by the properties of the components in the network and Ohm's law. The angle of the current is expressed using the current phase angle. | describes the varying value of the voltage as a cosine function of time. In figure 7.3, this function is plotted, with the phase shifted by 20 degrees as an example.
ψ | ψ | than the voltage. This is caused by the properties of the components in the network and Ohm's law. The angle of the current is expressed using the current phase angle.
i | i | the voltage. This is caused by the properties of the components in the network and Ohm's law. The angle of the current is expressed using the current phase angle. ψ
. De momentane waarde van de stroom is dan: | . The instantaneous value of the current is then: | voltage. This is caused by the properties of the components in the network and Ohm's law. The angle of the current is expressed using the current phase angle. ψ i
[ | [ | components in the network and Ohm's law. The angle of the current is expressed using the current phase angle. ψ i . The instantaneous value of the current is then:
7.2 | 7.2 | in the network and Ohm's law. The angle of the current is expressed using the current phase angle. ψ i . The instantaneous value of the current is then: [
] | ] | the network and Ohm's law. The angle of the current is expressed using the current phase angle. ψ i . The instantaneous value of the current is then: [ 7.2
waarin: | where: | network and Ohm's law. The angle of the current is expressed using the current phase angle. ψ i . The instantaneous value of the current is then: [ 7.2 ]
î = √2·I | î = √2·I | and Ohm's law. The angle of the current is expressed using the current phase angle. ψ i . The instantaneous value of the current is then: [ 7.2 ] where:
eff | eff | The angle of the current is expressed using the current phase angle. ψ i . The instantaneous value of the current is then: [ 7.2 ] where: î = √2·I
topwaarde van de stroom | peak value of the current | angle of the current is expressed using the current phase angle. ψ i . The instantaneous value of the current is then: [ 7.2 ] where: î = √2·I eff
ω = 2πf | ω = 2πf | expressed using the current phase angle. ψ i . The instantaneous value of the current is then: [ 7.2 ] where: î = √2·I eff peak value of the current
nethoekfrequentie | nethoekfrequentie | current phase angle. ψ i . The instantaneous value of the current is then: [ 7.2 ] where: î = √2·I eff peak value of the current ω = 2πf
ψ | ψ | phase angle. ψ i . The instantaneous value of the current is then: [ 7.2 ] where: î = √2·I eff peak value of the current ω = 2πf nethoekfrequentie
i | i | angle. ψ i . The instantaneous value of the current is then: [ 7.2 ] where: î = √2·I eff peak value of the current ω = 2πf nethoekfrequentie ψ
stroomfasehoek | stroomfasehoek | ψ i . The instantaneous value of the current is then: [ 7.2 ] where: î = √2·I eff peak value of the current ω = 2πf nethoekfrequentie ψ i
Het hoekverschil tussen stroom en spanning is: | The phase difference between current and voltage is: | i . The instantaneous value of the current is then: [ 7.2 ] where: î = √2·I eff peak value of the current ω = 2πf nethoekfrequentie ψ i stroomfasehoek
[ | [ | is then: [ 7.2 ] where: î = √2·I eff peak value of the current ω = 2πf nethoekfrequentie ψ i stroomfasehoek The phase difference between current and voltage is:
7.3 | 7.3 | then: [ 7.2 ] where: î = √2·I eff peak value of the current ω = 2πf nethoekfrequentie ψ i stroomfasehoek The phase difference between current and voltage is: [
] | ] | [ 7.2 ] where: î = √2·I eff peak value of the current ω = 2πf nethoekfrequentie ψ i stroomfasehoek The phase difference between current and voltage is: [ 7.3
Hierdoor kan de stroomfasehoek ook geschreven worden als: | As a result, the current phase angle can also be written as: | 7.2 ] where: î = √2·I eff peak value of the current ω = 2πf nethoekfrequentie ψ i stroomfasehoek The phase difference between current and voltage is: [ 7.3 ]
[ | [ | ω = 2πf nethoekfrequentie ψ i stroomfasehoek The phase difference between current and voltage is: [ 7.3 ] As a result, the current phase angle can also be written as:
7.4 | 7.4
] | ] | 2πf nethoekfrequentie ψ i stroomfasehoek The phase difference between current and voltage is: [ 7.3 ] As a result, the current phase angle can also be written as: [ 7.4
waardoor vergelijking 7.2 over gaat in: | which transforms equation 7.2 into: | nethoekfrequentie ψ i stroomfasehoek The phase difference between current and voltage is: [ 7.3 ] As a result, the current phase angle can also be written as: [ 7.4 ]
[ | [ | phase difference between current and voltage is: [ 7.3 ] As a result, the current phase angle can also be written as: [ 7.4 ] which transforms equation 7.2 into:
7.5 | 7.5 | difference between current and voltage is: [ 7.3 ] As a result, the current phase angle can also be written as: [ 7.4 ] which transforms equation 7.2 into: [
] | ] | between current and voltage is: [ 7.3 ] As a result, the current phase angle can also be written as: [ 7.4 ] which transforms equation 7.2 into: [ 7.5
Uit de functies van de momentane waarde van stroom en spanning kan de functie voor de momentane waarde van het vermogen worden afgeleid door het product te nemen van de momentane spanning en stroom. | From the functions of the instantaneous value of current and voltage, the function for the instantaneous value of power can be derived by taking the product of the instantaneous voltage and current. | current and voltage is: [ 7.3 ] As a result, the current phase angle can also be written as: [ 7.4 ] which transforms equation 7.2 into: [ 7.5 ]
[ | [ | functions of the instantaneous value of current and voltage, the function for the instantaneous value of power can be derived by taking the product of the instantaneous voltage and current.
7.6 | 7.6 | of the instantaneous value of current and voltage, the function for the instantaneous value of power can be derived by taking the product of the instantaneous voltage and current. [
] | ] | the instantaneous value of current and voltage, the function for the instantaneous value of power can be derived by taking the product of the instantaneous voltage and current. [ 7.6
Door gebruik te maken van de algemene goniometrische relaties volgt uit vergelijking 7.6: | By using the general trigonometric relationships, it follows from equation 7.6: | instantaneous value of current and voltage, the function for the instantaneous value of power can be derived by taking the product of the instantaneous voltage and current. [ 7.6 ]
[ | [ | value of power can be derived by taking the product of the instantaneous voltage and current. [ 7.6 ] By using the general trigonometric relationships, it follows from equation 7.6:
7.7 | 7.7 | of power can be derived by taking the product of the instantaneous voltage and current. [ 7.6 ] By using the general trigonometric relationships, it follows from equation 7.6: [
] | ] | power can be derived by taking the product of the instantaneous voltage and current. [ 7.6 ] By using the general trigonometric relationships, it follows from equation 7.6: [ 7.7
Deze vergelijking kan worden opgesplitst in twee delen. Hierin valt op dat in het eerste deel de bekende cos(φ) voorkomt, die ook wel aangeduid wordt als ‘arbeidsfactor‘. Het eerste deel van de vergelijking is tijdsonafhankelijk en wordt het gemiddelde vermogen genoemd. Het tweede deel van de vergelijking is tijdsafhankelijk en wisselt met de dubbele frequentie. | This equation can be split into two parts. It is notable that in the first part, the well-known cos(φ) appears, which is also referred to as the 'power factor.' The first part of the equation is time-independent and is called the average power. The second part of the equation is time-dependent and oscillates at twice the frequency. | can be derived by taking the product of the instantaneous voltage and current. [ 7.6 ] By using the general trigonometric relationships, it follows from equation 7.6: [ 7.7 ]
[ | [ | 'power factor.' The first part of the equation is time-independent and is called the average power. The second part of the equation is time-dependent and oscillates at twice the frequency.
7.8 | 7.8 | factor.' The first part of the equation is time-independent and is called the average power. The second part of the equation is time-dependent and oscillates at twice the frequency. [
] | ] | The first part of the equation is time-independent and is called the average power. The second part of the equation is time-dependent and oscillates at twice the frequency. [ 7.8
Bij beschouwing van het vermogen door een zuivere weerstand is stroom zuiver resistief en is het hoekverschil tussen stroom en spanning | When considering the power through a pure resistor, the current is purely resistive, and the phase angle between current and voltage is zero. | first part of the equation is time-independent and is called the average power. The second part of the equation is time-dependent and oscillates at twice the frequency. [ 7.8 ]
φ = 0 rad | φ = 0 rad | at twice the frequency. [ 7.8 ] When considering the power through a pure resistor, the current is purely resistive, and the phase angle between current and voltage is zero.
. In dat geval vereenvoudigt formule 7.7 in: | . In that case, formula 7.7 simplifies to: | [ 7.8 ] When considering the power through a pure resistor, the current is purely resistive, and the phase angle between current and voltage is zero. φ = 0 rad
[ | [ | a pure resistor, the current is purely resistive, and the phase angle between current and voltage is zero. φ = 0 rad . In that case, formula 7.7 simplifies to:
7.9 | 7.9 | pure resistor, the current is purely resistive, and the phase angle between current and voltage is zero. φ = 0 rad . In that case, formula 7.7 simplifies to: [
] | ] | resistor, the current is purely resistive, and the phase angle between current and voltage is zero. φ = 0 rad . In that case, formula 7.7 simplifies to: [ 7.9
Figuur 7.4 illustreert dit. Hier is duidelijk te zien dat het momentane vermogen steeds positief is en met de dubbele frequentie wisselt om het gemiddelde vermogen (P gemiddeld) van ongeveer 0,4 pu. Het gemiddelde vermogen is het vermogen waarmee arbeid wordt verricht. | Figure 7.4 illustrates this. Here, it is clearly visible that the instantaneous power is always positive and oscillates at double the frequency around the average power (P average) of approximately 0.4 pu. The average power is the power with which work is performed. | the current is purely resistive, and the phase angle between current and voltage is zero. φ = 0 rad . In that case, formula 7.7 simplifies to: [ 7.9 ]
Figuur 7.4 Momentane waarden van spanning, stroom en vermogen | Figure 7.4 Instantaneous values of voltage, current, and power | is always positive and oscillates at double the frequency around the average power (P average) of approximately 0.4 pu. The average power is the power with which work is performed.
Het volgende voorbeeld gaat uit van een impedantie, waarbij de stroom 45 graden na-ijlt op de spanning. Volgens tabel 7.2 is dit een inductieve belasting. In geval van een 45 graden na-ijlende stroom is | The following example assumes an impedance where the current lags the voltage by 45 degrees. According to Table 7.2, this is an inductive load. In the case of a 45-degree lagging current, | around the average power (P average) of approximately 0.4 pu. The average power is the power with which work is performed. Figure 7.4 Instantaneous values of voltage, current, and power
φ = 45·(2π/360) rad | φ = 45·(2π/360) rad | example assumes an impedance where the current lags the voltage by 45 degrees. According to Table 7.2, this is an inductive load. In the case of a 45-degree lagging current,
en ontstaat figuur 7.5. In deze figuur valt op dat het momentane vermogen nu niet meer altijd positief is. Het gemiddelde vermogen, waarmee arbeid wordt verricht, is in dat geval ook kleiner geworden (ongeveer 0,3 pu), doordat cos(φ) nu gelijk is aan 0,7. | and figure 7.5 is created. In this figure, it is noticeable that the instantaneous power is no longer always positive. The average power, with which work is performed, has also decreased in this case (approximately 0.3 pu), because cos(φ) is now equal to 0.7. | where the current lags the voltage by 45 degrees. According to Table 7.2, this is an inductive load. In the case of a 45-degree lagging current, φ = 45·(2π/360) rad
Figuur 7.5 Momentane waarden van spanning, 45 graden naijlende stroom en vermogen | Figure 7.5 Instantaneous values of voltage, 45-degree lagging current, and power | power is no longer always positive. The average power, with which work is performed, has also decreased in this case (approximately 0.3 pu), because cos(φ) is now equal to 0.7.
In geval van een zuiver inductieve belasting ontstaat een 90 graden na-ijlende stroom met | In the case of a purely inductive load, a 90-degree lagging current is generated with | work is performed, has also decreased in this case (approximately 0.3 pu), because cos(φ) is now equal to 0.7. Figure 7.5 Instantaneous values of voltage, 45-degree lagging current, and power
φ = 90·(2π/360) rad | φ = 90·(2π/360) rad | now equal to 0.7. Figure 7.5 Instantaneous values of voltage, 45-degree lagging current, and power In the case of a purely inductive load, a 90-degree lagging current is generated with
en ontstaat figuur 7.6. In deze figuur valt op dat het momentane vermogen even vaak positief als negatief is. Het gemiddelde vermogen, waarmee arbeid wordt verricht, is in dat geval gelijk aan nul geworden, doordat cos(φ) nu gelijk is aan 0. Dat betekent dat in dit geval geen actief vermogen wordt getransporteerd. Dat klopt, want dit is een eigenschap van een ideale spoel. | and figure 7.6 is created. In this figure, it is noticeable that the instantaneous power is as often positive as it is negative. The average power, with which work is performed, has in that case become equal to zero because cos(φ) is now equal to 0. This means that no active power is being transmitted in this case. That is correct, because this is a characteristic of an ideal inductor. | Figure 7.5 Instantaneous values of voltage, 45-degree lagging current, and power In the case of a purely inductive load, a 90-degree lagging current is generated with φ = 90·(2π/360) rad
Figuur 7.6 Momentane waarden van spanning, 90 graden na-ijlende stroom (zuiver inductief) en vermogen | Figure 7.6 Instantaneous values of voltage, 90-degree lagging current (purely inductive), and power | cos(φ) is now equal to 0. This means that no active power is being transmitted in this case. That is correct, because this is a characteristic of an ideal inductor.
Het gemiddelde vermogen | The average power | being transmitted in this case. That is correct, because this is a characteristic of an ideal inductor. Figure 7.6 Instantaneous values of voltage, 90-degree lagging current (purely inductive), and power
P | P | this case. That is correct, because this is a characteristic of an ideal inductor. Figure 7.6 Instantaneous values of voltage, 90-degree lagging current (purely inductive), and power The average power
gemiddeld | gemiddeld | case. That is correct, because this is a characteristic of an ideal inductor. Figure 7.6 Instantaneous values of voltage, 90-degree lagging current (purely inductive), and power The average power P
, waarmee arbeid wordt verricht, is gelijk aan het bekende actieve vermogen P, uitgedrukt in Watt (W). | , with which work is performed, is equal to the known active power P, expressed in Watts (W). | That is correct, because this is a characteristic of an ideal inductor. Figure 7.6 Instantaneous values of voltage, 90-degree lagging current (purely inductive), and power The average power P gemiddeld
[ | [ | 90-degree lagging current (purely inductive), and power The average power P gemiddeld , with which work is performed, is equal to the known active power P, expressed in Watts (W).
7.10 | 7.10 | lagging current (purely inductive), and power The average power P gemiddeld , with which work is performed, is equal to the known active power P, expressed in Watts (W). [
] | ] | current (purely inductive), and power The average power P gemiddeld , with which work is performed, is equal to the known active power P, expressed in Watts (W). [ 7.10
Het product van de effectieve waarde van spanning en stroom wordt het schijnbare vermogen | The product of the effective value of voltage and current is called the apparent power. | (purely inductive), and power The average power P gemiddeld , with which work is performed, is equal to the known active power P, expressed in Watts (W). [ 7.10 ]
S | S | is equal to the known active power P, expressed in Watts (W). [ 7.10 ] The product of the effective value of voltage and current is called the apparent power.
genoemd, uitgedrukt in Volt-Ampère (VA). Dit is een zeer belangrijke waarde, omdat alle installaties op basis van het schijnbare vermogen worden ontworpen. Deze ontwerpparameter wordt op de naamplaat van onder andere transformatoren vermeld. | called, expressed in Volt-Amperes (VA). This is a very important value because all installations are designed based on the apparent power. This design parameter is listed on the nameplate of, among other things, transformers. | equal to the known active power P, expressed in Watts (W). [ 7.10 ] The product of the effective value of voltage and current is called the apparent power. S
[ | [ | (VA). This is a very important value because all installations are designed based on the apparent power. This design parameter is listed on the nameplate of, among other things, transformers.
7.11 | 7.11 | This is a very important value because all installations are designed based on the apparent power. This design parameter is listed on the nameplate of, among other things, transformers. [
] | ] | is a very important value because all installations are designed based on the apparent power. This design parameter is listed on the nameplate of, among other things, transformers. [ 7.11
Hiermee kan het blindvermogen | This allows the reactive power | a very important value because all installations are designed based on the apparent power. This design parameter is listed on the nameplate of, among other things, transformers. [ 7.11 ]
Q | Q | all installations are designed based on the apparent power. This design parameter is listed on the nameplate of, among other things, transformers. [ 7.11 ] This allows the reactive power
, het vermogensaandeel waarmee geen arbeid kan worden verricht, worden uitgerekend. Het wordt uitgedrukt in var. | , the power component with which no work can be performed, to be calculated. It is expressed in var. | installations are designed based on the apparent power. This design parameter is listed on the nameplate of, among other things, transformers. [ 7.11 ] This allows the reactive power Q
[ | [ | things, transformers. [ 7.11 ] This allows the reactive power Q , the power component with which no work can be performed, to be calculated. It is expressed in var.
7.12 | 7.12 | transformers. [ 7.11 ] This allows the reactive power Q , the power component with which no work can be performed, to be calculated. It is expressed in var. [
] | ] | [ 7.11 ] This allows the reactive power Q , the power component with which no work can be performed, to be calculated. It is expressed in var. [ 7.12
7.3 Fasor-notatie in het complexe vlak | 7.3 Phasor Notation in the Complex Plane | 7.11 ] This allows the reactive power Q , the power component with which no work can be performed, to be calculated. It is expressed in var. [ 7.12 ]
Behalve met een wisselende cosinusfunctie kan de spanning ook worden weergegeven met een ronddraaiende wijzer in het complexe vlak. De wijzer draait met dezelfde snelheid rond als de rotor van een generator, die uit twee magneetpolen is opgebouwd. De snelheid wordt uitgedrukt in de hoekfrequentie ω en is als zodanig terug te vinden in de vergelijkingen 7.1 en 7.2. Figuur 7.7 illustreert dit. | In addition to a varying cosine function, the voltage can also be represented by a rotating vector in the complex plane. The vector rotates at the same speed as the rotor of a generator, which is composed of two magnetic poles. The speed is expressed in the angular frequency ω and can be found as such in equations 7.1 and 7.2. Figure 7.7 illustrates this. | Q , the power component with which no work can be performed, to be calculated. It is expressed in var. [ 7.12 ] 7.3 Phasor Notation in the Complex Plane
Figuur 7.7 Vergelijking ronddraaiende generatorrotor en spanningswijzer in het complexe vlak | Figure 7.7 Comparison of rotating generator rotor and voltage phasor in the complex plane | is composed of two magnetic poles. The speed is expressed in the angular frequency ω and can be found as such in equations 7.1 and 7.2. Figure 7.7 illustrates this.
De ronddraaiende wijzer wordt beschreven door de cosinus-tijdfunctie van vergelijking 7.1 uit te breiden met een imaginair deel, waarmee de functie van de complexe momentane waarde ontstaat. Deze uitgebreide vergelijking beschrijft de positie van de pijlpunt van de wijzer van figuur 7.7 in het complexe vlak als functie van de tijd. De functie kan worden beschreven met cosinus- en sinustermen, maar ook met een complexe e-macht. | The rotating pointer is described by extending the cosine time function of equation 7.1 with an imaginary part, resulting in the function of the complex instantaneous value. This extended equation describes the position of the arrowhead of the pointer in figure 7.7 in the complex plane as a function of time. The function can be described with cosine and sine terms, but also with a complex exponential. | ω and can be found as such in equations 7.1 and 7.2. Figure 7.7 illustrates this. Figure 7.7 Comparison of rotating generator rotor and voltage phasor in the complex plane
[ | [ | the pointer in figure 7.7 in the complex plane as a function of time. The function can be described with cosine and sine terms, but also with a complex exponential.
7.13 | 7.13 | pointer in figure 7.7 in the complex plane as a function of time. The function can be described with cosine and sine terms, but also with a complex exponential. [
] | ] | in figure 7.7 in the complex plane as a function of time. The function can be described with cosine and sine terms, but also with a complex exponential. [ 7.13
De stroom wordt in het complexe vlak beschreven met onderstaande formule: | The current is described in the complex plane with the following formula: | figure 7.7 in the complex plane as a function of time. The function can be described with cosine and sine terms, but also with a complex exponential. [ 7.13 ]
[ | [ | function can be described with cosine and sine terms, but also with a complex exponential. [ 7.13 ] The current is described in the complex plane with the following formula:
7.14 | 7.14 | can be described with cosine and sine terms, but also with a complex exponential. [ 7.13 ] The current is described in the complex plane with the following formula: [
] | ] | be described with cosine and sine terms, but also with a complex exponential. [ 7.13 ] The current is described in the complex plane with the following formula: [ 7.14
Door gebruik te maken van vergelijking 7.4, kan de complexe stroomfunctie van vergelijking 7.14 ook als volgt geschreven worden: | By using equation 7.4, the complex current function from equation 7.14 can also be written as follows: | described with cosine and sine terms, but also with a complex exponential. [ 7.13 ] The current is described in the complex plane with the following formula: [ 7.14 ]
[ | [ | is described in the complex plane with the following formula: [ 7.14 ] By using equation 7.4, the complex current function from equation 7.14 can also be written as follows:
7.15 | 7.15 | described in the complex plane with the following formula: [ 7.14 ] By using equation 7.4, the complex current function from equation 7.14 can also be written as follows: [
] | ] | in the complex plane with the following formula: [ 7.14 ] By using equation 7.4, the complex current function from equation 7.14 can also be written as follows: [ 7.15
De uitgebreide complexe vergelijkingen voor spanning (7.13) en stroom (7.15) zijn de basis voor het complexe rekenen met stromen, spanningen en vermogens. In de elektrische energietechniek wordt veelvuldig gebruik gemaakt van wijzers in het complexe vlak. Daarbij wordt steeds gerekend met de effectieve waarden en wordt de tijdsafhankelijkheid weggelaten. De relatie tussen de effectieve waarde en de topwaarde is een factor | The extended complex equations for voltage (7.13) and current (7.15) form the basis for complex calculations involving currents, voltages, and power. In electrical power engineering, phasors in the complex plane are frequently used. In these calculations, the effective values are always used, and the time dependency is omitted. The relationship between the effective value and the peak value is a factor | the complex plane with the following formula: [ 7.14 ] By using equation 7.4, the complex current function from equation 7.14 can also be written as follows: [ 7.15 ]
√2 | √2 | frequently used. In these calculations, the effective values are always used, and the time dependency is omitted. The relationship between the effective value and the peak value is a factor
. De tijdsafhankelijkheid is in de complexe e-macht notatie vertegenwoordigd door de term | . The time dependency is represented in the complex exponential notation by the term | used. In these calculations, the effective values are always used, and the time dependency is omitted. The relationship between the effective value and the peak value is a factor √2
e | e | is omitted. The relationship between the effective value and the peak value is a factor √2 . The time dependency is represented in the complex exponential notation by the term
jωt | jωt | omitted. The relationship between the effective value and the peak value is a factor √2 . The time dependency is represented in the complex exponential notation by the term e
. Als vergelijking 7.13 wordt gedeeld door | . If equation 7.13 is divided by | The relationship between the effective value and the peak value is a factor √2 . The time dependency is represented in the complex exponential notation by the term e jωt
√2 | √2 | the peak value is a factor √2 . The time dependency is represented in the complex exponential notation by the term e jωt . If equation 7.13 is divided by
en door | and by | peak value is a factor √2 . The time dependency is represented in the complex exponential notation by the term e jωt . If equation 7.13 is divided by √2
e | e | is a factor √2 . The time dependency is represented in the complex exponential notation by the term e jωt . If equation 7.13 is divided by √2 and by
jωt | jωt | a factor √2 . The time dependency is represented in the complex exponential notation by the term e jωt . If equation 7.13 is divided by √2 and by e
, gaat deze over in de tijdsonafhankelijke fasor: | , this transforms into the time-independent phasor: | factor √2 . The time dependency is represented in the complex exponential notation by the term e jωt . If equation 7.13 is divided by √2 and by e jωt
[ | [ | represented in the complex exponential notation by the term e jωt . If equation 7.13 is divided by √2 and by e jωt , this transforms into the time-independent phasor:
7.16 | 7.16 | in the complex exponential notation by the term e jωt . If equation 7.13 is divided by √2 and by e jωt , this transforms into the time-independent phasor: [
] | ] | the complex exponential notation by the term e jωt . If equation 7.13 is divided by √2 and by e jωt , this transforms into the time-independent phasor: [ 7.16
Deze fasor is een wijzer in het complexe vlak, waarvan de lengte gelijk is aan de effectieve waarde | This phasor is a vector in the complex plane, whose length is equal to the effective value. | complex exponential notation by the term e jωt . If equation 7.13 is divided by √2 and by e jωt , this transforms into the time-independent phasor: [ 7.16 ]
U | U | by e jωt , this transforms into the time-independent phasor: [ 7.16 ] This phasor is a vector in the complex plane, whose length is equal to the effective value.
eff | eff | e jωt , this transforms into the time-independent phasor: [ 7.16 ] This phasor is a vector in the complex plane, whose length is equal to the effective value. U
van de spanning en de hoek op | of the voltage and the angle at | jωt , this transforms into the time-independent phasor: [ 7.16 ] This phasor is a vector in the complex plane, whose length is equal to the effective value. U eff
t=0 | t=0 | phasor: [ 7.16 ] This phasor is a vector in the complex plane, whose length is equal to the effective value. U eff of the voltage and the angle at
ten opzichte van de reële as gelijk is aan de spanningfasehoek | with respect to the real axis is equal to the voltage phase angle | [ 7.16 ] This phasor is a vector in the complex plane, whose length is equal to the effective value. U eff of the voltage and the angle at t=0
ψ | ψ | length is equal to the effective value. U eff of the voltage and the angle at t=0 with respect to the real axis is equal to the voltage phase angle
u | u | is equal to the effective value. U eff of the voltage and the angle at t=0 with respect to the real axis is equal to the voltage phase angle ψ
. | . | equal to the effective value. U eff of the voltage and the angle at t=0 with respect to the real axis is equal to the voltage phase angle ψ u
Figuur 7.8 Spanningfasor in het complexe vlak | Figure 7.8 Voltage phasor in the complex plane | to the effective value. U eff of the voltage and the angle at t=0 with respect to the real axis is equal to the voltage phase angle ψ u .
Figuur 7.9 Spanningfasor en na-ijlende (inductieve) stroomfasor in het complexe vlak | Figure 7.9 Voltage phasor and lagging (inductive) current phasor in the complex plane | voltage and the angle at t=0 with respect to the real axis is equal to the voltage phase angle ψ u . Figure 7.8 Voltage phasor in the complex plane
Dit gaat ook op voor de stroom. Als evenzo vergelijking 7.15 wordt gedeeld door | This also applies to the current. Similarly, if equation 7.15 is divided by | equal to the voltage phase angle ψ u . Figure 7.8 Voltage phasor in the complex plane Figure 7.9 Voltage phasor and lagging (inductive) current phasor in the complex plane
√2 | √2 | in the complex plane Figure 7.9 Voltage phasor and lagging (inductive) current phasor in the complex plane This also applies to the current. Similarly, if equation 7.15 is divided by
en door | and by | the complex plane Figure 7.9 Voltage phasor and lagging (inductive) current phasor in the complex plane This also applies to the current. Similarly, if equation 7.15 is divided by √2
e | e | plane Figure 7.9 Voltage phasor and lagging (inductive) current phasor in the complex plane This also applies to the current. Similarly, if equation 7.15 is divided by √2 and by
jωt | jωt | Figure 7.9 Voltage phasor and lagging (inductive) current phasor in the complex plane This also applies to the current. Similarly, if equation 7.15 is divided by √2 and by e
, gaat deze over in de fasor-notatie voor de stroom: | , this converts to the phasor notation for the current: | 7.9 Voltage phasor and lagging (inductive) current phasor in the complex plane This also applies to the current. Similarly, if equation 7.15 is divided by √2 and by e jωt
[ | [ | complex plane This also applies to the current. Similarly, if equation 7.15 is divided by √2 and by e jωt , this converts to the phasor notation for the current:
7.17 | 7.17 | plane This also applies to the current. Similarly, if equation 7.15 is divided by √2 and by e jωt , this converts to the phasor notation for the current: [
] | ] | This also applies to the current. Similarly, if equation 7.15 is divided by √2 and by e jωt , this converts to the phasor notation for the current: [ 7.17
Figuur 7.9 illustreert dit voor de fasors van spanning en na-ijlende (inductieve) stroom. Hierin is ook het verband tussen de fasehoeken van spanning ( | Figure 7.9 illustrates this for the phasors of voltage and lagging (inductive) current. It also shows the relationship between the phase angles of voltage | also applies to the current. Similarly, if equation 7.15 is divided by √2 and by e jωt , this converts to the phasor notation for the current: [ 7.17 ]
ψ | ψ | for the current: [ 7.17 ] Figure 7.9 illustrates this for the phasors of voltage and lagging (inductive) current. It also shows the relationship between the phase angles of voltage
u | u | the current: [ 7.17 ] Figure 7.9 illustrates this for the phasors of voltage and lagging (inductive) current. It also shows the relationship between the phase angles of voltage ψ
) en stroom ( | ) and current ( | current: [ 7.17 ] Figure 7.9 illustrates this for the phasors of voltage and lagging (inductive) current. It also shows the relationship between the phase angles of voltage ψ u
ψ | ψ | Figure 7.9 illustrates this for the phasors of voltage and lagging (inductive) current. It also shows the relationship between the phase angles of voltage ψ u ) and current (
i | i | 7.9 illustrates this for the phasors of voltage and lagging (inductive) current. It also shows the relationship between the phase angles of voltage ψ u ) and current ( ψ
) en de verschilhoek ( | ) and the phase difference ( | illustrates this for the phasors of voltage and lagging (inductive) current. It also shows the relationship between the phase angles of voltage ψ u ) and current ( ψ i
φ | φ | voltage and lagging (inductive) current. It also shows the relationship between the phase angles of voltage ψ u ) and current ( ψ i ) and the phase difference (
) zichtbaar. | ) visible. | and lagging (inductive) current. It also shows the relationship between the phase angles of voltage ψ u ) and current ( ψ i ) and the phase difference ( φ
Het complexe vermogen is gedefinieerd met de fasor | The complex power is defined with the phasor | (inductive) current. It also shows the relationship between the phase angles of voltage ψ u ) and current ( ψ i ) and the phase difference ( φ ) visible.
S | S | the phase angles of voltage ψ u ) and current ( ψ i ) and the phase difference ( φ ) visible. The complex power is defined with the phasor
, waarvan de lengte | , of which the length | phase angles of voltage ψ u ) and current ( ψ i ) and the phase difference ( φ ) visible. The complex power is defined with the phasor S
S | S | u ) and current ( ψ i ) and the phase difference ( φ ) visible. The complex power is defined with the phasor S , of which the length
gelijk is aan het schijnbare vermogen. Het reële deel is gelijk aan het actieve vermogen | is equal to the apparent power. The real part is equal to the active power. | ) and current ( ψ i ) and the phase difference ( φ ) visible. The complex power is defined with the phasor S , of which the length S
P | P | The complex power is defined with the phasor S , of which the length S is equal to the apparent power. The real part is equal to the active power.
en het imaginaire deel is gelijk aan het blindvermogen | and the imaginary part is equal to the reactive power | complex power is defined with the phasor S , of which the length S is equal to the apparent power. The real part is equal to the active power. P
Q | Q | which the length S is equal to the apparent power. The real part is equal to the active power. P and the imaginary part is equal to the reactive power
. | . | the length S is equal to the apparent power. The real part is equal to the active power. P and the imaginary part is equal to the reactive power Q
[ | [ | length S is equal to the apparent power. The real part is equal to the active power. P and the imaginary part is equal to the reactive power Q .
7.18 | 7.18 | S is equal to the apparent power. The real part is equal to the active power. P and the imaginary part is equal to the reactive power Q . [
] | ] | is equal to the apparent power. The real part is equal to the active power. P and the imaginary part is equal to the reactive power Q . [ 7.18
Door gebruik te maken van vergelijkingen 7.10 voor P en vergelijking 7.12 voor | By using equations 7.10 for P and equation 7.12 for | equal to the apparent power. The real part is equal to the active power. P and the imaginary part is equal to the reactive power Q . [ 7.18 ]
Q | Q | to the active power. P and the imaginary part is equal to the reactive power Q . [ 7.18 ] By using equations 7.10 for P and equation 7.12 for
gaat vergelijking 7.18 voor | equation 7.18 becomes | the active power. P and the imaginary part is equal to the reactive power Q . [ 7.18 ] By using equations 7.10 for P and equation 7.12 for Q
S | S | P and the imaginary part is equal to the reactive power Q . [ 7.18 ] By using equations 7.10 for P and equation 7.12 for Q equation 7.18 becomes
over in onderstaande vergelijking, waarbij de cosinus- en sinustermen ook beschreven kunnen worden met een complexe e-macht. | in the following equation, where the cosine and sine terms can also be described with a complex exponential. | and the imaginary part is equal to the reactive power Q . [ 7.18 ] By using equations 7.10 for P and equation 7.12 for Q equation 7.18 becomes S
[ | [ | 7.10 for P and equation 7.12 for Q equation 7.18 becomes S in the following equation, where the cosine and sine terms can also be described with a complex exponential.
7.19 | 7.19 | for P and equation 7.12 for Q equation 7.18 becomes S in the following equation, where the cosine and sine terms can also be described with a complex exponential. [
] | ] | P and equation 7.12 for Q equation 7.18 becomes S in the following equation, where the cosine and sine terms can also be described with a complex exponential. [ 7.19
De hoek van de vermogenfasor | The angle of the power phasor | and equation 7.12 for Q equation 7.18 becomes S in the following equation, where the cosine and sine terms can also be described with a complex exponential. [ 7.19 ]
S | S | 7.18 becomes S in the following equation, where the cosine and sine terms can also be described with a complex exponential. [ 7.19 ] The angle of the power phasor
wordt dus geheel bepaald door de hoek | is therefore entirely determined by the angle | becomes S in the following equation, where the cosine and sine terms can also be described with a complex exponential. [ 7.19 ] The angle of the power phasor S
φ | φ | the cosine and sine terms can also be described with a complex exponential. [ 7.19 ] The angle of the power phasor S is therefore entirely determined by the angle
tussen de spanning- en stroomfasoren | between the voltage and current phasors | cosine and sine terms can also be described with a complex exponential. [ 7.19 ] The angle of the power phasor S is therefore entirely determined by the angle φ
U | U | be described with a complex exponential. [ 7.19 ] The angle of the power phasor S is therefore entirely determined by the angle φ between the voltage and current phasors
en | en | described with a complex exponential. [ 7.19 ] The angle of the power phasor S is therefore entirely determined by the angle φ between the voltage and current phasors U
I | I | with a complex exponential. [ 7.19 ] The angle of the power phasor S is therefore entirely determined by the angle φ between the voltage and current phasors U en
. Verder uitwerken van vergelijking 7.19, door | Further elaboration of equation 7.19, by | a complex exponential. [ 7.19 ] The angle of the power phasor S is therefore entirely determined by the angle φ between the voltage and current phasors U en I
U | U | The angle of the power phasor S is therefore entirely determined by the angle φ between the voltage and current phasors U en I Further elaboration of equation 7.19, by
eff | eff | angle of the power phasor S is therefore entirely determined by the angle φ between the voltage and current phasors U en I Further elaboration of equation 7.19, by U
te vermenigvuldigen met | to multiply by | of the power phasor S is therefore entirely determined by the angle φ between the voltage and current phasors U en I Further elaboration of equation 7.19, by U eff
e | e | phasor S is therefore entirely determined by the angle φ between the voltage and current phasors U en I Further elaboration of equation 7.19, by U eff to multiply by
jψu | jψu | S is therefore entirely determined by the angle φ between the voltage and current phasors U en I Further elaboration of equation 7.19, by U eff to multiply by e
en door | and by | is therefore entirely determined by the angle φ between the voltage and current phasors U en I Further elaboration of equation 7.19, by U eff to multiply by e jψu
I | I | entirely determined by the angle φ between the voltage and current phasors U en I Further elaboration of equation 7.19, by U eff to multiply by e jψu and by
eff | eff | determined by the angle φ between the voltage and current phasors U en I Further elaboration of equation 7.19, by U eff to multiply by e jψu and by I
te vermenigvuldigen met | to multiply by | by the angle φ between the voltage and current phasors U en I Further elaboration of equation 7.19, by U eff to multiply by e jψu and by I eff
e | e | φ between the voltage and current phasors U en I Further elaboration of equation 7.19, by U eff to multiply by e jψu and by I eff to multiply by
–jψi | –jψi | between the voltage and current phasors U en I Further elaboration of equation 7.19, by U eff to multiply by e jψu and by I eff to multiply by e
, levert: | , yields: | the voltage and current phasors U en I Further elaboration of equation 7.19, by U eff to multiply by e jψu and by I eff to multiply by e –jψi
[ | [ | and current phasors U en I Further elaboration of equation 7.19, by U eff to multiply by e jψu and by I eff to multiply by e –jψi , yields:
7.20 | 7.20 | current phasors U en I Further elaboration of equation 7.19, by U eff to multiply by e jψu and by I eff to multiply by e –jψi , yields: [
] | ] | phasors U en I Further elaboration of equation 7.19, by U eff to multiply by e jψu and by I eff to multiply by e –jψi , yields: [ 7.20
In vergelijking 7.20 valt het op dat de eerste term gelijk is aan de spanningfasor | In equation 7.20, it is noticeable that the first term is equal to the voltage phasor | U en I Further elaboration of equation 7.19, by U eff to multiply by e jψu and by I eff to multiply by e –jψi , yields: [ 7.20 ]
U | U | and by I eff to multiply by e –jψi , yields: [ 7.20 ] In equation 7.20, it is noticeable that the first term is equal to the voltage phasor
en dat de tweede term, op het minteken van de complexe e-macht na, gelijk is aan de stroomfasor | and that the second term, except for the minus sign of the complex exponential, is equal to the current phasor | by I eff to multiply by e –jψi , yields: [ 7.20 ] In equation 7.20, it is noticeable that the first term is equal to the voltage phasor U
I | I | the first term is equal to the voltage phasor U and that the second term, except for the minus sign of the complex exponential, is equal to the current phasor
. Voor het vervolg wordt nu de toegevoegd complexe waarde van de fasor | . For the continuation, the added complex value of the phasor is now considered | first term is equal to the voltage phasor U and that the second term, except for the minus sign of the complex exponential, is equal to the current phasor I
I | I | except for the minus sign of the complex exponential, is equal to the current phasor I . For the continuation, the added complex value of the phasor is now considered
gedefinieerd, waarvoor geldt dat de imaginaire waarde een tegengesteld teken heeft: | defined, for which the imaginary value has an opposite sign: | for the minus sign of the complex exponential, is equal to the current phasor I . For the continuation, the added complex value of the phasor is now considered I
[ | [ | to the current phasor I . For the continuation, the added complex value of the phasor is now considered I defined, for which the imaginary value has an opposite sign:
7.21 | 7.21 | the current phasor I . For the continuation, the added complex value of the phasor is now considered I defined, for which the imaginary value has an opposite sign: [
] | ] | current phasor I . For the continuation, the added complex value of the phasor is now considered I defined, for which the imaginary value has an opposite sign: [ 7.21
Hierdoor kan het complexe vermogen als volgt worden geschreven: | As a result, the complex power can be written as follows: | phasor I . For the continuation, the added complex value of the phasor is now considered I defined, for which the imaginary value has an opposite sign: [ 7.21 ]
[ | [ | the phasor is now considered I defined, for which the imaginary value has an opposite sign: [ 7.21 ] As a result, the complex power can be written as follows:
7.22 | 7.22 | phasor is now considered I defined, for which the imaginary value has an opposite sign: [ 7.21 ] As a result, the complex power can be written as follows: [
] | ] | is now considered I defined, for which the imaginary value has an opposite sign: [ 7.21 ] As a result, the complex power can be written as follows: [ 7.22
Deze laatste is de bekende vergelijking waarmee het complexe vermogen direct uit de complexe spanning en stroom wordt bepaald. Deze vergelijking is de basis van elke loadflowberekening. | This last one is the well-known equation by which the complex power is directly determined from the complex voltage and current. This equation is the basis of every load flow calculation. | now considered I defined, for which the imaginary value has an opposite sign: [ 7.21 ] As a result, the complex power can be written as follows: [ 7.22 ]
Bij het vergelijken van figuur 7.9 met de in tabel 7.2 gegeven vectordiagrammen wordt de relatie tussen fasehoek (voorijlend of na-ijlend) en belastingtype duidelijk. Onderstaand rekenvoorbeeld gaat hier nader op in. Uitgangspunt is een spanning van 1 V en een belasting met een inductieve impedantie van 1+j Ω. Onder gebruikmaking van de motorconventie volgt: | When comparing figure 7.9 with the vector diagrams given in table 7.2, the relationship between phase angle (leading or lagging) and load type becomes clear. The following calculation example elaborates on this. The starting point is a voltage of 1 V and a load with an inductive impedance of 1+j Ω. Using the motor convention, the following results: | last one is the well-known equation by which the complex power is directly determined from the complex voltage and current. This equation is the basis of every load flow calculation.
[ | [ | example elaborates on this. The starting point is a voltage of 1 V and a load with an inductive impedance of 1+j Ω. Using the motor convention, the following results:
7.23 | 7.23 | elaborates on this. The starting point is a voltage of 1 V and a load with an inductive impedance of 1+j Ω. Using the motor convention, the following results: [
] | ] | on this. The starting point is a voltage of 1 V and a load with an inductive impedance of 1+j Ω. Using the motor convention, the following results: [ 7.23
Volgens vergelijking 7.23 is het actieve vermogen P gelijk aan 0,5 W en is het blindvermogen Q gelijk aan 0,5 var. Ter controle van de juistheid van de tekenafspraken van de vermogens en de fasehoeken kunnen de vermogens ook worden afgeleid uit het schijnvermogen en het hoekverschil tussen de spanning en de stroom: | According to equation 7.23, the active power P is equal to 0.5 W and the reactive power Q is equal to 0.5 var. To verify the correctness of the sign conventions for the powers and the phase angles, the powers can also be derived from the apparent power and the phase difference between the voltage and the current: | this. The starting point is a voltage of 1 V and a load with an inductive impedance of 1+j Ω. Using the motor convention, the following results: [ 7.23 ]
[ | [ | the sign conventions for the powers and the phase angles, the powers can also be derived from the apparent power and the phase difference between the voltage and the current:
7.24 | 7.24 | sign conventions for the powers and the phase angles, the powers can also be derived from the apparent power and the phase difference between the voltage and the current: [
] | ] | conventions for the powers and the phase angles, the powers can also be derived from the apparent power and the phase difference between the voltage and the current: [ 7.24
7.4 Driefasen wisselstroomsysteem | 7.4 Three-phase alternating current system | for the powers and the phase angles, the powers can also be derived from the apparent power and the phase difference between the voltage and the current: [ 7.24 ]
De meeste wisselstroomsystemen zijn uitgevoerd als driefasensystemen, waarvan de drie fasen telkens een hoek van 120 graden met elkaar maken. In radialen is de onderlinge hoek dan gelijk aan | Most alternating current systems are designed as three-phase systems, where the three phases each form an angle of 120 degrees with each other. In radians, the mutual angle is then equal to | phase angles, the powers can also be derived from the apparent power and the phase difference between the voltage and the current: [ 7.24 ] 7.4 Three-phase alternating current system
2/3 π | 2/3 π | current systems are designed as three-phase systems, where the three phases each form an angle of 120 degrees with each other. In radians, the mutual angle is then equal to
. Figuur 7.10 toont hoe met drie paren van spoelen, die telkens 120 graden ten opzichte van elkaar zijn aangebracht op de stator van een generator, de spanningen worden opgewekt. In het voorbeeld zijn de spoelen in ster geschakeld. Door het linksom draaien van de rotor is de volgorde van de fasen: a, b, c. | Figure 7.10 shows how three pairs of coils, each positioned 120 degrees relative to each other on the stator of a generator, generate the voltages. In the example, the coils are connected in a star configuration. Due to the counterclockwise rotation of the rotor, the phase sequence is: a, b, c. | are designed as three-phase systems, where the three phases each form an angle of 120 degrees with each other. In radians, the mutual angle is then equal to 2/3 π
Figuur 7.10 Driefasengenerator als bron van drie fasenspanningen, in ster geschakeld | Figure 7.10 Three-phase generator as a source of three-phase voltages, star-connected | generator, generate the voltages. In the example, the coils are connected in a star configuration. Due to the counterclockwise rotation of the rotor, the phase sequence is: a, b, c.
De complexe momentane spanning van een gebalanceerde driefasige spanningsbron kan, naar analogie van vergelijking 7.13 in de vorige paragraaf, worden beschreven met onderstaande drie tijdfuncties voor de fasen a, b en c. Hierin zijn de drie spanningswijzers telkens 120 graden onderling verschoven. In radialen is dat | The complex instantaneous voltage of a balanced three-phase voltage source can, by analogy with equation 7.13 in the previous paragraph, be described with the following three time functions for phases a, b, and c. Here, the three voltage phasors are each shifted by 120 degrees relative to each other. In radians, that is | in a star configuration. Due to the counterclockwise rotation of the rotor, the phase sequence is: a, b, c. Figure 7.10 Three-phase generator as a source of three-phase voltages, star-connected
–2/3 π | –2/3 π | the following three time functions for phases a, b, and c. Here, the three voltage phasors are each shifted by 120 degrees relative to each other. In radians, that is
en | en | three time functions for phases a, b, and c. Here, the three voltage phasors are each shifted by 120 degrees relative to each other. In radians, that is –2/3 π
–4/3 π | –4/3 π | time functions for phases a, b, and c. Here, the three voltage phasors are each shifted by 120 degrees relative to each other. In radians, that is –2/3 π en
. De waarde van | . The value of | for phases a, b, and c. Here, the three voltage phasors are each shifted by 120 degrees relative to each other. In radians, that is –2/3 π en –4/3 π
–4/3 π | –4/3 π | and c. Here, the three voltage phasors are each shifted by 120 degrees relative to each other. In radians, that is –2/3 π en –4/3 π . The value of
komt overeen met | corresponds to | Here, the three voltage phasors are each shifted by 120 degrees relative to each other. In radians, that is –2/3 π en –4/3 π . The value of –4/3 π
+2/3 π | +2/3 π | three voltage phasors are each shifted by 120 degrees relative to each other. In radians, that is –2/3 π en –4/3 π . The value of –4/3 π corresponds to
. In de functies voor de drie spanningen wordt bij | . In the functions for the three voltages, the | phasors are each shifted by 120 degrees relative to each other. In radians, that is –2/3 π en –4/3 π . The value of –4/3 π corresponds to +2/3 π
ψ | ψ | each other. In radians, that is –2/3 π en –4/3 π . The value of –4/3 π corresponds to +2/3 π . In the functions for the three voltages, the
u | u | other. In radians, that is –2/3 π en –4/3 π . The value of –4/3 π corresponds to +2/3 π . In the functions for the three voltages, the ψ
voor de drie fasen respectievelijk de waarden | for the three phases respectively the values | In radians, that is –2/3 π en –4/3 π . The value of –4/3 π corresponds to +2/3 π . In the functions for the three voltages, the ψ u
0 | 0 | –4/3 π . The value of –4/3 π corresponds to +2/3 π . In the functions for the three voltages, the ψ u for the three phases respectively the values
, | , | π . The value of –4/3 π corresponds to +2/3 π . In the functions for the three voltages, the ψ u for the three phases respectively the values 0
–2/3 π | –2/3 π | . The value of –4/3 π corresponds to +2/3 π . In the functions for the three voltages, the ψ u for the three phases respectively the values 0 ,
en | en | value of –4/3 π corresponds to +2/3 π . In the functions for the three voltages, the ψ u for the three phases respectively the values 0 , –2/3 π
+2/3 π | +2/3 π | of –4/3 π corresponds to +2/3 π . In the functions for the three voltages, the ψ u for the three phases respectively the values 0 , –2/3 π en
opgeteld. | added. | π corresponds to +2/3 π . In the functions for the three voltages, the ψ u for the three phases respectively the values 0 , –2/3 π en +2/3 π
[ | [ | corresponds to +2/3 π . In the functions for the three voltages, the ψ u for the three phases respectively the values 0 , –2/3 π en +2/3 π added.
7.25 | 7.25 | to +2/3 π . In the functions for the three voltages, the ψ u for the three phases respectively the values 0 , –2/3 π en +2/3 π added. [
] | ] | +2/3 π . In the functions for the three voltages, the ψ u for the three phases respectively the values 0 , –2/3 π en +2/3 π added. [ 7.25
In bovenstaande vergelijkingen is | In the above equations, | π . In the functions for the three voltages, the ψ u for the three phases respectively the values 0 , –2/3 π en +2/3 π added. [ 7.25 ]
y | y | functions for the three voltages, the ψ u for the three phases respectively the values 0 , –2/3 π en +2/3 π added. [ 7.25 ] In the above equations,
u | u | for the three voltages, the ψ u for the three phases respectively the values 0 , –2/3 π en +2/3 π added. [ 7.25 ] In the above equations, y
de hoek van de spanning van fase a op | the angle of the voltage of phase a at | the three voltages, the ψ u for the three phases respectively the values 0 , –2/3 π en +2/3 π added. [ 7.25 ] In the above equations, y u
t=0 | t=0 | phases respectively the values 0 , –2/3 π en +2/3 π added. [ 7.25 ] In the above equations, y u the angle of the voltage of phase a at
. Figuur 7.11 illustreert dit, waarbij te zien is dat de fasevolgorde is: a-b-c. In de afbeelding is | Figure 7.11 illustrates this, showing that the phase sequence is: a-b-c. In the image, | respectively the values 0 , –2/3 π en +2/3 π added. [ 7.25 ] In the above equations, y u the angle of the voltage of phase a at t=0
ψ | ψ | In the above equations, y u the angle of the voltage of phase a at t=0 Figure 7.11 illustrates this, showing that the phase sequence is: a-b-c. In the image,
u | u | the above equations, y u the angle of the voltage of phase a at t=0 Figure 7.11 illustrates this, showing that the phase sequence is: a-b-c. In the image, ψ
gelijk aan nul genomen. | taken as zero. | above equations, y u the angle of the voltage of phase a at t=0 Figure 7.11 illustrates this, showing that the phase sequence is: a-b-c. In the image, ψ u
Figuur 7.11 Gebalanceerde driefasenspanningen als functie van de tijd | Figure 7.11 Balanced three-phase voltages as a function of time | u the angle of the voltage of phase a at t=0 Figure 7.11 illustrates this, showing that the phase sequence is: a-b-c. In the image, ψ u taken as zero.
7.5 Methode symmetrische componenten | 7.5 Symmetrical Components Method | t=0 Figure 7.11 illustrates this, showing that the phase sequence is: a-b-c. In the image, ψ u taken as zero. Figure 7.11 Balanced three-phase voltages as a function of time
De berekeningen aan driefasensystemen vereisen dat gelijktijdig aan de drie fasen van het totale systeem wordt gerekend. De berekeningen worden vele malen eenvoudiger indien ervan wordt uitgegaan dat de spanningen in het system perfect driefasensymmetrisch, ofwel gebalanceerd, zijn. Een driefasensysteem wordt in dat geval gemodelleerd alsof er maar één fase aanwezig is. De spanningen in de andere fasen kunnen dan eenvoudig worden afgeleid omdat bekend is dat zij plus of min 120 graden verschillen van de berekende fase. In het vervolg wordt ervan uitgegaan dat de in het net opgestelde voedingsbronnen een gebalanceerde spanning leveren. De kabels en transformatoren worden gemodelleerd als driefasensymmetrische componenten. | Calculations for three-phase systems require simultaneous consideration of all three phases of the entire system. The calculations become much simpler if it is assumed that the voltages in the system are perfectly three-phase symmetrical, or balanced. In that case, a three-phase system is modeled as if only one phase is present. The voltages in the other phases can then be easily derived because it is known that they differ by plus or minus 120 degrees from the calculated phase. Henceforth, it is assumed that the power sources installed in the network provide a balanced voltage. The cables and transformers are modeled as three-phase symmetrical components. | this, showing that the phase sequence is: a-b-c. In the image, ψ u taken as zero. Figure 7.11 Balanced three-phase voltages as a function of time 7.5 Symmetrical Components Method
Er zijn echter altijd oorzaken van onbalans, zoals een asymmetrische belasting of een asymmetrische storing in het net. Om niet terug te vallen op de berekeningen met alle fasen tegelijk, worden dit soort asymmetrische situaties in de meeste berekeningsmethoden berekend met behulp van de methode van de symmetrische componenten. Deze methode is in 1918 beschreven door Fortescue. Ook de internationale standaard IEC 60909 voor kortsluitberekeningen maakt gebruik van deze methode. | However, there are always causes of imbalance, such as an asymmetrical load or an asymmetrical fault in the network. To avoid reverting to calculations with all phases simultaneously, these types of asymmetrical situations are calculated in most methods using the symmetrical components method. This method was described by Fortescue in 1918. The international standard IEC 60909 for short-circuit calculations also uses this method. | from the calculated phase. Henceforth, it is assumed that the power sources installed in the network provide a balanced voltage. The cables and transformers are modeled as three-phase symmetrical components.
Belangrijk uitgangspunt bij de methode is dat het net symmetrisch is. De voedingen zijn over de drie fasen verdeeld en de verbindingen zijn driefasig symmetrisch. De methode van symmetrische componenten transformeert een driefasig wisselstroomnet in drie onafhankelijke enkelpolige systemen, genaamd: normaal netwerk, invers netwerk en homopolair netwerk. De Engelstalige benamingen voor deze drie systemen zijn respectievelijk: positive sequence, negative sequence en zero sequence. De specifieke onbalans op een foutplaats bepaalt de wijze waarop de drie onafhankelijke enkelpolige systemen (componentennetwerken) met elkaar worden verbonden. Een belangrijk voordeel van deze methode is dat netten en storingen in netten met deze methode eenvoudig kunnen worden doorgerekend. De methode maakt het mogelijk de berekeningen met de hand uit te voeren. | An important premise of the method is that the network is symmetrical. The power supplies are distributed over the three phases, and the connections are three-phase symmetrical. The symmetrical components method transforms a three-phase AC network into three independent single-phase systems, called: normal network, inverse network, and homopolar network. The English terms for these three systems are respectively: positive sequence, negative sequence, and zero sequence. The specific imbalance at a fault location determines how the three independent single-phase systems (component networks) are interconnected. A significant advantage of this method is that networks and faults in networks can be easily calculated using this method. The method allows for calculations to be performed manually. | are calculated in most methods using the symmetrical components method. This method was described by Fortescue in 1918. The international standard IEC 60909 for short-circuit calculations also uses this method.
7.5.1 Een nieuwe fasor-notatie | 7.5.1 A new phasor notation | interconnected. A significant advantage of this method is that networks and faults in networks can be easily calculated using this method. The method allows for calculations to be performed manually.
De basis voor de symmetrische componentenmethode wordt gevormd door drie vectoren in het complexe vlak, die 120 graden van elkaar zijn verschoven en de lengte 1 hebben. De methode introduceert een complexe vector | The basis for the symmetrical components method is formed by three vectors in the complex plane, which are shifted 120 degrees from each other and have a length of 1. The method introduces a complex vector | this method is that networks and faults in networks can be easily calculated using this method. The method allows for calculations to be performed manually. 7.5.1 A new phasor notation
a | a | method is formed by three vectors in the complex plane, which are shifted 120 degrees from each other and have a length of 1. The method introduces a complex vector
, van lengte 1 en met een hoek van 120 graden ten opzichte van de reële as. Een hoek van 120 graden is gelijk aan | , with a length of 1 and an angle of 120 degrees relative to the real axis. An angle of 120 degrees is equal to | is formed by three vectors in the complex plane, which are shifted 120 degrees from each other and have a length of 1. The method introduces a complex vector a
2/3 π | 2/3 π | introduces a complex vector a , with a length of 1 and an angle of 120 degrees relative to the real axis. An angle of 120 degrees is equal to
radialen. Deze vector kan op diverse manieren worden beschreven: | radians. This vector can be described in various ways: | complex vector a , with a length of 1 and an angle of 120 degrees relative to the real axis. An angle of 120 degrees is equal to 2/3 π
Complexe e-macht: | Complex exponential: | and an angle of 120 degrees relative to the real axis. An angle of 120 degrees is equal to 2/3 π radians. This vector can be described in various ways:
Polair: | Polar: | angle of 120 degrees relative to the real axis. An angle of 120 degrees is equal to 2/3 π radians. This vector can be described in various ways: Complex exponential:
Polair: | Polar: | of 120 degrees relative to the real axis. An angle of 120 degrees is equal to 2/3 π radians. This vector can be described in various ways: Complex exponential: Polar:
[ | [ | 120 degrees relative to the real axis. An angle of 120 degrees is equal to 2/3 π radians. This vector can be described in various ways: Complex exponential: Polar: Polar:
7.26 | 7.26 | degrees relative to the real axis. An angle of 120 degrees is equal to 2/3 π radians. This vector can be described in various ways: Complex exponential: Polar: Polar: [
] | ] | relative to the real axis. An angle of 120 degrees is equal to 2/3 π radians. This vector can be described in various ways: Complex exponential: Polar: Polar: [ 7.26
Door een vector met | By rotating a vector by | to the real axis. An angle of 120 degrees is equal to 2/3 π radians. This vector can be described in various ways: Complex exponential: Polar: Polar: [ 7.26 ]
a | a | angle of 120 degrees is equal to 2/3 π radians. This vector can be described in various ways: Complex exponential: Polar: Polar: [ 7.26 ] By rotating a vector by
te vermenigvuldigen ontstaat een nieuwe vector die 120 graden, ofwel | by multiplying, a new vector is created that is 120 degrees, or | of 120 degrees is equal to 2/3 π radians. This vector can be described in various ways: Complex exponential: Polar: Polar: [ 7.26 ] By rotating a vector by a
2/3 π | 2/3 π | be described in various ways: Complex exponential: Polar: Polar: [ 7.26 ] By rotating a vector by a by multiplying, a new vector is created that is 120 degrees, or
, verder gedraaid is. Zo ontstaat de vector | , further rotated. This creates the vector | in various ways: Complex exponential: Polar: Polar: [ 7.26 ] By rotating a vector by a by multiplying, a new vector is created that is 120 degrees, or 2/3 π
a | a | [ 7.26 ] By rotating a vector by a by multiplying, a new vector is created that is 120 degrees, or 2/3 π , further rotated. This creates the vector
2 | 2 | 7.26 ] By rotating a vector by a by multiplying, a new vector is created that is 120 degrees, or 2/3 π , further rotated. This creates the vector a
door de vector | by the vector | ] By rotating a vector by a by multiplying, a new vector is created that is 120 degrees, or 2/3 π , further rotated. This creates the vector a 2
a | a | a vector by a by multiplying, a new vector is created that is 120 degrees, or 2/3 π , further rotated. This creates the vector a 2 by the vector
met zichzelf te vermenigvuldigen. De hoek is 240 graden, ofwel | by multiplying itself. The angle is 240 degrees, or | vector by a by multiplying, a new vector is created that is 120 degrees, or 2/3 π , further rotated. This creates the vector a 2 by the vector a
4/3 π | 4/3 π | created that is 120 degrees, or 2/3 π , further rotated. This creates the vector a 2 by the vector a by multiplying itself. The angle is 240 degrees, or
, ten opzichte van de reële as en dat is gelijk aan –120 graden, ofwel | , relative to the real axis and that is equal to -120 degrees, or | is 120 degrees, or 2/3 π , further rotated. This creates the vector a 2 by the vector a by multiplying itself. The angle is 240 degrees, or 4/3 π
–2/3 π | –2/3 π | 2 by the vector a by multiplying itself. The angle is 240 degrees, or 4/3 π , relative to the real axis and that is equal to -120 degrees, or
. Figuur 7.12 illustreert dit voor de vectoren | Figure 7.12 illustrates this for the vectors | the vector a by multiplying itself. The angle is 240 degrees, or 4/3 π , relative to the real axis and that is equal to -120 degrees, or –2/3 π
1, a | 1, a | angle is 240 degrees, or 4/3 π , relative to the real axis and that is equal to -120 degrees, or –2/3 π Figure 7.12 illustrates this for the vectors
en | en | 240 degrees, or 4/3 π , relative to the real axis and that is equal to -120 degrees, or –2/3 π Figure 7.12 illustrates this for the vectors 1, a
a | a | degrees, or 4/3 π , relative to the real axis and that is equal to -120 degrees, or –2/3 π Figure 7.12 illustrates this for the vectors 1, a en
2 | 2 | or 4/3 π , relative to the real axis and that is equal to -120 degrees, or –2/3 π Figure 7.12 illustrates this for the vectors 1, a en a
. | . | 4/3 π , relative to the real axis and that is equal to -120 degrees, or –2/3 π Figure 7.12 illustrates this for the vectors 1, a en a 2
Figuur 7.12 Vectoren 1, a en a | Figure 7.12 Vectors 1, a, and a | π , relative to the real axis and that is equal to -120 degrees, or –2/3 π Figure 7.12 illustrates this for the vectors 1, a en a 2 .
2 | 2 | and that is equal to -120 degrees, or –2/3 π Figure 7.12 illustrates this for the vectors 1, a en a 2 . Figure 7.12 Vectors 1, a, and a
in het complexe vlak | in the complex plane | that is equal to -120 degrees, or –2/3 π Figure 7.12 illustrates this for the vectors 1, a en a 2 . Figure 7.12 Vectors 1, a, and a 2
De drie vectoren worden op de volgende wijze als complexe e-macht of polair beschreven: | The three vectors are described as complex exponentials or in polar form as follows: | -120 degrees, or –2/3 π Figure 7.12 illustrates this for the vectors 1, a en a 2 . Figure 7.12 Vectors 1, a, and a 2 in the complex plane
[ | [ | en a 2 . Figure 7.12 Vectors 1, a, and a 2 in the complex plane The three vectors are described as complex exponentials or in polar form as follows:
7.27 | 7.27 | a 2 . Figure 7.12 Vectors 1, a, and a 2 in the complex plane The three vectors are described as complex exponentials or in polar form as follows: [
] | ] | 2 . Figure 7.12 Vectors 1, a, and a 2 in the complex plane The three vectors are described as complex exponentials or in polar form as follows: [ 7.27
De vectoriële som van deze drie vectoren is gelijk aan nul. Dat betekent dat: | The vector sum of these three vectors is equal to zero. This means that: | . Figure 7.12 Vectors 1, a, and a 2 in the complex plane The three vectors are described as complex exponentials or in polar form as follows: [ 7.27 ]
[ | [ | three vectors are described as complex exponentials or in polar form as follows: [ 7.27 ] The vector sum of these three vectors is equal to zero. This means that:
7.28 | 7.28 | vectors are described as complex exponentials or in polar form as follows: [ 7.27 ] The vector sum of these three vectors is equal to zero. This means that: [
] | ] | are described as complex exponentials or in polar form as follows: [ 7.27 ] The vector sum of these three vectors is equal to zero. This means that: [ 7.28
Met behulp van deze vectoren kunnen de vergelijkingen van vergelijking 7.25 voor de momentane waarden van de spanning van een gebalanceerd stelsel ook als volgt geschreven worden: | Using these vectors, the equations from equation 7.25 for the instantaneous values of the voltage of a balanced system can also be written as follows: | described as complex exponentials or in polar form as follows: [ 7.27 ] The vector sum of these three vectors is equal to zero. This means that: [ 7.28 ]
[ | [ | means that: [ 7.28 ] Using these vectors, the equations from equation 7.25 for the instantaneous values of the voltage of a balanced system can also be written as follows:
7.29 | 7.29 | that: [ 7.28 ] Using these vectors, the equations from equation 7.25 for the instantaneous values of the voltage of a balanced system can also be written as follows: [
] | ] | [ 7.28 ] Using these vectors, the equations from equation 7.25 for the instantaneous values of the voltage of a balanced system can also be written as follows: [ 7.29
Hierbij wordt opgemerkt dat | It is noted that | 7.28 ] Using these vectors, the equations from equation 7.25 for the instantaneous values of the voltage of a balanced system can also be written as follows: [ 7.29 ]
e | e | vectors, the equations from equation 7.25 for the instantaneous values of the voltage of a balanced system can also be written as follows: [ 7.29 ] It is noted that
-j 2/3 π | -j 2/3 π | the equations from equation 7.25 for the instantaneous values of the voltage of a balanced system can also be written as follows: [ 7.29 ] It is noted that e
gelijk is aan | is equal to | equation 7.25 for the instantaneous values of the voltage of a balanced system can also be written as follows: [ 7.29 ] It is noted that e -j 2/3 π
e | e | the instantaneous values of the voltage of a balanced system can also be written as follows: [ 7.29 ] It is noted that e -j 2/3 π is equal to
j 4/3 π | j 4/3 π | instantaneous values of the voltage of a balanced system can also be written as follows: [ 7.29 ] It is noted that e -j 2/3 π is equal to e
. Uit vergelijking 7.29 kan geconcludeerd worden dat een gebalanceerd stelsel spanningsvectoren kan worden beschreven met één linksom roterende vector, vermenigvuldigd met drie vectoren die elk 120 graden ten opzichte van elkaar zijn verschoven. | From equation 7.29, it can be concluded that a balanced system of voltage vectors can be described with one counterclockwise rotating vector, multiplied by three vectors that are each shifted by 120 degrees relative to each other. | the voltage of a balanced system can also be written as follows: [ 7.29 ] It is noted that e -j 2/3 π is equal to e j 4/3 π
In de complexe fasor-notatie gaat het stelsel vergelijkingen van 7.29 voor een driefasensymmetrisch spanningsstelsel op dezelfde manier als vergelijking 7.16, door te delen door | In the complex phasor notation, the system of equations from 7.29 for a three-phase symmetrical voltage system proceeds in the same way as equation 7.16, by dividing by | that a balanced system of voltage vectors can be described with one counterclockwise rotating vector, multiplied by three vectors that are each shifted by 120 degrees relative to each other.
√2 | √2 | each other. In the complex phasor notation, the system of equations from 7.29 for a three-phase symmetrical voltage system proceeds in the same way as equation 7.16, by dividing by
en door | and by | other. In the complex phasor notation, the system of equations from 7.29 for a three-phase symmetrical voltage system proceeds in the same way as equation 7.16, by dividing by √2
e | e | the complex phasor notation, the system of equations from 7.29 for a three-phase symmetrical voltage system proceeds in the same way as equation 7.16, by dividing by √2 and by
jωt | jωt | complex phasor notation, the system of equations from 7.29 for a three-phase symmetrical voltage system proceeds in the same way as equation 7.16, by dividing by √2 and by e
, over in: | , resulting in: | phasor notation, the system of equations from 7.29 for a three-phase symmetrical voltage system proceeds in the same way as equation 7.16, by dividing by √2 and by e jωt
[ | [ | system of equations from 7.29 for a three-phase symmetrical voltage system proceeds in the same way as equation 7.16, by dividing by √2 and by e jωt , resulting in:
7.30 | 7.30 | of equations from 7.29 for a three-phase symmetrical voltage system proceeds in the same way as equation 7.16, by dividing by √2 and by e jωt , resulting in: [
] | ] | equations from 7.29 for a three-phase symmetrical voltage system proceeds in the same way as equation 7.16, by dividing by √2 and by e jωt , resulting in: [ 7.30
7.5.2 Splitsing in drie spanningsstelsels | 7.5.2 Splitting into Three Voltage Systems | from 7.29 for a three-phase symmetrical voltage system proceeds in the same way as equation 7.16, by dividing by √2 and by e jωt , resulting in: [ 7.30 ]
Het idee van Fortescue was om ieder willekeurig ongebalanceerd stelsel van vectoren te beschrijven met behulp van drie onafhankelijke gebalanceerde linksom draaiende stelsels van vectoren, genaamd het normale, inverse en homopolaire stelsel. In het homopolaire stelsel zijn de drie vectoren gelijk aan elkaar en gelijk gericht. In het normale stelsel zijn de drie vectoren gelijk aan elkaar en maken zij een hoek van 120 graden ten opzichte van elkaar. In het normale stelsel is de vectorvolgorde a-b-c. | Fortescue's idea was to describe any arbitrary unbalanced system of vectors using three independent balanced counterclockwise rotating systems of vectors, called the normal, inverse, and homopolar systems. In the homopolar system, the three vectors are equal to each other and are aligned in the same direction. In the normal system, the three vectors are equal to each other and form an angle of 120 degrees relative to each other. In the normal system, the vector sequence is a-b-c. | voltage system proceeds in the same way as equation 7.16, by dividing by √2 and by e jωt , resulting in: [ 7.30 ] 7.5.2 Splitting into Three Voltage Systems
Figuur 7.13 Spanningen in het homopolaire, normale en inverse stelsel | Figure 7.13 Voltages in the homopolar, normal, and inverse systems | normal system, the three vectors are equal to each other and form an angle of 120 degrees relative to each other. In the normal system, the vector sequence is a-b-c.
Ook in het inverse stelsel zijn de drie vectoren gelijk aan elkaar en maken zij een hoek van 120 graden ten opzichte van elkaar, maar is de vectorvolgorde a-c-b. Elk componentstelsel heeft een eigen specifieke hoekverdraaiing ten opzichte van de reële as. Deze drie componentstelsels zijn hierboven afgebeeld. Met de drie vectorstelsels van figuur 7.13 kunnen alle (asymmetrische) driefasenstelsels worden samengesteld. Dit wordt geïllustreerd aan de hand van een voorbeeld. Onderstaand voorbeeld geeft de constructie weer van een willekeurig asymmetrisch spanningsstelsel. | In the inverse system, the three vectors are also equal to each other and form an angle of 120 degrees relative to each other, but the vector sequence is a-c-b. Each component system has its own specific angular displacement relative to the real axis. These three component systems are depicted above. With the three vector systems from Figure 7.13, all (asymmetrical) three-phase systems can be constructed. This is illustrated with an example. The following example shows the construction of an arbitrary asymmetrical voltage system. | and form an angle of 120 degrees relative to each other. In the normal system, the vector sequence is a-b-c. Figure 7.13 Voltages in the homopolar, normal, and inverse systems
Figuur 7.14 Voorbeeld van een asymmetrisch spanningsstelsel | Figure 7.14 Example of an asymmetrical voltage system | vector systems from Figure 7.13, all (asymmetrical) three-phase systems can be constructed. This is illustrated with an example. The following example shows the construction of an arbitrary asymmetrical voltage system.
Hieronder zal met behulp van een grafische decompositie worden aangetoond dat dit stelsel kan worden samengesteld met behulp van: | Below, it will be demonstrated using a graphical decomposition that this system can be constructed using: | systems can be constructed. This is illustrated with an example. The following example shows the construction of an arbitrary asymmetrical voltage system. Figure 7.14 Example of an asymmetrical voltage system
homopolaire component: 20% en hoek 10° | homopolar component: 20% at an angle of 10° | of an arbitrary asymmetrical voltage system. Figure 7.14 Example of an asymmetrical voltage system Below, it will be demonstrated using a graphical decomposition that this system can be constructed using:
normale component: 100% en hoek 0° | normal component: 100% and angle 0° | Example of an asymmetrical voltage system Below, it will be demonstrated using a graphical decomposition that this system can be constructed using: homopolar component: 20% at an angle of 10°
inverse component: 30% en hoek –20° | inverse component: 30% and angle –20° | Below, it will be demonstrated using a graphical decomposition that this system can be constructed using: homopolar component: 20% at an angle of 10° normal component: 100% and angle 0°
Figuur 7.15 Spanningen in het homopolaire, normale en inverse stelsel | Figure 7.15 Voltages in the homopolar, normal, and inverse systems | a graphical decomposition that this system can be constructed using: homopolar component: 20% at an angle of 10° normal component: 100% and angle 0° inverse component: 30% and angle –20°
Het asymmetrische stelsel wordt geconstrueerd door voor elke fase de vectoren op te tellen. Zo geldt voor de drie fasen: | The asymmetrical system is constructed by adding the vectors for each phase. Thus, for the three phases, the following applies: | homopolar component: 20% at an angle of 10° normal component: 100% and angle 0° inverse component: 30% and angle –20° Figure 7.15 Voltages in the homopolar, normal, and inverse systems
[ | [ | Figure 7.15 Voltages in the homopolar, normal, and inverse systems The asymmetrical system is constructed by adding the vectors for each phase. Thus, for the three phases, the following applies:
7.31 | 7.31 | 7.15 Voltages in the homopolar, normal, and inverse systems The asymmetrical system is constructed by adding the vectors for each phase. Thus, for the three phases, the following applies: [
] | ] | Voltages in the homopolar, normal, and inverse systems The asymmetrical system is constructed by adding the vectors for each phase. Thus, for the three phases, the following applies: [ 7.31
Figuur 7.16 Constructie van een asymmetrisch stelsel uit het homopolaire, normale en inverse stelsel | Figure 7.16 Construction of an asymmetrical system from the homopolar, normal, and inverse systems | in the homopolar, normal, and inverse systems The asymmetrical system is constructed by adding the vectors for each phase. Thus, for the three phases, the following applies: [ 7.31 ]
7.5.3 Wiskundige decompositie | 7.5.3 Mathematical Decomposition | the vectors for each phase. Thus, for the three phases, the following applies: [ 7.31 ] Figure 7.16 Construction of an asymmetrical system from the homopolar, normal, and inverse systems
De componentspanningen van figuur 7.15 kunnen worden ontbonden in drie genormeerde componentstelsels, die zijn opgebouwd met de vectoren | The component voltages of figure 7.15 can be decomposed into three normalized component systems, which are constructed with the vectors | each phase. Thus, for the three phases, the following applies: [ 7.31 ] Figure 7.16 Construction of an asymmetrical system from the homopolar, normal, and inverse systems 7.5.3 Mathematical Decomposition
1 | 1 | from the homopolar, normal, and inverse systems 7.5.3 Mathematical Decomposition The component voltages of figure 7.15 can be decomposed into three normalized component systems, which are constructed with the vectors
, | , | the homopolar, normal, and inverse systems 7.5.3 Mathematical Decomposition The component voltages of figure 7.15 can be decomposed into three normalized component systems, which are constructed with the vectors 1
a | a | homopolar, normal, and inverse systems 7.5.3 Mathematical Decomposition The component voltages of figure 7.15 can be decomposed into three normalized component systems, which are constructed with the vectors 1 ,
en | en | normal, and inverse systems 7.5.3 Mathematical Decomposition The component voltages of figure 7.15 can be decomposed into three normalized component systems, which are constructed with the vectors 1 , a
a | a | and inverse systems 7.5.3 Mathematical Decomposition The component voltages of figure 7.15 can be decomposed into three normalized component systems, which are constructed with the vectors 1 , a en
2 | 2 | inverse systems 7.5.3 Mathematical Decomposition The component voltages of figure 7.15 can be decomposed into three normalized component systems, which are constructed with the vectors 1 , a en a
, en drie bijbehorende complexe vectoren. Figuur 7.17 geeft de ontbinding van de drie componentstelsels van figuur 7.15 weer. | , and three corresponding complex vectors. Figure 7.17 shows the decomposition of the three component systems from figure 7.15. | systems 7.5.3 Mathematical Decomposition The component voltages of figure 7.15 can be decomposed into three normalized component systems, which are constructed with the vectors 1 , a en a 2
Figuur 7.17 Genormeerde homopolaire, normale en inverse stelsels met vermenigvuldigingsfactoren | Figure 7.17 Normalized homopolar, normal, and inverse systems with multiplication factors | are constructed with the vectors 1 , a en a 2 , and three corresponding complex vectors. Figure 7.17 shows the decomposition of the three component systems from figure 7.15.
Voor het stelsel van figuur 7.15 kunnen alle vectoren worden beschreven met behulp van de drie genormeerde componentenstelsels en hun complexe vermenigvuldigingsfactoren. In de vergelijkingen 7.32 zijn de vermenigvuldigingsfactoren | For the system in figure 7.15, all vectors can be described using the three normalized component systems and their complex multiplication factors. In equations 7.32, the multiplication factors are | , and three corresponding complex vectors. Figure 7.17 shows the decomposition of the three component systems from figure 7.15. Figure 7.17 Normalized homopolar, normal, and inverse systems with multiplication factors
U | U | factors For the system in figure 7.15, all vectors can be described using the three normalized component systems and their complex multiplication factors. In equations 7.32, the multiplication factors are
0 | 0 | For the system in figure 7.15, all vectors can be described using the three normalized component systems and their complex multiplication factors. In equations 7.32, the multiplication factors are U
, | , | the system in figure 7.15, all vectors can be described using the three normalized component systems and their complex multiplication factors. In equations 7.32, the multiplication factors are U 0
U | U | system in figure 7.15, all vectors can be described using the three normalized component systems and their complex multiplication factors. In equations 7.32, the multiplication factors are U 0 ,
1 | 1 | in figure 7.15, all vectors can be described using the three normalized component systems and their complex multiplication factors. In equations 7.32, the multiplication factors are U 0 , U
en | en | figure 7.15, all vectors can be described using the three normalized component systems and their complex multiplication factors. In equations 7.32, the multiplication factors are U 0 , U 1
U | U | 7.15, all vectors can be described using the three normalized component systems and their complex multiplication factors. In equations 7.32, the multiplication factors are U 0 , U 1 en
2 | 2 | all vectors can be described using the three normalized component systems and their complex multiplication factors. In equations 7.32, the multiplication factors are U 0 , U 1 en U
de complexe spanningsvectoren die voor ieder componentstelsel de effectieve waarde en de fasehoek vastleggen. Bijvoorbeeld voor fase b geldt: | the complex voltage vectors that determine the effective value and phase angle for each component system. For example, for phase b: | vectors can be described using the three normalized component systems and their complex multiplication factors. In equations 7.32, the multiplication factors are U 0 , U 1 en U 2
[ | [ | are U 0 , U 1 en U 2 the complex voltage vectors that determine the effective value and phase angle for each component system. For example, for phase b:
7.32 | 7.32 | U 0 , U 1 en U 2 the complex voltage vectors that determine the effective value and phase angle for each component system. For example, for phase b: [
] | ] | 0 , U 1 en U 2 the complex voltage vectors that determine the effective value and phase angle for each component system. For example, for phase b: [ 7.32
Analoog aan vergelijking 7.31 kan de constructie van elk driefasensystelsel vanuit de genormeerde symmetrische componenten worden beschreven als de som van de drie componentspanningen: | Analogous to equation 7.31, the construction of any three-phase system from the normalized symmetrical components can be described as the sum of the three component voltages: | , U 1 en U 2 the complex voltage vectors that determine the effective value and phase angle for each component system. For example, for phase b: [ 7.32 ]
[ | [ | b: [ 7.32 ] Analogous to equation 7.31, the construction of any three-phase system from the normalized symmetrical components can be described as the sum of the three component voltages:
7.33 | 7.33 | [ 7.32 ] Analogous to equation 7.31, the construction of any three-phase system from the normalized symmetrical components can be described as the sum of the three component voltages: [
] | ] | 7.32 ] Analogous to equation 7.31, the construction of any three-phase system from the normalized symmetrical components can be described as the sum of the three component voltages: [ 7.33
Dit kan worden omgezet in een matrixvergelijking. Het stelsel van vergelijking 7.33 gaat dan over in vergelijking 7.34, waarbij de matrix A de transformatiematrix wordt genoemd. | This can be converted into a matrix equation. The system of equation 7.33 then transforms into equation 7.34, where matrix A is called the transformation matrix. | ] Analogous to equation 7.31, the construction of any three-phase system from the normalized symmetrical components can be described as the sum of the three component voltages: [ 7.33 ]
[ | [ | voltages: [ 7.33 ] This can be converted into a matrix equation. The system of equation 7.33 then transforms into equation 7.34, where matrix A is called the transformation matrix.
7.34 | 7.34 | [ 7.33 ] This can be converted into a matrix equation. The system of equation 7.33 then transforms into equation 7.34, where matrix A is called the transformation matrix. [
] | ] | 7.33 ] This can be converted into a matrix equation. The system of equation 7.33 then transforms into equation 7.34, where matrix A is called the transformation matrix. [ 7.34
Van het voorbeeld van figuur 7.14 zijn de complexe waarden van de drie componenten: | From the example in figure 7.14, the complex values of the three components are: | ] This can be converted into a matrix equation. The system of equation 7.33 then transforms into equation 7.34, where matrix A is called the transformation matrix. [ 7.34 ]
[ | [ | then transforms into equation 7.34, where matrix A is called the transformation matrix. [ 7.34 ] From the example in figure 7.14, the complex values of the three components are:
7.35 | 7.35 | transforms into equation 7.34, where matrix A is called the transformation matrix. [ 7.34 ] From the example in figure 7.14, the complex values of the three components are: [
] | ] | into equation 7.34, where matrix A is called the transformation matrix. [ 7.34 ] From the example in figure 7.14, the complex values of the three components are: [ 7.35
Door deze waarden in te vullen in de vergelijkingen 7.33, worden de waarden van de fasen van het asymmetrische spanningsstelsel berekend: | By substituting these values into equations 7.33, the phase values of the asymmetrical voltage system are calculated: | equation 7.34, where matrix A is called the transformation matrix. [ 7.34 ] From the example in figure 7.14, the complex values of the three components are: [ 7.35 ]
[ | [ | figure 7.14, the complex values of the three components are: [ 7.35 ] By substituting these values into equations 7.33, the phase values of the asymmetrical voltage system are calculated:
7.36 | 7.36 | 7.14, the complex values of the three components are: [ 7.35 ] By substituting these values into equations 7.33, the phase values of the asymmetrical voltage system are calculated: [
] | ] | the complex values of the three components are: [ 7.35 ] By substituting these values into equations 7.33, the phase values of the asymmetrical voltage system are calculated: [ 7.36
De fysische analogie kan het best worden aangetoond met figuur 7.18, waar een asymmetrische spanningsbron wordt beschreven met een serieschakeling van de drie componentspanningsbronnen. Het is echter een fictieve ontbinding, aangezien de homopolaire, inverse en normale spanningsbronnen in werkelijkheid niet bestaan. | The physical analogy can best be demonstrated with figure 7.18, where an asymmetrical voltage source is described with a series connection of the three component voltage sources. However, it is a fictitious decomposition, as the homopolar, inverse, and normal voltage sources do not actually exist. | complex values of the three components are: [ 7.35 ] By substituting these values into equations 7.33, the phase values of the asymmetrical voltage system are calculated: [ 7.36 ]
Figuur 7.18 Fysische interpretatie van het samenstellen met componentensystemen | Figure 7.18 Physical interpretation of the assembly with component systems | is described with a series connection of the three component voltage sources. However, it is a fictitious decomposition, as the homopolar, inverse, and normal voltage sources do not actually exist.
In het ideale gebalanceerde geval is | In the ideally balanced case, | voltage sources. However, it is a fictitious decomposition, as the homopolar, inverse, and normal voltage sources do not actually exist. Figure 7.18 Physical interpretation of the assembly with component systems
U | U | a fictitious decomposition, as the homopolar, inverse, and normal voltage sources do not actually exist. Figure 7.18 Physical interpretation of the assembly with component systems In the ideally balanced case,
0 | 0 | fictitious decomposition, as the homopolar, inverse, and normal voltage sources do not actually exist. Figure 7.18 Physical interpretation of the assembly with component systems In the ideally balanced case, U
decomposition, as the homopolar, inverse, and normal voltage sources do not actually exist. Figure 7.18 Physical interpretation of the assembly with component systems In the ideally balanced case, U 0
en | en | the homopolar, inverse, and normal voltage sources do not actually exist. Figure 7.18 Physical interpretation of the assembly with component systems In the ideally balanced case, U 0 = 0
U | U | homopolar, inverse, and normal voltage sources do not actually exist. Figure 7.18 Physical interpretation of the assembly with component systems In the ideally balanced case, U 0 = 0 en
2 | 2 | inverse, and normal voltage sources do not actually exist. Figure 7.18 Physical interpretation of the assembly with component systems In the ideally balanced case, U 0 = 0 en U
and normal voltage sources do not actually exist. Figure 7.18 Physical interpretation of the assembly with component systems In the ideally balanced case, U 0 = 0 en U 2
zodat we alleen te maken hebben met | so that we only have to deal with | voltage sources do not actually exist. Figure 7.18 Physical interpretation of the assembly with component systems In the ideally balanced case, U 0 = 0 en U 2 = 0
U | U | Physical interpretation of the assembly with component systems In the ideally balanced case, U 0 = 0 en U 2 = 0 so that we only have to deal with
1 | 1 | interpretation of the assembly with component systems In the ideally balanced case, U 0 = 0 en U 2 = 0 so that we only have to deal with U
. In praktijk is echter | . In practice, however | of the assembly with component systems In the ideally balanced case, U 0 = 0 en U 2 = 0 so that we only have to deal with U 1
U | U | component systems In the ideally balanced case, U 0 = 0 en U 2 = 0 so that we only have to deal with U 1 . In practice, however
0 | 0 | systems In the ideally balanced case, U 0 = 0 en U 2 = 0 so that we only have to deal with U 1 . In practice, however U
≠ 0 | ≠ 0 | In the ideally balanced case, U 0 = 0 en U 2 = 0 so that we only have to deal with U 1 . In practice, however U 0
en | en | ideally balanced case, U 0 = 0 en U 2 = 0 so that we only have to deal with U 1 . In practice, however U 0 ≠ 0
U | U | balanced case, U 0 = 0 en U 2 = 0 so that we only have to deal with U 1 . In practice, however U 0 ≠ 0 en
2 | 2 | case, U 0 = 0 en U 2 = 0 so that we only have to deal with U 1 . In practice, however U 0 ≠ 0 en U
≠ 0 | ≠ 0 | U 0 = 0 en U 2 = 0 so that we only have to deal with U 1 . In practice, however U 0 ≠ 0 en U 2
. Dit wordt veroorzaakt door de onbalans in het driefasensysteem. | . This is caused by the imbalance in the three-phase system.
Het is dus mogelijk om de fysieke spanningen | It is therefore possible to measure the physical voltages | have to deal with U 1 . In practice, however U 0 ≠ 0 en U 2 ≠ 0 . This is caused by the imbalance in the three-phase system.
U | U | however U 0 ≠ 0 en U 2 ≠ 0 . This is caused by the imbalance in the three-phase system. It is therefore possible to measure the physical voltages
a | a | U 0 ≠ 0 en U 2 ≠ 0 . This is caused by the imbalance in the three-phase system. It is therefore possible to measure the physical voltages U
, | , | 0 ≠ 0 en U 2 ≠ 0 . This is caused by the imbalance in the three-phase system. It is therefore possible to measure the physical voltages U a
U | U | ≠ 0 en U 2 ≠ 0 . This is caused by the imbalance in the three-phase system. It is therefore possible to measure the physical voltages U a ,
b | b | 0 en U 2 ≠ 0 . This is caused by the imbalance in the three-phase system. It is therefore possible to measure the physical voltages U a , U
en | en | en U 2 ≠ 0 . This is caused by the imbalance in the three-phase system. It is therefore possible to measure the physical voltages U a , U b
U | U | U 2 ≠ 0 . This is caused by the imbalance in the three-phase system. It is therefore possible to measure the physical voltages U a , U b en
c | c | 2 ≠ 0 . This is caused by the imbalance in the three-phase system. It is therefore possible to measure the physical voltages U a , U b en U
in een driefasenstelsel te beschrijven met behulp van de componentspanningen | in a three-phase system using the component voltages | ≠ 0 . This is caused by the imbalance in the three-phase system. It is therefore possible to measure the physical voltages U a , U b en U c
U | U | imbalance in the three-phase system. It is therefore possible to measure the physical voltages U a , U b en U c in a three-phase system using the component voltages
0 | 0 | in the three-phase system. It is therefore possible to measure the physical voltages U a , U b en U c in a three-phase system using the component voltages U
, | , | the three-phase system. It is therefore possible to measure the physical voltages U a , U b en U c in a three-phase system using the component voltages U 0
U | U | three-phase system. It is therefore possible to measure the physical voltages U a , U b en U c in a three-phase system using the component voltages U 0 ,
1 | 1 | system. It is therefore possible to measure the physical voltages U a , U b en U c in a three-phase system using the component voltages U 0 , U
en | en | It is therefore possible to measure the physical voltages U a , U b en U c in a three-phase system using the component voltages U 0 , U 1
U | U | is therefore possible to measure the physical voltages U a , U b en U c in a three-phase system using the component voltages U 0 , U 1 en
2 | 2 | therefore possible to measure the physical voltages U a , U b en U c in a three-phase system using the component voltages U 0 , U 1 en U
. Omgekeerd is het ook mogelijk om de componentspanningen te berekenen uit de fysieke spanningen. Door het stelsel vergelijkingen van 7.33 te inverteren, worden de navolgende vergelijkingen voor de decompositie uit de fysieke grootheden verkregen. | Conversely, it is also possible to calculate the component voltages from the physical voltages. By inverting the system of equations from 7.33, the following equations for the decomposition from the physical quantities are obtained. | possible to measure the physical voltages U a , U b en U c in a three-phase system using the component voltages U 0 , U 1 en U 2
[ | [ | possible to calculate the component voltages from the physical voltages. By inverting the system of equations from 7.33, the following equations for the decomposition from the physical quantities are obtained.
7.37 | 7.37 | to calculate the component voltages from the physical voltages. By inverting the system of equations from 7.33, the following equations for the decomposition from the physical quantities are obtained. [
] | ] | calculate the component voltages from the physical voltages. By inverting the system of equations from 7.33, the following equations for the decomposition from the physical quantities are obtained. [ 7.37
Ook dit kan worden opgeschreven als een matrixvergelijking. Hierbij is de matrix | This can also be written as a matrix equation. Here, the matrix is | the component voltages from the physical voltages. By inverting the system of equations from 7.33, the following equations for the decomposition from the physical quantities are obtained. [ 7.37 ]
A | A | from 7.33, the following equations for the decomposition from the physical quantities are obtained. [ 7.37 ] This can also be written as a matrix equation. Here, the matrix is
-1 | -1 | 7.33, the following equations for the decomposition from the physical quantities are obtained. [ 7.37 ] This can also be written as a matrix equation. Here, the matrix is A
de inverse transformatiematrix. Hiermee worden de grootheden van het componentensysteem afgeleid uit de grootheden van het fysieke systeem, zodat de componentspanningen in matrixnotatie als volgt worden berekend: | the inverse transformation matrix. This allows the quantities of the component system to be derived from the quantities of the physical system, so that the component stresses are calculated in matrix notation as follows: | the following equations for the decomposition from the physical quantities are obtained. [ 7.37 ] This can also be written as a matrix equation. Here, the matrix is A -1
[ | [ | This allows the quantities of the component system to be derived from the quantities of the physical system, so that the component stresses are calculated in matrix notation as follows:
7.38 | 7.38 | allows the quantities of the component system to be derived from the quantities of the physical system, so that the component stresses are calculated in matrix notation as follows: [
] | ] | the quantities of the component system to be derived from the quantities of the physical system, so that the component stresses are calculated in matrix notation as follows: [ 7.38
Samengevat geldt voor de transformatiematrix en de inverse transformatiematrix: | In summary, the following applies to the transformation matrix and the inverse transformation matrix: | quantities of the component system to be derived from the quantities of the physical system, so that the component stresses are calculated in matrix notation as follows: [ 7.38 ]
[ | [ | system, so that the component stresses are calculated in matrix notation as follows: [ 7.38 ] In summary, the following applies to the transformation matrix and the inverse transformation matrix:
7.39 | 7.39 | so that the component stresses are calculated in matrix notation as follows: [ 7.38 ] In summary, the following applies to the transformation matrix and the inverse transformation matrix: [
] | ] | that the component stresses are calculated in matrix notation as follows: [ 7.38 ] In summary, the following applies to the transformation matrix and the inverse transformation matrix: [ 7.39
De toestand in het net wordt niet alleen met spanningen beschreven maar ook met stromen. Voor de stroomvectoren | The state in the network is described not only by voltages but also by currents. For the current vectors | the component stresses are calculated in matrix notation as follows: [ 7.38 ] In summary, the following applies to the transformation matrix and the inverse transformation matrix: [ 7.39 ]
I | I | the transformation matrix and the inverse transformation matrix: [ 7.39 ] The state in the network is described not only by voltages but also by currents. For the current vectors
abc | abc | transformation matrix and the inverse transformation matrix: [ 7.39 ] The state in the network is described not only by voltages but also by currents. For the current vectors I
en | en | matrix and the inverse transformation matrix: [ 7.39 ] The state in the network is described not only by voltages but also by currents. For the current vectors I abc
I | I | and the inverse transformation matrix: [ 7.39 ] The state in the network is described not only by voltages but also by currents. For the current vectors I abc en
012 | 012 | the inverse transformation matrix: [ 7.39 ] The state in the network is described not only by voltages but also by currents. For the current vectors I abc en I
kunnen de hierboven beschreven transformaties op dezelfde manier worden uitgevoerd. In matrixnotatie ziet dat er als volgt uit: | the transformations described above can be performed in the same way. In matrix notation, it looks like this: | inverse transformation matrix: [ 7.39 ] The state in the network is described not only by voltages but also by currents. For the current vectors I abc en I 012
[ | [ | also by currents. For the current vectors I abc en I 012 the transformations described above can be performed in the same way. In matrix notation, it looks like this:
7.40 | 7.40 | by currents. For the current vectors I abc en I 012 the transformations described above can be performed in the same way. In matrix notation, it looks like this: [
] | ] | currents. For the current vectors I abc en I 012 the transformations described above can be performed in the same way. In matrix notation, it looks like this: [ 7.40
Het kan worden aangetoond dat ook impedanties van driefasensystemen beschreven kunnen worden met behulp van de symmetrische componentenmethode. Met de wet van Ohm en het gebruiken van de transformatie voor de stroom- en spanningsvectoren volgt namelijk: | It can be demonstrated that impedances of three-phase systems can also be described using the symmetrical components method. By applying Ohm's law and using the transformation for the current and voltage vectors, the following results: | For the current vectors I abc en I 012 the transformations described above can be performed in the same way. In matrix notation, it looks like this: [ 7.40 ]
[ | [ | impedances of three-phase systems can also be described using the symmetrical components method. By applying Ohm's law and using the transformation for the current and voltage vectors, the following results:
7.41 | 7.41 | of three-phase systems can also be described using the symmetrical components method. By applying Ohm's law and using the transformation for the current and voltage vectors, the following results: [
] | ] | three-phase systems can also be described using the symmetrical components method. By applying Ohm's law and using the transformation for the current and voltage vectors, the following results: [ 7.41
Hierin zijn | Herein are | systems can also be described using the symmetrical components method. By applying Ohm's law and using the transformation for the current and voltage vectors, the following results: [ 7.41 ]
U | U | also be described using the symmetrical components method. By applying Ohm's law and using the transformation for the current and voltage vectors, the following results: [ 7.41 ] Herein are
abc | abc | be described using the symmetrical components method. By applying Ohm's law and using the transformation for the current and voltage vectors, the following results: [ 7.41 ] Herein are U
, | , | described using the symmetrical components method. By applying Ohm's law and using the transformation for the current and voltage vectors, the following results: [ 7.41 ] Herein are U abc
I | I | using the symmetrical components method. By applying Ohm's law and using the transformation for the current and voltage vectors, the following results: [ 7.41 ] Herein are U abc ,
abc | abc | the symmetrical components method. By applying Ohm's law and using the transformation for the current and voltage vectors, the following results: [ 7.41 ] Herein are U abc , I
en | en | symmetrical components method. By applying Ohm's law and using the transformation for the current and voltage vectors, the following results: [ 7.41 ] Herein are U abc , I abc
Z | Z | components method. By applying Ohm's law and using the transformation for the current and voltage vectors, the following results: [ 7.41 ] Herein are U abc , I abc en
abc | abc | method. By applying Ohm's law and using the transformation for the current and voltage vectors, the following results: [ 7.41 ] Herein are U abc , I abc en Z
respectievelijk de spanningsmatrix, de stroommatrix en de impedantiematrix in het abc-stelsel en zijn | respectively the voltage matrix, the current matrix, and the impedance matrix in the abc system and are | By applying Ohm's law and using the transformation for the current and voltage vectors, the following results: [ 7.41 ] Herein are U abc , I abc en Z abc
U | U | [ 7.41 ] Herein are U abc , I abc en Z abc respectively the voltage matrix, the current matrix, and the impedance matrix in the abc system and are
012 | 012 | 7.41 ] Herein are U abc , I abc en Z abc respectively the voltage matrix, the current matrix, and the impedance matrix in the abc system and are U
, | , | ] Herein are U abc , I abc en Z abc respectively the voltage matrix, the current matrix, and the impedance matrix in the abc system and are U 012
I | I | Herein are U abc , I abc en Z abc respectively the voltage matrix, the current matrix, and the impedance matrix in the abc system and are U 012 ,
012 | 012 | are U abc , I abc en Z abc respectively the voltage matrix, the current matrix, and the impedance matrix in the abc system and are U 012 , I
en | en | U abc , I abc en Z abc respectively the voltage matrix, the current matrix, and the impedance matrix in the abc system and are U 012 , I 012
Z | Z | abc , I abc en Z abc respectively the voltage matrix, the current matrix, and the impedance matrix in the abc system and are U 012 , I 012 en
012 | 012 | , I abc en Z abc respectively the voltage matrix, the current matrix, and the impedance matrix in the abc system and are U 012 , I 012 en Z
respectievelijk de spanningsmatrix, de stroommatrix en de impedantiematrix in het componentenstelsel. Voor de relatie tussen de impedantiematrix in het abc- en componentenstelsel geldt: | respectively the voltage matrix, the current matrix, and the impedance matrix in the component system. For the relationship between the impedance matrix in the abc system and the component system, the following applies: | I abc en Z abc respectively the voltage matrix, the current matrix, and the impedance matrix in the abc system and are U 012 , I 012 en Z 012
[ | [ | matrix, the current matrix, and the impedance matrix in the component system. For the relationship between the impedance matrix in the abc system and the component system, the following applies:
7.42 | 7.42 | the current matrix, and the impedance matrix in the component system. For the relationship between the impedance matrix in the abc system and the component system, the following applies: [
] | ] | current matrix, and the impedance matrix in the component system. For the relationship between the impedance matrix in the abc system and the component system, the following applies: [ 7.42
Ook elke kabelverbinding, transformator, belasting en opwekker kan worden gemodelleerd met normale, inverse en homopolaire impedanties. Voor de meeste berekeningen is het voldoende als wordt aangenomen dat de systemen driefasensymmetrisch zijn. In dat geval vereenvoudigt het systeem zodanig dat alleen rekening hoeft worden gehouden met de normale impedantie | Each cable connection, transformer, load, and generator can also be modeled with normal, inverse, and homopolar impedances. For most calculations, it is sufficient to assume that the systems are three-phase symmetric. In that case, the system simplifies such that only the normal impedance needs to be considered. | matrix, and the impedance matrix in the component system. For the relationship between the impedance matrix in the abc system and the component system, the following applies: [ 7.42 ]
Z | Z | For most calculations, it is sufficient to assume that the systems are three-phase symmetric. In that case, the system simplifies such that only the normal impedance needs to be considered.
1 | 1 | most calculations, it is sufficient to assume that the systems are three-phase symmetric. In that case, the system simplifies such that only the normal impedance needs to be considered. Z
en de homopolaire impedantie | and the homopolar impedance | calculations, it is sufficient to assume that the systems are three-phase symmetric. In that case, the system simplifies such that only the normal impedance needs to be considered. Z 1
Z | Z | to assume that the systems are three-phase symmetric. In that case, the system simplifies such that only the normal impedance needs to be considered. Z 1 and the homopolar impedance
0 | 0 | assume that the systems are three-phase symmetric. In that case, the system simplifies such that only the normal impedance needs to be considered. Z 1 and the homopolar impedance Z
. De normale impedantie is gelijk aan de fase-impedantie. De inverse impedantie hoeft niet apart te worden bepaald, want deze is in dit geval gelijk aan de normale impedantie. De homopolaire impedantie wijkt af van de normale impedantie en moet wel apart vastgesteld worden. De volgende paragraaf beschrijft een asymmetrisch stroomstelsel en de homopolaire impedantie. | The normal impedance is equal to the phase impedance. The inverse impedance does not need to be determined separately, as it is equal to the normal impedance in this case. The homopolar impedance differs from the normal impedance and must be determined separately. The next paragraph describes an asymmetric power system and the homopolar impedance. | that the systems are three-phase symmetric. In that case, the system simplifies such that only the normal impedance needs to be considered. Z 1 and the homopolar impedance Z 0
7.6 Asymmetrisch stroomstelsel en homopolaire impedantie | 7.6 Asymmetric power system and homopolar impedance | normal impedance in this case. The homopolar impedance differs from the normal impedance and must be determined separately. The next paragraph describes an asymmetric power system and the homopolar impedance.
Figuur 7.19 is een uitbreiding op figuur 7.18, waarin een spanningsbron met homopolaire, normale en inverse componenten | Figure 7.19 is an extension of Figure 7.18, which includes a voltage source with homopolar, normal, and inverse components. | impedance differs from the normal impedance and must be determined separately. The next paragraph describes an asymmetric power system and the homopolar impedance. 7.6 Asymmetric power system and homopolar impedance
(U | (U | and the homopolar impedance. 7.6 Asymmetric power system and homopolar impedance Figure 7.19 is an extension of Figure 7.18, which includes a voltage source with homopolar, normal, and inverse components.
0 | 0 | the homopolar impedance. 7.6 Asymmetric power system and homopolar impedance Figure 7.19 is an extension of Figure 7.18, which includes a voltage source with homopolar, normal, and inverse components. (U
, U | , U | homopolar impedance. 7.6 Asymmetric power system and homopolar impedance Figure 7.19 is an extension of Figure 7.18, which includes a voltage source with homopolar, normal, and inverse components. (U 0
1 | 1 | 7.6 Asymmetric power system and homopolar impedance Figure 7.19 is an extension of Figure 7.18, which includes a voltage source with homopolar, normal, and inverse components. (U 0 , U
en | en | Asymmetric power system and homopolar impedance Figure 7.19 is an extension of Figure 7.18, which includes a voltage source with homopolar, normal, and inverse components. (U 0 , U 1
U | U | power system and homopolar impedance Figure 7.19 is an extension of Figure 7.18, which includes a voltage source with homopolar, normal, and inverse components. (U 0 , U 1 en
2 | 2 | system and homopolar impedance Figure 7.19 is an extension of Figure 7.18, which includes a voltage source with homopolar, normal, and inverse components. (U 0 , U 1 en U
) zijn opgenomen. Achter de samengestelde spanningsbron is een willekeurig driefasencircuit met een retourpad opgenomen. Het driefasencircuit bestaat uit de impedanties | ) are included. Behind the composite voltage source, an arbitrary three-phase circuit with a return path is included. The three-phase circuit consists of the impedances | and homopolar impedance Figure 7.19 is an extension of Figure 7.18, which includes a voltage source with homopolar, normal, and inverse components. (U 0 , U 1 en U 2
Z | Z | U 1 en U 2 ) are included. Behind the composite voltage source, an arbitrary three-phase circuit with a return path is included. The three-phase circuit consists of the impedances
a | a | 1 en U 2 ) are included. Behind the composite voltage source, an arbitrary three-phase circuit with a return path is included. The three-phase circuit consists of the impedances Z
, Z | , Z | en U 2 ) are included. Behind the composite voltage source, an arbitrary three-phase circuit with a return path is included. The three-phase circuit consists of the impedances Z a
b | b | 2 ) are included. Behind the composite voltage source, an arbitrary three-phase circuit with a return path is included. The three-phase circuit consists of the impedances Z a , Z
en | en | ) are included. Behind the composite voltage source, an arbitrary three-phase circuit with a return path is included. The three-phase circuit consists of the impedances Z a , Z b
Z | Z | are included. Behind the composite voltage source, an arbitrary three-phase circuit with a return path is included. The three-phase circuit consists of the impedances Z a , Z b en
c | c | included. Behind the composite voltage source, an arbitrary three-phase circuit with a return path is included. The three-phase circuit consists of the impedances Z a , Z b en Z
, die niet gelijk aan elkaar hoeven te zijn. In de meeste driefasensystemen zijn deze drie impedanties wel gelijk aan elkaar, waardoor aangenomen mag worden dat de normale impedantie | , which do not need to be equal to each other. In most three-phase systems, these three impedances are equal to each other, allowing the assumption that the normal impedance | Behind the composite voltage source, an arbitrary three-phase circuit with a return path is included. The three-phase circuit consists of the impedances Z a , Z b en Z c
Z | Z | , which do not need to be equal to each other. In most three-phase systems, these three impedances are equal to each other, allowing the assumption that the normal impedance
1 | 1 | which do not need to be equal to each other. In most three-phase systems, these three impedances are equal to each other, allowing the assumption that the normal impedance Z
gelijk is aan de fase-impedantie, bijvoorbeeld | is equal to the phase impedance, for example | do not need to be equal to each other. In most three-phase systems, these three impedances are equal to each other, allowing the assumption that the normal impedance Z 1
Z | Z | other. In most three-phase systems, these three impedances are equal to each other, allowing the assumption that the normal impedance Z 1 is equal to the phase impedance, for example
a | a | In most three-phase systems, these three impedances are equal to each other, allowing the assumption that the normal impedance Z 1 is equal to the phase impedance, for example Z
. De inverse impedantie | . The inverse impedance | most three-phase systems, these three impedances are equal to each other, allowing the assumption that the normal impedance Z 1 is equal to the phase impedance, for example Z a
Z | Z | three impedances are equal to each other, allowing the assumption that the normal impedance Z 1 is equal to the phase impedance, for example Z a . The inverse impedance
2 | 2 | impedances are equal to each other, allowing the assumption that the normal impedance Z 1 is equal to the phase impedance, for example Z a . The inverse impedance Z
is dan gelijk aan de normale impedantie. Er is een retourpad met een retourimpedantie | is then equal to the normal impedance. There is a return path with a return impedance | are equal to each other, allowing the assumption that the normal impedance Z 1 is equal to the phase impedance, for example Z a . The inverse impedance Z 2
Z | Z | to the phase impedance, for example Z a . The inverse impedance Z 2 is then equal to the normal impedance. There is a return path with a return impedance
E | E | the phase impedance, for example Z a . The inverse impedance Z 2 is then equal to the normal impedance. There is a return path with a return impedance Z
. Het retourpad kan een vierde geleider zijn, zoals bij LS-kabels, en het kan door aarde lopen, zoals in MS-netten. | The return path can be a fourth conductor, as in low-voltage cables, and it can run through the ground, as in medium-voltage networks. | phase impedance, for example Z a . The inverse impedance Z 2 is then equal to the normal impedance. There is a return path with a return impedance Z E
Figuur 7.19 Voedingsbron met belasting en retourimpedantie | Figure 7.19 Power source with load and return impedance | path with a return impedance Z E The return path can be a fourth conductor, as in low-voltage cables, and it can run through the ground, as in medium-voltage networks.
De van vergelijkingen 7.40 afgeleide componenttransformatie beschrijft de relatie tussen de stromen in het fictieve componentnetwerk en het fysieke stelsel: | The component transformation derived from equations 7.40 describes the relationship between the currents in the fictitious component network and the physical system: | path can be a fourth conductor, as in low-voltage cables, and it can run through the ground, as in medium-voltage networks. Figure 7.19 Power source with load and return impedance
[ | [ | 7.19 Power source with load and return impedance The component transformation derived from equations 7.40 describes the relationship between the currents in the fictitious component network and the physical system:
7.43 | 7.43 | Power source with load and return impedance The component transformation derived from equations 7.40 describes the relationship between the currents in the fictitious component network and the physical system: [
] | ] | source with load and return impedance The component transformation derived from equations 7.40 describes the relationship between the currents in the fictitious component network and the physical system: [ 7.43
Hieruit blijkt dat de homopolaire stroom gelijk is aan een derde van de som van de drie fasestromen. In geval van een perfect gebalanceerd driefasensysteem, zal de homopolaire stroom nul zijn. In geval van een niet gebalanceerd systeem loopt er een retourstroom en is uit figuur 7.19 af te leiden dat deze gelijk is aan de vectoriële som van de drie fasenstromen en dus gelijk is aan: | From this, it appears that the homopolar current is equal to one-third of the sum of the three phase currents. In the case of a perfectly balanced three-phase system, the homopolar current will be zero. In the case of an unbalanced system, a return current flows, and it can be deduced from figure 7.19 that this is equal to the vector sum of the three phase currents and thus is equal to: | with load and return impedance The component transformation derived from equations 7.40 describes the relationship between the currents in the fictitious component network and the physical system: [ 7.43 ]
I | I | a return current flows, and it can be deduced from figure 7.19 that this is equal to the vector sum of the three phase currents and thus is equal to:
E | E | return current flows, and it can be deduced from figure 7.19 that this is equal to the vector sum of the three phase currents and thus is equal to: I
current flows, and it can be deduced from figure 7.19 that this is equal to the vector sum of the three phase currents and thus is equal to: I E
a | a | and it can be deduced from figure 7.19 that this is equal to the vector sum of the three phase currents and thus is equal to: I E = I
+ I | + I | it can be deduced from figure 7.19 that this is equal to the vector sum of the three phase currents and thus is equal to: I E = I a
b | b | be deduced from figure 7.19 that this is equal to the vector sum of the three phase currents and thus is equal to: I E = I a + I
+ I | + I c | deduced from figure 7.19 that this is equal to the vector sum of the three phase currents and thus is equal to: I E = I a + I b
c | c | 7.19 that this is equal to the vector sum of the three phase currents and thus is equal to: I E = I a + I b + I c
that this is equal to the vector sum of the three phase currents and thus is equal to: I E = I a + I b + I c c
0 | 0 | is equal to the vector sum of the three phase currents and thus is equal to: I E = I a + I b + I c c = 3I
. | . | equal to the vector sum of the three phase currents and thus is equal to: I E = I a + I b + I c c = 3I 0
Hieruit kan een manier worden afgeleid om de homopolaire impedantie te meten. Dit vindt plaats door het aanbrengen van een homopolaire spanning op de drie parallelgeschakelde fasen, zoals aangegeven in figuur 7.20. De amplitudes van de normale en inverse spanningsbronnen | From this, a method can be derived to measure the homopolar impedance. This is done by applying a homopolar voltage to the three parallel-connected phases, as shown in figure 7.20. The amplitudes of the normal and inverse voltage sources | to the vector sum of the three phase currents and thus is equal to: I E = I a + I b + I c c = 3I 0 .
(U | (U<sub>0</sub> | the homopolar impedance. This is done by applying a homopolar voltage to the three parallel-connected phases, as shown in figure 7.20. The amplitudes of the normal and inverse voltage sources
1 | 1 | homopolar impedance. This is done by applying a homopolar voltage to the three parallel-connected phases, as shown in figure 7.20. The amplitudes of the normal and inverse voltage sources (U<sub>0</sub>
en | en | impedance. This is done by applying a homopolar voltage to the three parallel-connected phases, as shown in figure 7.20. The amplitudes of the normal and inverse voltage sources (U<sub>0</sub> 1
U | U | This is done by applying a homopolar voltage to the three parallel-connected phases, as shown in figure 7.20. The amplitudes of the normal and inverse voltage sources (U<sub>0</sub> 1 en
2 | 2 | is done by applying a homopolar voltage to the three parallel-connected phases, as shown in figure 7.20. The amplitudes of the normal and inverse voltage sources (U<sub>0</sub> 1 en U
) | ) | done by applying a homopolar voltage to the three parallel-connected phases, as shown in figure 7.20. The amplitudes of the normal and inverse voltage sources (U<sub>0</sub> 1 en U 2
zijn in dat geval nul. | are in that case zero. | by applying a homopolar voltage to the three parallel-connected phases, as shown in figure 7.20. The amplitudes of the normal and inverse voltage sources (U<sub>0</sub> 1 en U 2 )
Figuur 7.20 Meting van de homopolaire impedantie | Figure 7.20 Measurement of the homopolar impedance | to the three parallel-connected phases, as shown in figure 7.20. The amplitudes of the normal and inverse voltage sources (U<sub>0</sub> 1 en U 2 ) are in that case zero.
In een gebalanceerd driefasensymmetrisch net geldt voor de te meten lijnimpedantie: | In a balanced three-phase symmetrical network, the following applies to the line impedance to be measured: | in figure 7.20. The amplitudes of the normal and inverse voltage sources (U<sub>0</sub> 1 en U 2 ) are in that case zero. Figure 7.20 Measurement of the homopolar impedance
Z | Z | 2 ) are in that case zero. Figure 7.20 Measurement of the homopolar impedance In a balanced three-phase symmetrical network, the following applies to the line impedance to be measured:
L | L | ) are in that case zero. Figure 7.20 Measurement of the homopolar impedance In a balanced three-phase symmetrical network, the following applies to the line impedance to be measured: Z
are in that case zero. Figure 7.20 Measurement of the homopolar impedance In a balanced three-phase symmetrical network, the following applies to the line impedance to be measured: Z L
a | a | that case zero. Figure 7.20 Measurement of the homopolar impedance In a balanced three-phase symmetrical network, the following applies to the line impedance to be measured: Z L = Z
case zero. Figure 7.20 Measurement of the homopolar impedance In a balanced three-phase symmetrical network, the following applies to the line impedance to be measured: Z L = Z a
b | b | Figure 7.20 Measurement of the homopolar impedance In a balanced three-phase symmetrical network, the following applies to the line impedance to be measured: Z L = Z a = Z
7.20 Measurement of the homopolar impedance In a balanced three-phase symmetrical network, the following applies to the line impedance to be measured: Z L = Z a = Z b
c | c | of the homopolar impedance In a balanced three-phase symmetrical network, the following applies to the line impedance to be measured: Z L = Z a = Z b = Z
, zodat voor de stromen geldt: | , so the following applies to the currents: | the homopolar impedance In a balanced three-phase symmetrical network, the following applies to the line impedance to be measured: Z L = Z a = Z b = Z c
I | I | network, the following applies to the line impedance to be measured: Z L = Z a = Z b = Z c , so the following applies to the currents:
a | a | the following applies to the line impedance to be measured: Z L = Z a = Z b = Z c , so the following applies to the currents: I
following applies to the line impedance to be measured: Z L = Z a = Z b = Z c , so the following applies to the currents: I a
b | b | to the line impedance to be measured: Z L = Z a = Z b = Z c , so the following applies to the currents: I a = I
the line impedance to be measured: Z L = Z a = Z b = Z c , so the following applies to the currents: I a = I b
c | c | impedance to be measured: Z L = Z a = Z b = Z c , so the following applies to the currents: I a = I b = I
to be measured: Z L = Z a = Z b = Z c , so the following applies to the currents: I a = I b = I c
0 | 0 | measured: Z L = Z a = Z b = Z c , so the following applies to the currents: I a = I b = I c = I
. Dan is uit de afbeelding af te leiden dat voor de meting volgt: | . Then it can be deduced from the image that for the measurement: | Z L = Z a = Z b = Z c , so the following applies to the currents: I a = I b = I c = I 0
[ | [ | the following applies to the currents: I a = I b = I c = I 0 . Then it can be deduced from the image that for the measurement:
7.44 | 7.44 | following applies to the currents: I a = I b = I c = I 0 . Then it can be deduced from the image that for the measurement: [
] | ] | applies to the currents: I a = I b = I c = I 0 . Then it can be deduced from the image that for the measurement: [ 7.44
Uit bovenstaande vergelijking volgt voor de homopolaire impedantie: | From the above equation, it follows for the homopolar impedance: | to the currents: I a = I b = I c = I 0 . Then it can be deduced from the image that for the measurement: [ 7.44 ]
[ | [ | c = I 0 . Then it can be deduced from the image that for the measurement: [ 7.44 ] From the above equation, it follows for the homopolar impedance:
7.45 | 7.45
] | ] | I 0 . Then it can be deduced from the image that for the measurement: [ 7.44 ] From the above equation, it follows for the homopolar impedance: [ 7.45
Tijdens de meting worden drie fasen kortgesloten en wordt derhalve de parallelschakeling van drie homopolaire impedanties gemeten: | During the measurement, three phases are short-circuited, and therefore the parallel connection of three homopolar impedances is measured: | 0 . Then it can be deduced from the image that for the measurement: [ 7.44 ] From the above equation, it follows for the homopolar impedance: [ 7.45 ]
I | I | the above equation, it follows for the homopolar impedance: [ 7.45 ] During the measurement, three phases are short-circuited, and therefore the parallel connection of three homopolar impedances is measured:
M | M | above equation, it follows for the homopolar impedance: [ 7.45 ] During the measurement, three phases are short-circuited, and therefore the parallel connection of three homopolar impedances is measured: I
equation, it follows for the homopolar impedance: [ 7.45 ] During the measurement, three phases are short-circuited, and therefore the parallel connection of three homopolar impedances is measured: I M
0 | 0 | follows for the homopolar impedance: [ 7.45 ] During the measurement, three phases are short-circuited, and therefore the parallel connection of three homopolar impedances is measured: I M = 3I
. Als gevolg wordt de homopolaire impedantie uit de meting bepaald door de gemeten impedantie met 3 te vermenigvuldigen. | As a result, the homopolar impedance from the measurement is determined by multiplying the measured impedance by 3. | for the homopolar impedance: [ 7.45 ] During the measurement, three phases are short-circuited, and therefore the parallel connection of three homopolar impedances is measured: I M = 3I 0
[ | [ | connection of three homopolar impedances is measured: I M = 3I 0 As a result, the homopolar impedance from the measurement is determined by multiplying the measured impedance by 3.
7.46 | 7.46 | of three homopolar impedances is measured: I M = 3I 0 As a result, the homopolar impedance from the measurement is determined by multiplying the measured impedance by 3. [
] | ] | three homopolar impedances is measured: I M = 3I 0 As a result, the homopolar impedance from the measurement is determined by multiplying the measured impedance by 3. [ 7.46
De homopolaire impedantie wordt dus bepaald door het totale retourcircuit, dat bestaat uit de nulgeleider (indien aanwezig), de afscherming en wapening van de kabel, de grond, geleidende buizen, tram- en treinrails en alle andere geleidende voorwerpen in het retourcircuit. Dit maakt het zo moeilijk de waarde van de homopolaire impedantie te berekenen. Om die reden is het verstandig van belangrijke circuits, voordat zij in bedrijf worden genomen, de homopolaire impedantie te meten. | The homopolar impedance is thus determined by the entire return circuit, which consists of the neutral conductor (if present), the shielding and armoring of the cable, the ground, conductive pipes, tram and train rails, and all other conductive objects in the return circuit. This makes it so difficult to calculate the value of the homopolar impedance. For this reason, it is advisable to measure the homopolar impedance of important circuits before they are put into operation. | homopolar impedances is measured: I M = 3I 0 As a result, the homopolar impedance from the measurement is determined by multiplying the measured impedance by 3. [ 7.46 ]
7.7 Rekenen met behulp van genormeerde grootheden | 7.7 Calculations Using Normalized Quantities | so difficult to calculate the value of the homopolar impedance. For this reason, it is advisable to measure the homopolar impedance of important circuits before they are put into operation.
In veel berekeningsprogramma’s wordt niet gerekend met de werkelijke fysische grootheden, maar met genormeerde grootheden. Dit wordt gedaan zodat het mogelijk wordt om tegelijkertijd aan laagspannings- middenspannings en hoogspanningssystemen te rekenen, waarvan de grootheden numeriek onderling veel verschillen. In computerprogramma’s zou gebruik van fysische grootheden namelijk kunnen leiden tot numerieke problemen. De genormeerde grootheden worden uitgedrukt in per unit (pu). Een tweede voordeel van deze methode is dat het met de hand berekenen van kortsluitstromen over de spanningniveaus van meerdere transformatoren veel eenvoudiger wordt. | In many calculation programs, actual physical quantities are not used, but normalized quantities are. This is done to make it possible to simultaneously calculate low-voltage, medium-voltage, and high-voltage systems, whose quantities differ numerically from each other. Using physical quantities in computer programs could lead to numerical problems. The normalized quantities are expressed in per unit (pu). A second advantage of this method is that manually calculating short-circuit currents across the voltage levels of multiple transformers becomes much simpler. | value of the homopolar impedance. For this reason, it is advisable to measure the homopolar impedance of important circuits before they are put into operation. 7.7 Calculations Using Normalized Quantities
Alle grootheden worden genormeerd met behulp van basisgrootheden. Een aantal basisgrootheden wordt gekozen, waarna de overige basisgrootheden worden afgeleid. Meestal wordt de basisgrootheid voor spanning en voor vermogen gekozen, waarna de basisgrootheden voor stroom en impedantie worden afgeleid. Indien de basisgrootheid van het vermogen willekeurig gekozen wordt en de basisgrootheid van de spanning gelijk genomen wordt aan de nominale spanning per spanningniveau, geldt voor de basisgrootheden: | All quantities are normalized using base quantities. A number of base quantities are chosen, after which the remaining base quantities are derived. Usually, the base quantity for voltage and power is chosen, after which the base quantities for current and impedance are derived. If the base quantity for power is chosen arbitrarily and the base quantity for voltage is taken to be equal to the nominal voltage per voltage level, the following applies to the base quantities: | normalized quantities are expressed in per unit (pu). A second advantage of this method is that manually calculating short-circuit currents across the voltage levels of multiple transformers becomes much simpler.
S | S | for power is chosen arbitrarily and the base quantity for voltage is taken to be equal to the nominal voltage per voltage level, the following applies to the base quantities:
basis | basis | power is chosen arbitrarily and the base quantity for voltage is taken to be equal to the nominal voltage per voltage level, the following applies to the base quantities: S
keuze voor een 3-fasig basis vermogen | choice for a 3-phase base power | is chosen arbitrarily and the base quantity for voltage is taken to be equal to the nominal voltage per voltage level, the following applies to the base quantities: S basis
(MVA) | (MVA) | quantity for voltage is taken to be equal to the nominal voltage per voltage level, the following applies to the base quantities: S basis choice for a 3-phase base power
U | U | for voltage is taken to be equal to the nominal voltage per voltage level, the following applies to the base quantities: S basis choice for a 3-phase base power (MVA)
basis | basis | voltage is taken to be equal to the nominal voltage per voltage level, the following applies to the base quantities: S basis choice for a 3-phase base power (MVA) U
gekoppelde spanning per spanningsniveau | coupled voltage per voltage level | is taken to be equal to the nominal voltage per voltage level, the following applies to the base quantities: S basis choice for a 3-phase base power (MVA) U basis
(kV) | (kV) | to the nominal voltage per voltage level, the following applies to the base quantities: S basis choice for a 3-phase base power (MVA) U basis coupled voltage per voltage level
I | I | the nominal voltage per voltage level, the following applies to the base quantities: S basis choice for a 3-phase base power (MVA) U basis coupled voltage per voltage level (kV)
basis | basis | nominal voltage per voltage level, the following applies to the base quantities: S basis choice for a 3-phase base power (MVA) U basis coupled voltage per voltage level (kV) I
basis fasestroom: | base phase current: | voltage per voltage level, the following applies to the base quantities: S basis choice for a 3-phase base power (MVA) U basis coupled voltage per voltage level (kV) I basis
(kA) | (kA) | level, the following applies to the base quantities: S basis choice for a 3-phase base power (MVA) U basis coupled voltage per voltage level (kV) I basis base phase current:
Z | Z | the following applies to the base quantities: S basis choice for a 3-phase base power (MVA) U basis coupled voltage per voltage level (kV) I basis base phase current: (kA)
basis | basis | following applies to the base quantities: S basis choice for a 3-phase base power (MVA) U basis coupled voltage per voltage level (kV) I basis base phase current: (kA) Z
basis impedantie: | base impedance: | applies to the base quantities: S basis choice for a 3-phase base power (MVA) U basis coupled voltage per voltage level (kV) I basis base phase current: (kA) Z basis
(Ω) | (Ω) | the base quantities: S basis choice for a 3-phase base power (MVA) U basis coupled voltage per voltage level (kV) I basis base phase current: (kA) Z basis base impedance:
Indien in de relatie voor de basisimpedantie teller en noemer met | If in the relationship for the base impedance, the numerator and denominator are | base quantities: S basis choice for a 3-phase base power (MVA) U basis coupled voltage per voltage level (kV) I basis base phase current: (kA) Z basis base impedance: (Ω)
U | U | coupled voltage per voltage level (kV) I basis base phase current: (kA) Z basis base impedance: (Ω) If in the relationship for the base impedance, the numerator and denominator are
basis | basis | voltage per voltage level (kV) I basis base phase current: (kA) Z basis base impedance: (Ω) If in the relationship for the base impedance, the numerator and denominator are U
vermenigvuldigd worden, gaat deze over in: | are multiplied, it becomes: | per voltage level (kV) I basis base phase current: (kA) Z basis base impedance: (Ω) If in the relationship for the base impedance, the numerator and denominator are U basis
Z | Z | I basis base phase current: (kA) Z basis base impedance: (Ω) If in the relationship for the base impedance, the numerator and denominator are U basis are multiplied, it becomes:
basis | basis | basis base phase current: (kA) Z basis base impedance: (Ω) If in the relationship for the base impedance, the numerator and denominator are U basis are multiplied, it becomes: Z
basis impedantie: | base impedance: | base phase current: (kA) Z basis base impedance: (Ω) If in the relationship for the base impedance, the numerator and denominator are U basis are multiplied, it becomes: Z basis
(Ω) | (Ω) | current: (kA) Z basis base impedance: (Ω) If in the relationship for the base impedance, the numerator and denominator are U basis are multiplied, it becomes: Z basis base impedance:
De relatie tussen vermogen, spanning, stroom en impedantie is aldus bepaald: | The relationship between power, voltage, current, and impedance is thus determined: | (kA) Z basis base impedance: (Ω) If in the relationship for the base impedance, the numerator and denominator are U basis are multiplied, it becomes: Z basis base impedance: (Ω)
[ | [ | the base impedance, the numerator and denominator are U basis are multiplied, it becomes: Z basis base impedance: (Ω) The relationship between power, voltage, current, and impedance is thus determined:
7.47 | 7.47 | base impedance, the numerator and denominator are U basis are multiplied, it becomes: Z basis base impedance: (Ω) The relationship between power, voltage, current, and impedance is thus determined: [
] | ] | impedance, the numerator and denominator are U basis are multiplied, it becomes: Z basis base impedance: (Ω) The relationship between power, voltage, current, and impedance is thus determined: [ 7.47
De genormeerde grootheden worden dan als volgt afgeleid uit de fysische grootheden en hun basisgrootheden: | The normalized quantities are then derived from the physical quantities and their base quantities as follows: | the numerator and denominator are U basis are multiplied, it becomes: Z basis base impedance: (Ω) The relationship between power, voltage, current, and impedance is thus determined: [ 7.47 ]
[ | [ | The relationship between power, voltage, current, and impedance is thus determined: [ 7.47 ] The normalized quantities are then derived from the physical quantities and their base quantities as follows:
7.48 | 7.48 | relationship between power, voltage, current, and impedance is thus determined: [ 7.47 ] The normalized quantities are then derived from the physical quantities and their base quantities as follows: [
] | ] | between power, voltage, current, and impedance is thus determined: [ 7.47 ] The normalized quantities are then derived from the physical quantities and their base quantities as follows: [ 7.48
Als gevolg geldt voor de wet van Ohm: | As a result, Ohm's law applies: | power, voltage, current, and impedance is thus determined: [ 7.47 ] The normalized quantities are then derived from the physical quantities and their base quantities as follows: [ 7.48 ]
[ | [ | thus determined: [ 7.47 ] The normalized quantities are then derived from the physical quantities and their base quantities as follows: [ 7.48 ] As a result, Ohm's law applies:
7.49 | 7.49 | determined: [ 7.47 ] The normalized quantities are then derived from the physical quantities and their base quantities as follows: [ 7.48 ] As a result, Ohm's law applies: [
] | ] | [ 7.47 ] The normalized quantities are then derived from the physical quantities and their base quantities as follows: [ 7.48 ] As a result, Ohm's law applies: [ 7.49
Door links en rechts van het gelijkteken te delen door de basisspanning, volgens de bovenstaande definitie, volgt dezelfde uitdrukking in per unit: | By dividing both sides of the equal sign by the base voltage, according to the above definition, the same expression in per unit follows: | 7.47 ] The normalized quantities are then derived from the physical quantities and their base quantities as follows: [ 7.48 ] As a result, Ohm's law applies: [ 7.49 ]
[ | [ | Ohm's law applies: [ 7.49 ] By dividing both sides of the equal sign by the base voltage, according to the above definition, the same expression in per unit follows:
7.50 | 7.50 | law applies: [ 7.49 ] By dividing both sides of the equal sign by the base voltage, according to the above definition, the same expression in per unit follows: [
] | ] | applies: [ 7.49 ] By dividing both sides of the equal sign by the base voltage, according to the above definition, the same expression in per unit follows: [ 7.50
Bij het gebruik van het per unit systeem geldt voor de per unit-waarden: | When using the per unit system, the following applies to the per unit values: | [ 7.49 ] By dividing both sides of the equal sign by the base voltage, according to the above definition, the same expression in per unit follows: [ 7.50 ]
het vermogen representeert het driefasig vermogen | the power represents the three-phase power | voltage, according to the above definition, the same expression in per unit follows: [ 7.50 ] When using the per unit system, the following applies to the per unit values:
de spanning representeert de gekoppelde spanning | the voltage represents the line-to-line voltage | the same expression in per unit follows: [ 7.50 ] When using the per unit system, the following applies to the per unit values: the power represents the three-phase power
de stroom representeert de fasestroom | the current represents the phase current | follows: [ 7.50 ] When using the per unit system, the following applies to the per unit values: the power represents the three-phase power the voltage represents the line-to-line voltage
de impedantie representeert de fase-impedantie. | the impedance represents the phase impedance. | the per unit system, the following applies to the per unit values: the power represents the three-phase power the voltage represents the line-to-line voltage the current represents the phase current